Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 018113.20 - SUSTAINABLE DESIGN REQUIREMENTS - LEED v4.1 BD+C: NEW CONSTRUCTION AND MAJOR RENOVATION

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Review the Evaluations and applicable USGBC LEED Rating System before revising this Section.

Where practical, terminology used in this Section has been made identical to or at least consistent with terminology used in UGBC's LEED Rating Systems; if questions arise relating to terminology, review the applicable LEED reference guide and the standards referenced by applicable USGBC LEED Rating System for possible explanations.

If Project design team does not include a LEED Accredited Professional (LEED AP), consider engaging a Sustainability Consultant; INc "LEED Accredited Professional" applies if at least one principal participant of Project team is a LEED AP. Note that all LEED credits are optional, so delete requirements for credits not sought.

- GENERAL

      - SUMMARY

        - Section includes general requirements and procedures for compliance with USGBC's LEED prerequisites and credits needed for Project to obtain LEED [Certified] [Silver] [Gold] [Platinum] certification based on USGBC's "LEED v4.1 for Building Design and Construction" (hereafter, LEED v4.1 BD+C).

          - Specific requirements for LEED are also included in other Sections.

          - Other LEED prerequisites and credits needed to obtain LEED certification depend on product selections and may not be specifically identified as LEED requirements. Compliance with requirements needed to obtain LEED prerequisites and credits may be used as one criterion to evaluate substitution requests and comparable product requests.

If retaining first subparagraph below, attach a copy of LEED checklist to end of this Section as information for Contractor.

          - A copy of LEED Project checklist is attached at end of this Section for information only.

            - Some LEED prerequisites and credits needed to obtain indicated LEED certification depend on Architect's design and other aspects of Project that are not part of the Work of the Contract.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - ANSI/BIFMA e3 Furniture Sustainability Standard: Standard addressing environmental and social impacts throughout the furniture supply chain.

        - Bio-Based Materials: Products containing some percentage of biologically renewable resource.

        - BUG Rating Method: The BUG rating of a fixture determines how much light trespass is produced by considering backlight (B), uplight (U), and glare (G).

        - Chain-of-Custody Certificates: Certificates signed by manufacturers certifying that wood used to make products was obtained from forests certified by an FSC-accredited certification body to comply with FSC STD-01-001. Certificates to include evidence that manufacturer is certified for chain of custody by an FSC-accredited certification body.

        - Cradle to Cradle: Product certification assessing material health, material reutilization, renewable energy and carbon management, water stewardship, and social fairness.

        - Declare: A product transparency disclosure that identifies material source, composition, and end-of-life procedures.

        - Environmental Product Declaration (EPD): A transparency reporting tool communicating what a product is made of and the environmental impact.

        - Extended Producer Responsibility: A waste management strategy promoting integration of life-cycle costs associated with goods into the market price of products. Typically, this involves a take-back or recycling program run by manufacturer at the end of the product's lifespan.

        - Facts: Standard evaluating sustainability of furniture products over the product life cycle.

        - Health Product Declaration (HPD): Disclosure of products contents and associated health information.

        - LEED: USGBC's "LEED v4.1 for Building Design and Construction." Definitions that are part of this document apply to this Section.

        - Living Product Challenge: A product framework for manufacturers examining place, water, energy, health, materials, and equity in production of materials.

        - Manufacturer Inventory: A published, complete content inventory for products.

        - Product Lens: Transparency disclosure highlighting hazard information.

        - REACH Optimization: International standard outlining hazardous substances of high concern to be avoided in material composition.

Note that LEED uses the term "preconsumer" rather than "postindustrial." Also note that when manufacturers and trade associations use the term "postindustrial," it often includes spills, scraps, and damaged and surplus materials that are fed back into the same manufacturing process and that these materials are not considered recycled content by USGBC's LEED Rating Systems.

        - Recycled Content: The recycled content value of a material assembly to be determined by weight. The recycled fraction of the assembly is then multiplied by the cost of assembly to determine the recycled content value.

          - "Postconsumer" material is defined as waste material generated by households or by commercial, industrial, and institutional facilities in their role as end users of the product, which can no longer be used for its intended purpose.

          - "Preconsumer" material is defined as material diverted from the waste stream during the manufacturing process. Reutilization of materials (such as rework, regrind, or scrap, generated in a process and capable of being reclaimed within the same process that generated it) is excluded.

        - Regional Materials: Materials that have been extracted, harvested, or recovered, as well as manufactured, within 100 miles (160 km) of Project site. If only a fraction of a product or material is extracted/harvested/recovered and manufactured locally, then only that percentage (by weight) contributes to the regional value.

        - WaterSense Label: The WaterSense label from the EPA specifies water efficiency and performance.

        - Whole-Building Life-Cycle Assessment: The Life Cycle Assessment (LCA) is a methodology that evaluates the carbon and other environmental impacts of building materials over the projected lifespan of the building.

      - PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a conference.

        - Preinstallation Conference: Conduct conference at [Project site] <Insert location>. Review sustainability goals, municipal and state sustainability requirements, LEED objectives, and action plans for meeting requirements.

      - ADMINISTRATIVE REQUIREMENTS

Retain one of two paragraphs in this article. Retain first if Architect or Owner submits LEED documentation to USGBC; retain second if Contractor does.

        - Respond to questions and requests from Architect about USGBC's LEED prerequisites and credits that are Contractor's responsibility, that depend on product selection or product qualities, or that depend on Contractor's procedures until USGBC has made its determination on Project's LEED certification application.

        - Submit documentation to USGBC and respond to questions and requests from USGBC about its LEED prerequisites and credits that are Contractor's responsibility, that depend on product selection or product qualities, or that depend on Contractor's procedures until USGBC has made its determination on Project's LEED certification application.

          - Document correspondence with USGBC as informational submittals.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

Requirements in this article assume that product data and cost information are submitted to Architect, who then either fills out the LEED online forms or forwards the submittals to Owner or Sustainability Consultant to fill out the forms. Submittals include documentation needed to verify compliance with LEED requirements so that Architect, Owner, or Sustainability Consultant can be assured, when filling out the online forms, that requirements have been met. Although USGBC's LEED reference guides do not specifically identify who can certify compliance, submittals could be deleted if requirements in this Section are revised to require Contractor to fill out the online forms and to notify Architect or Owner when completed.

        - General: Submit sustainable design submittals required by other Sections.

Retain first paragraph below if separate sustainable design submittals are required.

        - Sustainable design submittals are in addition to other submittals.

          - If submitted item is identical to that submitted to comply with other requirements, include additional copy with other submittal as a record of compliance with indicated LEED requirements instead of separate sustainable design submittal. Mark additional copy "Sustainable design submittal."

Submittals in "Sustainable Design Documentation Submittals" Paragraph below may be necessary to verify compliance with indicated USGBC LEED prerequisites and credits. Additional submittals may be required in other Sections.

        - Sustainable Design Documentation Submittals:

          - Plumbing submittal packages.

          - Mechanical submittal packages.

          - EPDs complying with LEED requirements.

          - Documentation for products that comply with LEED requirements for multi-attribute optimization.

          - Sustainability reports for products that comply with LEED requirements for sourcing of raw materials.

          - Material ingredient reports for products that comply with LEED requirements for material ingredient reporting.

          - Documentation for products that comply with LEED requirements for material ingredient optimization.

          - Documentation complying with Section 017419 "Construction Waste Management and Disposal."

First eight subparagraphs below are based on requiring all materials in a category to comply with minimum requirements. An alternative is the budget method. If the budget method is used, add a submittal showing calculations.

          - Product data for adhesives and sealants used inside the weatherproofing system, indicating VOC content and laboratory test reports showing compliance with requirements for low-emitting materials.

          - Product data for paints and coatings used inside the weatherproofing system, indicating VOC content and laboratory test reports showing compliance with requirements for low-emitting materials.

          - Laboratory test reports for flooring, indicating compliance with requirements for low-emitting materials.

          - Laboratory test reports for wall materials, indicating compliance with requirements for low-emitting materials.

          - Laboratory test reports for ceilings, indicating compliance with requirements for low-emitting materials.

          - Laboratory test reports for insulation, indicating compliance with requirements for low-emitting materials.

          - Laboratory test reports for furniture, indicating compliance with requirements for low-emitting materials.

          - Laboratory test reports for products containing composite wood or agrifiber products or wood glues, indicating compliance with requirements for low-emitting materials.

          - Construction Indoor Air Quality (IAQ) Management:

            - Construction IAQ management plan.

            - Product data for temporary filtration media.

            - Product data for filtration media used during occupancy.

            - Construction Documentation: Six photographs at three different times during construction period, along with a brief description of SMACNA approach employed, documenting implementation of IAQ management measures, including protection of ducts and on-site stored or installed absorptive materials.

Delete "IAQ Assessment" Subparagraph below if using Owner-engaged IAQ testing.

          - IAQ Assessment:

Retain first two subparagraphs below if using building air flush-out procedures.

            - Signed statement describing the building air flush-out procedures, including dates when flush-out was begun and completed and statement that filtration media was replaced after flush-out.

            - Product data for filtration media used during flush-out and occupancy.

Retain subparagraph below if using Contractor-engaged IAQ testing.

            - Report from testing and inspecting agency indicating results of IAQ testing and documentation showing compliance with IAQ testing procedures and requirements.

      - INFORMATIONAL SUBMITTALS

Information submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

        - Qualification Data: For LEED coordinator.

        - Project Materials Cost Data: Provide statement indicating total cost for materials used for Project. Costs exclude labor, overhead, and profit. Include breakout of costs for the following categories of items:

          - Plumbing.

          - Mechanical.

          - Electrical.

          - Specialty items, such as elevators and equipment.

"Sustainable Design Action Plans" Paragraph below requires Contractor to make early submittals indicating how certain LEED requirements will be met. This action can provide reassurance that Contractor understands LEED requirements and can clear up misunderstandings before they become a bigger problem.

        - Sustainable Design Action Plans: Provide preliminary submittals within [seven] [14] [30] [60] <Insert number> days of date established for [commencement of the Work] [the Notice to Proceed] [the Notice of Award], indicating how the following requirements will be met:

          - List of proposed products with EPDs.

          - List of proposed products complying with requirements for multi-attribute optimization.

          - List of proposed products complying with requirements for sourcing of raw materials.

          - List of proposed products complying with requirements for material ingredient reporting.

          - List of proposed products complying with requirements for material ingredient optimization.

          - Waste management plan complying with Section 017419 "Construction Waste Management and Disposal."

          - Construction IAQ management plan.

          - IAQ assessment plan.

        - Sustainable Design Progress Reports: Concurrent with each Application for Payment, submit reports comparing actual construction and purchasing activities with sustainable design action plans.

      - QUALITY ASSURANCE

Requiring that Contractor engage a LEED AP to coordinate LEED requirements may help avoid inadvertent errors that could jeopardize Project's LEED certification if Contractors' personnel have limited experience.

        - LEED Coordinator: Engage an experienced LEED AP to coordinate LEED requirements. LEED coordinator may also serve as waste management coordinator.

- PRODUCTS

      - MATERIALS

Usually, retain first paragraph below when requirements for salvaged and refurbished materials, recycled content, bio-based materials, or certified wood are included in other Sections. This action will help ensure that credit requirements are met if costs differ from Architect's estimates.

        - Provide products and procedures necessary to obtain LEED credits indicated as Contractor's responsibility. Although other Sections may specify some requirements that contribute to these LEED credits, Contractor provides additional materials and procedures necessary to obtain LEED credits indicated.

        - At least 20 different products from at least five different manufacturers have EPDs that comply with LEED requirements. Product-specific Type III EPDs are valued as one and one-half of a product.

        - At least 10 percent, by cost, of permanently installed products for Project comply with LEED requirements for multi-attribute optimization.

        - At least 20 different products from at least five different manufacturers have publically released reports that comply with LEED requirements for sourcing of raw materials.

        - At least 20 different products from at least five different manufacturers comply with LEED requirements for material ingredient reporting.

        - At least 10 percent, by cost, of permanently installed products for Project comply with LEED requirements for material ingredient optimization.

"Recycled Content" Paragraph below is an alternative to requiring recycled content in Sections where such products are specified.

        - Recycled Content: Building materials have recycled content such that postconsumer recycled content plus one-half of preconsumer recycled content for Project constitutes a minimum of <Insert number> percent of cost of materials used for Project.

          - Cost of postconsumer recycled content plus one-half of preconsumer recycled content of an item to be determined by dividing weight of postconsumer recycled content plus one-half of preconsumer recycled content in the item by total weight of the item and multiplying by cost of the item.

          - Do not include [furniture, ]plumbing, mechanical and electrical components, and specialty items, such as elevators and equipment, in the calculation.

      - LOW-EMITTING MATERIALS

This article contains requirements applicable to EQc "Low-Emitting Materials." If retaining this article, coordinate with Sections where relevant products are specified to avoid conflicting requirements in those Sections.

        - Paints and Coatings: For field applications that are inside the weatherproofing system, 75 percent of paints and coatings meet the VOC emissions evaluation and 100 percent meet the VOC content evaluations.

Adhesives and sealants are required in many Sections where, without being specifically mentioned, they may be specified only by the requirement to install products in accordance with manufacturer's written instructions. For this reason, it is probably best to retain "Adhesives and Sealants" Paragraph below if this credit is required.

        - Adhesives and Sealants: For field applications that are inside the weatherproofing system, 75 percent of adhesives and sealants meet the VOC emissions evaluation and 100 percent meet the VOC content evaluations.

        - Flooring: A minimum of 90 percent of flooring products meet the VOC emissions evaluation or inherently non-emitting sources criteria or salvaged and reused materials criteria. Subflooring is excluded.

        - Walls: A minimum of 75 percent of wall panel products meet the VOC emissions evaluation or inherently non-emitting sources criteria or salvaged and reused materials criteria. Wall panel products include wall paneling, wall coverings, wall tile, surface wall structures, cubicle/curtain/partition walls, trim, doors, frames, windows, and window treatments. Removable/interchangeable fabric panels, built-in cabinetry, and vertical structural elements are excluded.

        - Ceilings: A minimum of 90 percent of ceilings meet the VOC emissions evaluation or inherently non-emitting sources criteria or salvaged and reused materials criteria. Ceiling products include ceiling panels, ceiling tile, surface ceiling structures, suspended systems, and glazed skylights. Overhead structural elements are excluded.

        - Insulation: A minimum of 75 percent of insulation products meet the VOC emissions evaluation. Insulation products include all thermal and acoustic boards, batts, rolls, blankets, sound attenuation fire blankets, and foamed-in-place, loose-fill, blown, and sprayed insulation. HVAC duct and plumbing piping insulation are excluded.

        - Furniture: A minimum of 75 percent of furniture meets the furniture emissions evaluation or inherently non-emitting sources or salvaged and reused materials criteria. All standalone furniture is included.

If retaining "Composite Wood" Paragraph below, coordinate with Sections where composite wood products are specified to avoid conflicting requirements in those Sections.

        - Composite Wood: A minimum of 75 percent of all composite wood meet the formaldehyde emissions evaluation or salvaged and reused materials criteria. Composite wood materials include particleboard, MDF, hardwood veneer plywood, and structural composite wood.

- EXECUTION

      - NONSMOKING BUILDING

        - Smoking is not permitted within the building or within 25 ft. (8 m) of entrances, operable windows, or outdoor-air intakes.

      - CONSTRUCTION WASTE MANAGEMENT

        - Comply with Section 017419 "Construction Waste Management and Disposal."

      - CONSTRUCTION INDOOR AIR QUALITY (IAQ) MANAGEMENT

        - Comply with SMACNA's "SMACNA IAQ Guideline for Occupied Buildings under Construction."

Coordinate first subparagraph below with Section 015000 "Temporary Facilities and Controls." Identify air handlers and associated return-air inlets authorized by Owner for use during construction period.

          - If Owner authorizes use of permanent heating, cooling, and ventilating systems during construction period as specified in Section 015000 "Temporary Facilities and Controls," install MERV 8 filter media in accordance with ASHRAE 52.2 at each return-air inlet for the air-handling system used during construction.

          - Replace air filters immediately prior to occupancy with new filters specified in Section 234100 "Particulate Air Filtration."

      - INDOOR AIR QUALITY (IAQ) ASSESSMENT

        - Flush-Out:

Project's mechanical engineer of record should verify that HVAC system design and equipment indicated are capable of delivering flush-out indicated. Provide HVAC system and equipment operating information necessary to achieve credit. If Project HVAC systems and equipment cannot suit requirement, consider requiring temporary systems and equipment.

          - After construction ends, prior to occupancy and with all interior finishes installed, perform a building flush-out by supplying a total volume of 14,000 cu. ft. (4 300 000 L) of outdoor air per sq. ft. (sq. m) of floor area while maintaining an internal temperature of at least 60 deg F (16 deg C) and a relative humidity no higher than 60 percent.

In first subparagraph below, indicate operating procedure for each HVAC system and piece of equipment and the operating duration required for flush-out.

            - <Insert operating requirements>.

          - If occupancy is desired prior to flush-out completion, the space may be occupied following delivery of a minimum of 3500 cu. ft. (1 070 000 L) of outdoor air per sq. ft. (sq. m) of floor area to the space. Once a space is occupied, it is ventilated at a minimum rate of 0.30 cfm per sq. ft. (1.52 L/s per sq. m) of outside air or the design minimum outside-air rate prerequisite, whichever is greater. During each day of the flush-out period, ventilation begins a minimum of three hours prior to occupancy and continues during occupancy. These conditions are maintained until a total of 14,000 cu. ft./sq. ft. (4 300 000 L/sq. m) of outside air has been delivered to the space.

In subparagraph below, indicate operating procedure for each HVAC system and piece of equipment and the operating duration required for flush-out.

            - <Insert operating requirements>.

        - Air-Quality Testing: [Engage] [Owner will engage] testing agency to perform the following:

The EPA standard referenced in first subparagraph below is available NTIS, with PB90200288 ordering number; (800) 553-6847.

          - Conduct baseline IAQ testing, after construction ends and prior to occupancy, using testing protocols consistent with the EPA's "Compendium of Methods for the Determination of Air Pollutants in Indoor Air," and as additionally detailed in USGBC's "LEED v4.1 Reference Guide for Building Design and Construction."

          - Demonstrate that contaminant maximum concentrations listed below are not exceeded:

Note that it may be necessary to comply with all requirements in EQc "Indoor Air Quality Assessment" to comply with limits specified in 16 subparagraphs below.

            - Carbon Monoxide: 9 ppm and no greater than 2 ppm above outdoor levels.

            - Particulates (PM10): 50 mcg/cu. m.

            - Particulates (PM2.5): 12 mcg/cu. m.

            - Ozone: 0.07 ppm, in accordance with ASTM D5149.

            - Formaldehyde: 20 mcg/cu. m.

            - Acetaldehyde: 140 mcg/cu. m.

            - Benzene: 3 mcg/cu. m.

            - Hexane: 7000 mcg/cu. m.

            - Naphthalene: 9 mcg/cu. m.

            - Phenol: 200 mcg/cu. m.

            - Styrene: 900 mcg/cu. m.

            - Tetrachloroethylene: 35 mcg/cu. m.

            - Toluene: 300 mcg/cu. m.

            - Vinyl Acetate: 200 mcg/cu. m.

            - Dichlorobenzene: 800 mcg/cu. m.

            - Xylenes - Total: 700 mcg/cu. m.

First subparagraph below is part of LEED credit requirements but creates requirements that are contingent on field conditions that are unknown at time of bid and could influence bids. Also, requirements may result in claims for extra payment and time. Revise to suit office practice.

          - For each sampling point where the maximum concentration limits are exceeded, take corrective action until requirements have been met.

          - Air-sample testing to be conducted as follows:

            - All measurements to be conducted prior to occupancy but during normal occupied hours, and with building ventilation system starting at the normal daily start time and operated at the minimum outside-airflow rate for the occupied mode throughout the duration of the air testing.

            - Building to have all interior finishes installed, including, but not limited to, millwork, doors, paint, carpet, and acoustic tiles. Nonfixed furnishings such as workstations and partitions are encouraged, but not required, to be in place for the testing.

            - Number of sampling locations varies depending on the size of building and number of ventilation systems. For each portion of building served by a separate ventilation system, the number of sampling points to not be less than one per 5000 sq. ft. (465 sq. m).[ For large open spaces, one sampling point per 50,000 sq. ft. (4654 sq. m) may be used.]

            - Air samples to be collected between 3 and 6 ft. (0.9 and 1.8 m) from the floor to represent the breathing zone of occupants, and over a minimum four-hour period.

END OF SECTION 018113.20