Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 033000 - CAST-IN-PLACE CONCRETE

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Access Manufacturer-Provided, AIA MasterSpec-Based Sections:

<Double click here for this Section based on specific manufacturer’s products set as Basis-of-Design at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED 2009, LEED v4, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using the hypertext links.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Cast-in-place concrete, including concrete materials, mixture design, placement procedures, and finishes.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 031000 "Concrete Forming and Accessories" for form-facing materials, form liners, insulating concrete forms, and waterstops.

          - Section 032000 "Concrete Reinforcing" for steel reinforcing bars and welded-wire reinforcement.

          - Section 033300 "Architectural Concrete" for general building applications of specially finished formed concrete.

          - Section 033543 "Polished Concrete Finishing" for concrete floors scheduled to receive a polished concrete finish.

          - Section 035300 "Concrete Topping" for emery- and iron-aggregate concrete floor toppings.

          - Section 312000 "Earth Moving" for drainage fill under slabs-on-ground.

          - Section 321313 "Concrete Paving" for concrete pavement and walks.

          - Section 321316 "Decorative Concrete Paving" for decorative concrete pavement and walks.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

Definition in "Cementitious Materials" Paragraph below refers to those materials that make up the cementitious component of the water/cement ratio (w/cm).

        - Cementitious Materials: Portland cement alone or in combination with one or more of the following: blended hydraulic cement, fly ash, slag cement, other pozzolans, and silica fume; materials subject to compliance with requirements.

        - Water/Cement Ratio (w/cm): The ratio by weight of water to cementitious materials.

      - PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a conference.

        - Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

Retain first subparagraph below if warranted by complexity of design mixtures and quality control of concrete materials.

          - Require representatives of each entity directly concerned with cast-in-place concrete to attend, including the following:

            - Contractor's superintendent.

            - Independent testing agency responsible for concrete design mixtures.

            - Ready-mix concrete manufacturer.

            - Concrete Subcontractor.

Retain first subparagraph below if special concrete finishes are included in Project.

            - Special concrete finish Subcontractor.

          - Review the following:

            - Special inspection and testing and inspecting agency procedures for field quality control.

            - Construction joints, control joints, isolation joints, and joint-filler strips.

            - Semirigid joint fillers.

            - Vapor-retarder installation.

            - Anchor rod and anchorage device installation tolerances.

            - Cold and hot weather concreting procedures.

            - Concrete finishes and finishing.

            - Curing procedures.

            - Forms and form-removal limitations.

            - Shoring and reshoring procedures.

            - Methods for achieving specified floor and slab flatness and levelness.

            - Floor and slab flatness and levelness measurements.

            - Concrete repair procedures.

            - Concrete protection.

            - Initial curing and field curing of field test cylinders (ASTM C31/C31M.)

            - Protection of field cured field test cylinders.

      - ACTION SUBMITTALS

        - Product Data: For each of the following.

          - Portland cement.

          - Fly ash.

          - Slag cement.

          - Blended hydraulic cement.

          - Silica fume.

          - Performance-based hydraulic cement

          - Aggregates.

          - Admixtures:

            - Include limitations of use, including restrictions on cementitious materials, supplementary cementitious materials, air entrainment, aggregates, temperature at time of concrete placement, relative humidity at time of concrete placement, curing conditions, and use of other admixtures.

          - Color pigments.

          - Fiber reinforcement.

          - Vapor retarders.

          - Floor and slab treatments.

          - Liquid floor treatments.

          - Curing materials.

Retain first subparagraph below if color pigments are applicable to Project.

            - Include documentation from color pigment manufacturer, indicating that proposed methods of curing are recommended by color pigment manufacturer.

          - Joint fillers.

          - Repair materials.

        - Sustainable Design Submittals:

          - <Double click to insert sustainable design text for recycled content.>

          - <Double click to insert sustainable design text for regional materials.>

          - <Double click to insert sustainable design text for liquid floor treatments and curing and sealing compounds.>

        - <Double click to insert sustainable design text for advanced inventory and assessment>

Design mixtures in "Design Mixtures" Paragraph below are usually considered to be an action submittal.

        - Design Mixtures: For each concrete mixture, include the following:

          - Mixture identification.

          - Minimum 28-day compressive strength.

          - Durability exposure class.

          - Maximum w/cm.

          - Calculated equilibrium unit weight, for lightweight concrete.

          - Slump limit.

          - Air content.

          - Nominal maximum aggregate size.

          - Steel-fiber reinforcement content.

          - Synthetic micro-fiber content.

          - Indicate amounts of mixing water to be withheld for later addition at Project site if permitted.

Retain first two subparagraphs below if permeability-reducing admixture is applicable to any concrete mix design.

          - Include manufacturer's certification that permeability-reducing admixture is compatible with mix design.

          - Include certification that dosage rate for permeability-reducing admixture matches dosage rate used in performance compliance test.

          - Intended placement method.

          - Submit alternate design mixtures when characteristics of materials, Project conditions, weather, test results, or other circumstances warrant adjustments.

        - Shop Drawings:

          - Construction Joint Layout: Indicate proposed construction joints required to construct the structure.

            - Location of construction joints is subject to approval of the Architect.

        - Samples: For [manufacturer's standard colors for color pigment] [vapor retarder] <Insert products>.

        - Concrete Schedule: For each location of each Class of concrete indicated in "Concrete Mixtures" Article, including the following:

          - Concrete Class designation.

          - Location within Project.

          - Exposure Class designation.

          - Formed Surface Finish designation and final finish.

          - Final finish for floors.

          - Curing process.

          - Floor treatment if any.

      - INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as supplemented in "Quality Assurance" Article.

        - Qualification Data: For the following:

          - Installer: Include copies of applicable ACI certificates.

          - Ready-mixed concrete manufacturer.

Retain subparagraph below if Contractor retains testing agency for field quality control.

          - Testing agency: Include copies of applicable ACI certificates.

Retain "Material Certificates" Paragraph below to require submittal of material certificates from manufacturers.

        - Material Certificates: For each of the following, signed by manufacturers:

Revise 11 subparagraphs below to suit Project.

          - Cementitious materials.

          - Admixtures.

          - Fiber reinforcement.

          - Curing compounds.

          - Floor and slab treatments.

          - Bonding agents.

          - Adhesives.

          - Vapor retarders.

          - Semirigid joint filler.

          - Joint-filler strips.

          - Repair materials.

Retain "Material Test Reports" Paragraph below for material test reports that are Contractor's responsibility.

        - Material Test Reports: For the following, from a qualified testing agency:

          - Portland cement.

          - Fly ash.

          - Slag cement.

          - Blended hydraulic cement.

          - Silica fume.

          - Performance-based hydraulic cement.

          - Aggregates.

          - Admixtures:

            - Permeability-Reducing Admixture: Include independent test reports, indicating compliance with specified requirements, including dosage rate used in test.

Retain first paragraph below if Contractor engages testing agency for measuring floor surface flatness and levelness.

        - Floor surface flatness and levelness measurements report, indicating compliance with specified tolerances.

        - Research Reports:

          - For concrete admixtures in accordance with ICC's Acceptance Criteria AC198.

          - For sheet vapor retarder/termite barrier, showing compliance with ICC AC380.

        - Preconstruction Test Reports: For each mix design.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

Retain paragraph below if preinstallation conference is held.

        - Minutes of preinstallation conference.

      - QUALITY ASSURANCE

Retain "Installer Qualifications" Paragraph below if required. See Section 014000 "Quality Requirements" for general installer qualifications. Verify availability of qualified personnel with a local ACI chapter or concrete contractors. These desirable programs may have limited grass-roots penetration.

        - Installer Qualifications: A qualified installer who employs Project personnel qualified as an ACI-certified Flatwork Technician and Finisher and a supervisor who is a certified ACI Flatwork Concrete Finisher/Technician or an ACI Concrete Flatwork Technician [with experience installing and finishing concrete, incorporating permeability-reducing admixtures].

          - Post-Installed Concrete Anchors Installers: ACI-certified Adhesive Anchor Installer.

        - Ready-Mixed Concrete Manufacturer Qualifications: A firm experienced in manufacturing ready-mixed concrete products and that complies with ASTM C94/C94M requirements for production facilities and equipment.

Retain subparagraph below if required.

          - Manufacturer certified in accordance with NRMCA's "Certification of Ready Mixed Concrete Production Facilities."

Retain "Laboratory Testing Agency Qualifications" Paragraph below if Contractor retains testing agency for concrete mixture design or material test reports.

        - Laboratory Testing Agency Qualifications: A testing agency qualified in accordance with ASTM C1077 and ASTM E329 for testing indicated and employing an ACI-certified Concrete Quality Control Technical Manager.

Retain subparagraph below if requiring minimum qualifications for laboratory personnel performing testing and for laboratory supervisor.

          - Personnel performing laboratory tests to be an ACI-certified Concrete Strength Testing Technician and Concrete Laboratory Testing Technician, Grade I. Testing agency laboratory supervisor to be an ACI-certified Concrete Laboratory Testing Technician, Grade II.

Retain "Field Quality-Control Testing Agency Qualifications" Paragraph below if Contractor retains testing agency field quality control. Retain option if field quality-control testing agency employed by Contractor must be approved by authorities having jurisdiction.

        - Field Quality-Control Testing Agency Qualifications: An independent agency,[ acceptable to authorities having jurisdiction,] qualified in accordance with ASTM C1077 and ASTM E329 for testing indicated.

Retain subparagraph below, required by ACI 301 (ACI 301M) and ASTM C31/C31M if emphasis is needed. ASTM C1077 notes relevant field certification by ACI, NRMCA, and Portland Cement Association; or the National Institute for Certification in Engineering Technologies may demonstrate evidence of competence.

          - Personnel conducting field tests to be qualified as an ACI Concrete Field Testing Technician, Grade 1, in accordance with ACI CPP 610.1 or an equivalent certification program.

Retain "Mockups" Paragraph below if required. If retaining, indicate location, concrete type, and other details of mockups on Drawings or by inserts. Revise wording if only one mockup is required or if mockup of concrete in another location in a building is required.

        - Mockups: Cast concrete [slab-on-ground] [and] [formed-surface] panels to demonstrate typical joints, surface finish, texture, tolerances, floor treatments, and standard of workmanship.

Panel for slab-on-ground may need to be enlarged if powered riding trowels are used and if it is a portion of the floor slab. Dividing panel into four equal sections permits observation of saw joints and may be used for demonstrating different classes of polished concrete specified under Section 033543 "Polished Concrete Finishing" or other special finishes.

          - Slab-On-Ground: Build panel approximately 15 feet by 15 feet (3.35 meters by 3.35 meters) <Insert area> in the location indicated or, if not indicated, as directed by Architect.

            - Divide panel into four equal panels to demonstrate saw joint cutting.

          - Formed Surfaces: Build panel approximately 100 sq. ft. (9.3 sq. m) <Insert area> in the location indicated or, if not indicated, as directed by Architect.

Retain subparagraph below if the intention is to make an exception to the default requirement in Section 014000 "Quality Requirements" for demolishing and removing mockups.

          - Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

      - PRECONSTRUCTION TESTING

        - Preconstruction Testing Service: Engage a qualified testing agency to perform preconstruction testing on each concrete mixture.

          - Include the following information in each test report:

            - Admixture dosage rates.

            - Slump.

            - Air content.

            - Seven-day compressive strength.

            - 28-day compressive strength.

            - Permeability.

      - DELIVERY, STORAGE, AND HANDLING

        - Comply with ASTM C94/C94M and ACI 301 (ACI 301M).

      - FIELD CONDITIONS

        - Cold-Weather Placement: Comply with ACI 301 (ACI 301M) and ACI 306.1 and as follows.

          - Protect concrete work from physical damage or reduced strength that could be caused by frost, freezing actions, or low temperatures.

          - When average high and low temperature is expected to fall below 40 deg F (4.4 deg C) for three successive days, maintain delivered concrete mixture temperature within the temperature range required by ACI 301 (ACI 301M).

          - Do not use frozen materials or materials containing ice or snow.

          - Do not place concrete in contact with surfaces less than 35 deg F (1.7 deg C), other than reinforcing steel.

          - Do not use calcium chloride, salt, or other materials containing antifreeze agents or chemical accelerators unless otherwise specified and approved in mixture designs.

        - Hot-Weather Placement: Comply with ACI 301 (ACI 301M) and ACI 305.1 (ACI 305.1M), and as follows:

          - Maintain concrete temperature at time of discharge to not exceed 95 deg F (35 deg C).

          - Fog-spray forms, steel reinforcement, and subgrade just before placing concrete. Keep subgrade uniformly moist without standing water, soft spots, or dry areas.

      - WARRANTY

When warranties are required, verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws. Manufacturers of self-adhering sheet waterproofing rarely offer more than a materials-only warranty. These warranties customarily do not include costs of excavating and exposing the waterproofing membrane or backfilling and restoring affected construction.

        - Manufacturer's Warranty: Manufacturer agrees to furnish replacement sheet vapor retarder/termite barrier material and accessories for sheet vapor retarder/ termite barrier and accessories that do not comply with requirements or that fail to resist penetration by termites within specified warranty period.

          - Warranty Period: 10 years from date of Substantial Completion.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - CONCRETE, GENERAL

        - ACI Publications: Comply with ACI 301 (ACI 301M) unless modified by requirements in the Contract Documents.

      - CONCRETE MATERIALS

        - <Double click to insert sustainable design text for regional materials (concrete).>

        - Source Limitations:

          - Obtain all concrete mixtures from a single ready-mixed concrete manufacturer for entire Project.

          - Obtain each type or class of cementitious material of the same brand from the same manufacturer's plant.

          - Obtain aggregate from single source.

          - Obtain each type of admixture from single source from single manufacturer.

        - Cementitious Materials:

Retain type and color of portland cement from options in "Portland Cement" Subparagraph below.

          - Portland Cement: ASTM C150/C150M, [Type I] [Type II] [Type I/II] [Type III] [Type V], [gray] [white].

Retain supplementary cementing materials in "Fly Ash" and "Slag Cement" subparagraphs below. Ready-mix-concrete manufacturer blends these materials with portland cement. Fly ash, slag cement, or pozzolanic materials may slow rate of concrete strengthening and affect color uniformity.

          - Fly Ash: ASTM C618, Class C or F.

          - Slag Cement: ASTM C989/C989M, Grade 100 or 120.

Retain "Blended Hydraulic Cement" Subparagraph below if factory-blended hydraulic cement is permitted; verify availability of options before specifying. Fly ash, slag cement, or pozzolanic materials in the nonportland cement part of blended hydraulic cement may slow rate of concrete strengthening and affect color uniformity. Insert ASTM C1157/C1157M if acceptable.

          - Blended Hydraulic Cement: ASTM C595/C595M, [Type IS, portland blast-furnace slag] [Type IP, portland-pozzolan] [Type IL, portland-limestone] [Type IT, ternary blended] cement.

Silica fume in "Silica Fume" Subparagraph below is most often used in high-strength concrete and in special applications, such as bridge decks, to enhance durability by lowering permeability of concrete. ACI 301 (ACI 301M) identifies silica fume as a cementitious material.

          - Silica Fume: ASTM C1240 amorphous silica.

Retain one or more options in "Performance-Based Hydraulic Cement" Paragraph below. For low reactivity with alkali-silica-reactive aggregates, add the optional suffix "(R)" to selected Type (e.g., Type MS(R). This option should only be specified for use with aggregates with known alkali-reactivity.

          - Performance-Based Hydraulic Cement: ASTM C1157/C1157M: [Type GU, general use] [Type HE, high early strength] [Type MS, moderate sulfate resistance] [Type HS, high sulfate resistance] [Type MH, moderate heat of hydration] [Type LH, low heat of hydration].

Retain class of aggregate from options in "Normal-Weight Aggregates" Paragraph below or revise to suit Project. ASTM C33/C33M limits deleterious substances in coarse aggregate, depending on climate severity and in-service location of concrete. Classes in first set of options are ASTM C33/C33M default classes for concrete exposed to weather for Severe (S), Moderate (M), and Negligible (N) weathering regions, respectively. Revise first two options to "Class 4S" or "4M" if concrete is exposed to frequent wetting.

        - Normal-Weight Aggregates: ASTM C33/C33M, [Class 3S] [Class 3M] [Class 1N] <Insert class> coarse aggregate or better, graded. Provide aggregates from a single source.

Retain "Alkali-Silica Reaction" Subparagraph below if damage caused by concrete expansion from alkali silica or alkali carbonate reactions is anticipated.

          - Alkali-Silica Reaction: Comply with one of the following:

            - Expansion Result of Aggregate: Not more than 0.04 percent at one-year when tested in accordance with ASTM C1293.

            - Expansion Results of Aggregate and Cementitious Materials in Combination: Not more than 0.10 percent at an age of 16 days when tested in accordance with ASTM C1567.

            - Alkali Content in Concrete: Not more than 4 lb./cu. yd. (2.37 kg/cu. m) for moderately reactive aggregate or 3 lb./cu. yd. (1.78 kg/cu. m) for highly reactive aggregate, when tested in accordance with ASTM C1293 and categorized in accordance with ASTM C1778, based on alkali content being calculated in accordance with ACI 301 (ACI 301M).

Retain coarse-aggregate size from three options in "Maximum Coarse-Aggregate Size" Subparagraph below; insert gradation requirements if preferred. Aggregate size limits relate to spacing of steel reinforcement, depth of slab, or thickness of concrete member.

          - Maximum Coarse-Aggregate Size: [1-1/2 inches (38 mm)] [1 inch (25 mm)] [3/4 inch (19 mm)] <Insert dimension> nominal.

Retain "Fine Aggregate" Subparagraph below if optional restriction for fine aggregate in ASTM C33/C33M is required.

          - Fine Aggregate: Free of materials with deleterious reactivity to alkali in cement.

Retain "Lightweight Aggregate" Paragraph below if using lightweight aggregate for structural lightweight concrete. Retain size limit from four options below.

        - Lightweight Aggregate: ASTM C330/C330M, [1-inch (25-mm)] [3/4-inch (19-mm)] [1/2-inch (13-mm)] [3/8-inch (10-mm)] nominal maximum aggregate size.

        - Air-Entraining Admixture: ASTM C260/C260M.

        - Chemical Admixtures: Certified by manufacturer to be compatible with other admixtures that do not contribute water-soluble chloride ions exceeding those permitted in hardened concrete. Do not use calcium chloride or admixtures containing calcium chloride[ in steel-reinforced concrete].

Retain one or more chemical admixtures from "Water-Reducing Admixture"; "Retarding Admixture"; "Water-Reducing and -Retarding Admixture"; "High-Range, Water-Reducing Admixture"; "High-Range, Water-Reducing and -Retarding Admixture"; and "Plasticizing and Retarding Admixture" subparagraphs below.

          - Water-Reducing Admixture: ASTM C494/C494M, Type A.

          - Retarding Admixture: ASTM C494/C494M, Type B.

          - Water-Reducing and -Retarding Admixture: ASTM C494/C494M, Type D.

          - High-Range, Water-Reducing Admixture: ASTM C494/C494M, Type F.

          - High-Range, Water-Reducing and -Retarding Admixture: ASTM C494/C494M, Type G.

          - Plasticizing and Retarding Admixture: ASTM C1017/C1017M, Type II.

Retain "Set-Accelerating Corrosion-Inhibiting Admixture" Subparagraph below if set-accelerating corrosion inhibitors are required. Set-accelerating products are usually calcium nitrite-based admixtures and comply with ASTM C494/C494M, Type C.

          - Set-Accelerating Corrosion-Inhibiting Admixture: Commercially formulated, anodic inhibitor or mixed cathodic and anodic inhibitor; capable of forming a protective barrier and minimizing chloride reactions with steel reinforcement in concrete and complying with ASTM C494/C494M, Type C.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Non-Set-Accelerating Corrosion-Inhibiting Admixture" Subparagraph below if corrosion inhibitors that do not affect concrete setting time are required.

          - Non-Set-Accelerating Corrosion-Inhibiting Admixture: Commercially formulated, non-set-accelerating, anodic inhibitor or mixed cathodic and anodic inhibitor; capable of forming a protective barrier and minimizing chloride reactions with steel reinforcement in concrete.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Permeability-Reducing Admixture" Subparagraph below if required. Consider actual need, budget, and expected results. If retained, insert specific requirement for permeability-reducing admixture in applicable paragraph under "Concrete Mixtures" Article. See the Evaluations.

          - Permeability-Reducing Admixture: ASTM C494/C494M, Type S, hydrophilic, permeability-reducing crystalline admixture, capable of reducing water absorption of concrete exposed to hydrostatic pressure (PRAH).

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Permeability: No leakage when tested in accordance with U.S. Army Corps of Engineers CRD C48 at a hydraulic pressure of 200 psi (1.28 MPa) for 14 days.

Retain "Color Pigment" Paragraph below for integrally colored concrete.

        - Color Pigment: ASTM C979/C979M, synthetic mineral-oxide pigments, color stable,[ free of carbon black,] nonfading, and resistant to lime and other alkalis.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain one of three options in "Color" Subparagraph below.

          - Color: [As indicated by manufacturer's designation] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

        - Water and Water Used to Make Ice: ASTM C94/C94M, potable [or] [complying with ASTM C1602/C1602M, including all limits listed in Table 2 and the requirements of paragraph 5.4]

      - FIBER REINFORCEMENT

Retain "Carbon-Steel-Wire Fiber" or "Carbon-Steel Cut Sheet Fiber" Paragraph below if using steel-fiber reinforcement. Retain length of fiber from first set of options and the ratio of length to effective diameter from second set of options for aspect ratio. When using steel-fiber reinforcement for minimum shear resistance, revise retained paragraph to ASTM C1116/C1116M wire with an aspect ratio of not less than 50 and not to exceed 100.

        - Carbon-Steel-Wire Fiber: ASTM A820/A820M, Type 1, cold-drawn wire, deformed, minimum of [1.5 inches (38 mm)] [2 inches (50 mm)] [2.4 inches (60 mm)] <Insert dimension> long, with an aspect ratio of [35 to 40] [45 to 50] [60 to 65] <Insert ratio>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

If retaining "Carbon-Steel-Wire Fiber" Paragraph below, retain length of fiber from first set of options and the ratio of length to effective diameter from second set of options for aspect ratio. When using steel-fiber reinforcement for minimum shear resistance, revise paragraph to ASTM C1116/C1116M wire with an aspect ratio of not less than 50 and not to exceed 100.

        - Carbon-Steel Cut Sheet Fiber: ASTM A820/A820M, Type 2, cut sheet, deformed, minimum of [1.5 inches (38 mm)] [2 inches (50 mm)] [2.4 inches (60 mm)] <Insert dimension> long, and aspect ratio of [35 to 40] [45 to 50] [60 to 65] <Insert ratio>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Synthetic Monofilament Micro-Fiber" or "Synthetic Fibrillated Micro-Fiber" paragraphs below if using synthetic micro-fiber reinforcement. Revise fiber type if inserting polyester or nylon fibers. Monofilament fibers help reduce plastic shrinkage cracking. Manufacturers claim fibrillated fibers also improve hardened concrete properties.

        - Synthetic Monofilament Micro-Fiber: Monofilament polypropylene micro-fibers engineered and designed for use in concrete, complying with ASTM C1116/C1116M, Type III, [1/2 to 1-1/2 inches (13 to 38 mm)] [1 to 2-1/4 inches (25 to 57 mm)] <Insert dimensions> long.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Synthetic Fibrillated Micro-Fiber: Fibrillated polypropylene micro-fibers engineered and designed for use in concrete, complying with ASTM C1116/C1116M, Type III, [1/2 to 1-1/2 inches (13 to 38 mm)] [1 to 2-1/4 inches (25 to 57 mm)] <Insert dimensions> long.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Manufacturers claim macro-fiber reinforcement can be used for crack control and may substitute for welded-wire reinforcement and some light steel-reinforcement bar configurations in slabs-on-ground and composite slabs. The quantity of fiber required to be inserted into the concrete is calculated by a structural engineer, based on criteria furnished by the fiber manufacturer.

        - Synthetic Macro-Fiber: Synthetic macro-fibers engineered and designed for use in concrete, complying with ASTM C1116/C1116M, Type III, [1 to 2-1/4 inches (25 to 57 mm)] <Insert dimensions> long.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

      - VAPOR RETARDERS

Retain "Sheet Vapor Retarder Class A" or "Sheet Vapor Retarder Class C" Paragraph below if a nonbituminous water vapor retarder is required. Class A has the highest tensile strength and puncture resistance. Class C has the lowest. There are no manufactures of Class B vapor retarders.

Retain option and insert water-vapor permeance in "Sheet Vapor Retarder Class A" Paragraph below if requiring less than the 0.1 perms permitted by ASTM E1745. See the Evaluations. If inserting lower perm rating in option, coordinate with manufacturers and products selected.

        - Sheet Vapor Retarder, Class A: ASTM E1745, Class A[, except with maximum water-vapor permeance of] <Insert rating>; not less than 10 mils (0.25 mm) thick. Include manufacturer's recommended adhesive or pressure-sensitive tape.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain option and insert water-vapor permeance in "Sheet Vapor Retarder Class C" Paragraph below if requiring less than the 0.1 perms permitted by ASTM E1745. See the Evaluations. If inserting lower perm rating in option, coordinate with manufacturers and products selected.

        - Sheet Vapor Retarder, Class C: ASTM E1745, Class C[, except with maximum water-vapor permeance of] <Insert rating>; not less than 10 mils (0.25 mm) thick. Include manufacturer's recommended adhesive or pressure-sensitive joint tape.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Sheet Vapor Retarder/Termite Barrier" Paragraph below if vapor retarder/termite barrier is required.

        - Sheet Vapor Retarder/Termite Barrier: ASTM E1745, Class A, except with maximum water-vapor permeance of 0.03 perms; complying with ICC AC380. Include manufacturer's recommended adhesive or pressure-sensitive tape.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Low-Temperature Flexibility: Pass at minus 15 deg F (minus 26 deg C); ASTM D146/D146M.

          - Puncture Resistance: 224 lbf (996 N) minimum; ASTM E154/E154M.

          - Water Absorption: 0.1 percent weight-gain maximum after 48-hour immersion at 70 deg F (21 deg C); ASTM D570.

          - Hydrostatic-Head Resistance: 231 feet (70 m) minimum; ASTM D5385.

Retain "Bituminous Vapor Retarder" Paragraph below if bituminous vapor retarder is required.

        - Bituminous Vapor Retarder: ASTM E1993/E1993M, 110-mil- (2.8-mm-) thick, semiflexible, seven-ply sheet membrane, consisting of reinforced core and carrier sheet with fortified asphalt layers, protective weather coating, and removable plastic release liner. Furnish manufacturer's accessories, including bonding asphalt, pointing mastics, and self-adhering joint tape.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Water-Vapor Permeance: 0.0011 grains/h x sq. ft. x inches Hg (0.063 ng/Pa x s x sq. m) when tested in accordance with ASTM E154/E154M.

          - Tensile Strength: 156 lbf/inch (27.35 kN/m) when tested in accordance with ASTM E154/E154M.

          - Puncture Resistance: 140 lbf (662N) when tested in accordance with ASTM E154/E154M.

      - FLOOR AND SLAB TREATMENTS

Retain this article if one or more floor and slab treatments are required.

        - Slip-Resistive Emery Aggregate Finish: Factory-graded, packaged, rustproof, nonglazing, abrasive, crushed emery aggregate containing not less than 50 percent aluminum oxide and not less than 20 percent ferric oxide; unaffected by freezing, moisture, and cleaning materials with 100 percent passing [3/8-inch (10-mm)] [No. 4 (4.75-mm)] [No. 8 (2.36-mm)] <Insert size or gradation> sieve.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Slip-Resistive Aluminum Granule Finish: Factory-graded, packaged, rustproof, nonglazing, abrasive aggregate of not less than 95 percent fused aluminum-oxide granules.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Emery Dry-Shake Floor Hardener: [Pigmented] [Unpigmented], factory-packaged, dry combination of portland cement, graded emery aggregate, and plasticizing admixture; with emery aggregate consisting of no less than 60 percent of total aggregate content.

Retain one of three options in "Color" Subparagraph below if retaining first option in "Emery Dry-Shake Floor Hardener" Paragraph above.

          - Color: [As indicated by manufacturer's designation] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

        - Metallic Dry-Shake Floor Hardener: [Pigmented] [Unpigmented], factory-packaged, dry combination of portland cement, graded metallic aggregate, rust inhibitors, and plasticizing admixture; with metallic aggregate consisting of no less than 65 percent of total aggregate content.

Retain one of three options in "Color" Subparagraph below if retaining first option in "Metallic Dry-Shake Floor Hardener" Paragraph above.

          - Color: [As indicated by manufacturer's designation] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

Verify suitability of unpigmented mineral dry-shake floor hardener with manufacturer if air content of concrete exceeds 3 percent.

        - Unpigmented Mineral Dry-Shake Floor Hardener: Factory-packaged dry combination of portland cement, graded quartz aggregate, and plasticizing admixture.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Verify suitability of pigmented mineral dry-shake floor hardener with manufacturer if air content of concrete exceeds 3 percent.

        - Pigmented Mineral Dry-Shake Floor Hardener: Factory-packaged, dry combination of portland cement, graded quartz aggregate, color pigments, and plasticizing admixture. Use color pigments that are finely ground, nonfading mineral oxides interground with cement.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain one of three options in "Color" Subparagraph below.

          - Color: [As indicated by manufacturer's designation] [Match Architect's sample] [As selected by Architect from manufacturer's full range].

      - LIQUID FLOOR TREATMENTS

Penetrating liquid floor treatment in "Penetrating Liquid Floor Treatment" Paragraph below is commonly applied to harden and densify floors of warehouses and distribution facilities, imparting a clear satin sheen to finished floor. Pigmented products may also be available. Although formulations vary, manufacturers claim these nonfluosilicate liquids improve abrasion and chemical resistance and dustproof concrete surface. When approved by manufacturers, these products may be installed over mineral dry-shake floor hardeners or integrally colored concrete.

        - Penetrating Liquid Floor Treatment: Clear, chemically reactive, waterborne solution of inorganic silicate or siliconate materials and proprietary components; odorless; that penetrates, hardens, and densifies concrete surfaces.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - <Double click to insert sustainable design text for floor treatment products.>

      - CURING MATERIALS

Evaporation retarders temporarily reduce moisture loss from concrete surfaces awaiting finishing in hot, dry, and windy conditions. Evaporation retarders are not curing compounds.

        - Evaporation Retarder: Waterborne, monomolecular film forming, manufactured for application to fresh concrete.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain applicable curing aids and materials from remaining paragraphs.

        - Absorptive Cover: AASHTO M 182, Class 2, burlap cloth made from jute or kenaf, weighing approximately 9 oz./sq. yd. (305 g/sq. m) when dry.

        - Moisture-Retaining Cover: ASTM C171, polyethylene film burlap-polyethylene sheet.

          - Color:

            - Ambient Temperature Below 50 deg F (10 deg C): Black.

            - Ambient Temperature between 50 deg F (10 deg C) and 85 deg F (29 deg C): Any color.

            - Ambient Temperature Above 85 deg F (29 deg C): White.

        - Curing Paper: 8-feet- (2438-mm-) wide paper, consisting of two layers of fibered kraft paper laminated with double coating of asphalt.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Water: Potable or complying with ASTM C1602/C1602M.

Retain "Clear, Waterborne, Membrane-Forming, Dissipating Curing Compound" Paragraph below if a dissipating-type, waterborne, membrane-forming curing compound is required. Although the EPA mandates maximum VOC emissions of 350 g/L for curing compounds, verify VOC emission limits of authorities having jurisdiction. If slow breakdown of curing membrane could interfere with bonding of floor coverings, retain "Removal" Subparagraph in "Concrete Curing" Article in Part 3.

        - Clear, Waterborne, Membrane-Forming, Dissipating Curing Compound: ASTM C309, Type 1, Class B.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Clear, Waterborne, Membrane-Forming, Nondissipating Curing Compound" Paragraph below if a nondissipating-type, waterborne, membrane-forming curing compound with minimal solids content is required. Although the EPA mandates maximum VOC emissions of 350 g/L for curing compounds, verify VOC emission limits of authorities having jurisdiction. Retain option if applicable.

        - Clear, Waterborne, Membrane-Forming, Nondissipating Curing Compound: ASTM C309, Type 1, Class B[, certified by curing compound manufacturer to not interfere with bonding of floor covering].

Verify with manufacturer that retained products have been tested against interference with bonding of floor covering.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Clear, Waterborne, Membrane-Forming, Curing Compound" Paragraph below if a nondissipating-type, waterborne, membrane-forming, curing compound with a higher solids content is required. This product will partially seal the concrete. Although the EPA mandates maximum VOC emissions of 350 g/L for curing compounds, verify VOC emission limits of authorities having jurisdiction. Retain option if applicable.

        - Clear, Waterborne, Membrane-Forming, Curing Compound: ASTM C309, Type 1, Class B, 18 to 25 percent solids, nondissipating[, certified by curing compound manufacturer to not interfere with bonding of floor covering].

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Clear, Solvent-Borne, Membrane-Forming, Curing and Sealing Compound" Paragraph below if a clear, nonyellowing, solvent-borne, membrane-forming curing and sealing compound is required. Although the EPA mandates maximum VOC emissions of 700 g/L for curing and sealing compounds, verify VOC emission limits of authorities having jurisdiction.

        - Clear, Solvent-Borne, Membrane-Forming, Curing and Sealing Compound: ASTM C1315, Type 1, Class A.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - <Double click to insert sustainable design text for floor treatment products.>

Retain "Clear, Waterborne, Membrane-Forming, Curing and Sealing Compound" Paragraph below if a clear, nonyellowing, waterborne, membrane-forming, curing and sealing compound is required. Although the EPA mandates maximum VOC emissions of 700 g/L for curing and sealing compounds, verify VOC emission limits of authorities having jurisdiction.

        - Clear, Waterborne, Membrane-Forming, Curing and Sealing Compound: ASTM C1315, Type 1, Class A.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - <Double click to insert sustainable design text for floor treatment products.>

      - RELATED MATERIALS

Retain one or all options in "Expansion- and Isolation-Joint-Filler Strips" Paragraph below. Joint-filler strips are used in floor isolation joints.

        - Expansion- and Isolation-Joint-Filler Strips: [ASTM D1751, asphalt-saturated cellulosic fiber] [or] [ASTM D1752, cork or self-expanding cork].

Retain one of two options in "Semirigid Joint Filler" Paragraph below if semirigid joint filler is required to fill joints and support edges of trafficked control and construction joints.

        - Semirigid Joint Filler: Two-component, semirigid, 100 percent solids, [epoxy resin with a Type A shore durometer hardness of 80] [aromatic polyurea with a Type A shore durometer hardness range of 90 to 95] in accordance with ASTM D2240.

Bonding agent in "Bonding Agent" Paragraph below may be used directly from container or as an admixture in cement or sand-cement slurries and rubbing grout.

        - Bonding Agent: ASTM C1059/C1059M, Type II, nonredispersible, acrylic emulsion or styrene butadiene.

        - Epoxy Bonding Adhesive: ASTM C881, two-component epoxy resin, capable of humid curing and bonding to damp surfaces, of class suitable for application temperature and of grade and class to suit requirements, and as follows:

Retain types from two options in subparagraph below, based on service loadings.

          - [Types I and II, nonload bearing] [Types IV and V, load bearing], for bonding hardened or freshly mixed concrete to hardened concrete.

Retain "Floor Slab Protective Covering" Paragraph below if required to protect concrete floor surfaces scheduled to be polished or other special floor finishes.

        - Floor Slab Protective Covering: 8-feet- (2438-mm-) wide cellulose fabric.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

      - REPAIR MATERIALS

Retain "Repair Underlayment" Paragraph below as a repair material for floor and slab areas beneath floor coverings.

        - Repair Underlayment: Cement-based, polymer-modified, self-leveling product that can be applied in thicknesses from 1/8 inch (3 mm) and that can be feathered at edges to match adjacent floor elevations.

          - Cement Binder: ASTM C150/C150M portland cement or hydraulic or blended hydraulic cement, as defined in ASTM C219.

          - Primer: Product of underlayment manufacturer recommended for substrate, conditions, and application.

          - Aggregate: Well-graded, washed gravel, 1/8 to 1/4 inch (3 to 6 mm) or coarse sand, as recommended by underlayment manufacturer.

          - Compressive Strength: Not less than [4100 psi (29 MPa)] <Insert strength> at 28 days when tested in accordance with ASTM C109/C109M.

Retain "Repair Overlayment" Paragraph below as a repair material for floor or slab areas remaining exposed and not receiving floor coverings.

        - Repair Overlayment: Cement-based, polymer-modified, self-leveling product that can be applied in thicknesses from 1/4 inch (6 mm) and that can be filled in over a scarified surface to match adjacent floor elevations.

          - Cement Binder: ASTM C150/C150M portland cement or hydraulic or blended hydraulic cement, as defined in ASTM C219.

          - Primer: Product of topping manufacturer recommended for substrate, conditions, and application.

          - Aggregate: Well-graded, washed gravel, 1/8 to 1/4 inch (3.2 to 6 mm) or coarse sand as recommended by topping manufacturer.

          - Compressive Strength: Not less than [5000 psi (34.5 MPa)] <Insert strength> at 28 days when tested in accordance with ASTM C109/C109M.

      - CONCRETE MIXTURES, GENERAL

        - Prepare design mixtures for each type and strength of concrete, proportioned on the basis of laboratory trial mixture or field test data, or both, in accordance with ACI 301 (ACI 301M).

          - Use a qualified testing agency for preparing and reporting proposed mixture designs, based on laboratory trial mixtures.

In "Cementitious Materials" Paragraph below, neither ACI 301 (ACI 301M) nor ACI 318 (ACI 318M) limit amount of cementitious materials that can replace portland cement unless concrete is exposed to deicing chemicals. Identify parts of building or structure affected by these limits unless extending them to all concrete.

        - Cementitious Materials: Limit percentage, by weight, of cementitious materials other than portland cement in concrete as follows:

Percentages in five subparagraphs below repeat ACI 301 (ACI 301M), Table 4.2.1.1(b) limits for concrete Exposure Class F3. Revise to suit Project.

          - Fly Ash or Other Pozzolans: 25 percent by mass.

          - Slag Cement: 50 percent by mass.

Limits of silica fume alone or in combination with other cementitious materials below are based on ACI 301 (ACI 301M) and ACI 318 (ACI 318M).

          - Silica Fume: 10 percent by mass.

          - Total of Fly Ash or Other Pozzolans, Slag Cement, and Silica Fume: 50 percent by mass, with fly ash or pozzolans not exceeding 25 percent by mass and silica fume not exceeding 10 percent by mass.

          - Total of Fly Ash or Other Pozzolans and Silica Fume: 35 percent by mass with fly ash or pozzolans not exceeding 25 percent by mass and silica fume not exceeding 10 percent by mass.

        - Admixtures: Use admixtures in accordance with manufacturer's written instructions.

Use of chemical admixtures is typically the decision of the Contractor and concrete manufacturer. If any chemical admixture is required by the design team, consider inserting specific requirements in applicable paragraph in "Concrete Mixtures" Article.

Revise first four subparagraphs below to suit Project; delete if not required.

          - Use [water-reducing] [high-range water-reducing] [or] [plasticizing] admixture in concrete, as required, for placement and workability.

          - Use water-reducing and -retarding admixture when required by high temperatures, low humidity, or other adverse placement conditions.

          - Use water-reducing admixture in [pumped concrete,] [concrete for heavy-use industrial slabs] [concrete for parking structure slabs,] [and] [concrete with a w/cm below 0.50].

Insert locations and dosage of corrosion-inhibiting admixture in first subparagraph below if required.

          - Use corrosion-inhibiting admixture in concrete mixtures where indicated.

Insert locations and dosage of permeability-reducing admixture in subparagraph below if required.

          - Use permeability-reducing admixture in concrete mixtures where indicated.

Retain "Color Pigment" Paragraph below if integrally colored concrete is required, and indicate locations here or on Drawings.

        - Color Pigment: Add color pigment to concrete mixture in accordance with manufacturer's written instructions and to result in hardened concrete color consistent with approved mockup.

      - CONCRETE MIXTURES

This article contains examples of building elements that often need different concrete mixtures. Revise, consolidate, or add other building elements if more concrete mixtures are required. ASTM C94/C94M requires each "class" of concrete mixture be assigned a designation to facilitate identification of each concrete mixture delivered to the Project, and that this designation be identified on the delivery ticket. "Class" designations used below are examples only. Revise to suit Project. Do not duplicate "Class" designations used in Section 033300 "Architectural Concrete."

Consider inserting minimum cementitious material content for mix designs.

        - Class [A] <Insert designation>: Normal-weight concrete used for footings, grade beams, and tie beams.

          - Exposure Class: ACI 318 (ACI 318M) [F0] [F1] [F2] [F3] [S0] [S1] [S2] [S3] [W0] [W1] [C0] [C1] [C2].

Retain strength from first five options in "Minimum Compressive Strength" Subparagraph below, or revise to suit Project. Coordinate compressive strength with w/cm if concrete is subject to special exposure conditions or sulfate exposure, as identified in ACI 318 (ACI 318M).

          - Minimum Compressive Strength: [5000 psi (34.5 MPa)] [4500 psi (31 MPa)] [4000 psi (27.6 MPa)] [3500 psi (24.1 MPa)] [3000 psi (20.7 MPa)] [As indicated] <Insert strength> at 28 days.

Retain one option in "Maximum w/cm" Subparagraph below, revise subparagraph to suit Project, or delete subparagraph if in-service durability conditions are benign and limits on w/cm are not required. Coordinate w/cm with compressive strength. See the Evaluations for discussion.

          - Maximum w/cm: [0.50] [0.45] [0.40] <Insert number>.

Consider deleting "Slump Limit" Subparagraph below and allow the Contractor to select a target slump based on ASTM C143/C143M, as permitted under ACI 301 (ACI 301M). If retaining "Slump Limit" Subparagraph, retain slump limit from three options or revise to suit Project.

          - Slump Limit: [4 inches (100 mm), plus or minus 1 inch (25 mm)] [5 inches (125 mm), plus or minus 1 inch (25 mm)] [8 inches (200 mm), plus or minus 1 inch (25 mm) for concrete with verified slump of 3 inches (75 mm), plus or minus 1 inch (25 mm)before adding high-range water-reducing admixture or plasticizing admixture at Project site] <Insert limits>.

"Slump Flow Limit" Subparagraph below is for self-consolidating concrete. Consider deleting and allow the Contractor to select a target slump flow based on ASTM C1611/C1611M, as permitted under ACI 301 (ACI 301M). If retaining "Slump Flow Limit" Subparagraph, retain slump flow limit from two options, or revise to suit Project.

          - Slump Flow Limit: [22 inches (550 mm), plus or minus 1.5 inches (40 mm)] [30 inches (762 mm), plus or minus 2.5 inches (65 mm)] <Insert limits>.

          - Air Content:

Options in first two subparagraphs below are examples only. Revise to suite Project. See ACI 301 (ACI 301M), Table 4.2.2.7(b)1 for air content for additional Exposure Classes and aggregate sizes.

            - Exposure Class F1: [5.0 percent, plus or minus 1.5 percent at point of delivery for concrete containing 3/4-inch (19-mm) nominal maximum aggregate size] [4.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-inch (25-mm) nominal maximum aggregate size] [4.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-1/2-inch (38-mm) nominal maximum aggregate size].

            - Exposure Classes F2 and F3: [6 percent, plus or minus 1.5 percent at point of delivery for concrete containing 3/4-inch (19-mm) nominal maximum aggregate size] [6 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-inch (25-mm) nominal maximum aggregate size] [5.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-1/2-inch (38-mm) nominal maximum aggregate size].

Retain appropriate option in subparagraph below for chloride limits. Percentages below repeat ACI 318 (ACI 318M) limits. First option is for Exposure Class C0; second option is for Exposure Class C1; third option is for Exposure Class C2. ACI 301 (ACI 301M) and ACI 318 (ACI 318M) express this percentage by weight of cement, not cementitious material.

          - Limit water-soluble, chloride-ion content in hardened concrete to [1.00] [0.30] [0.15] <Insert number> percent by weight of cement.

        - Class [B] <Insert designation>: Normal-weight concrete used for foundation walls.

          - Exposure Class: ACI 318 (ACI 318M) [F0] [F1] [F2] [F3] [S0] [S1] [S2] [S3] [W0] [W1] [C0] [C1] [C2].

Retain strength from first five options in "Minimum Compressive Strength" Subparagraph below, or revise to suit Project. Coordinate compressive strength with w/cm if concrete is subject to special exposure conditions or sulfate exposure, as identified in ACI 318 (ACI 318M).

          - Minimum Compressive Strength: [5000 psi (34.5 MPa)] [4500 psi (31 MPa)] [4000 psi (27.6 MPa)] [3500 psi (24.1 MPa)] [3000 psi (20.7 MPa)] [As indicated] <Insert strength> at 28 days.

Retain w/cm from three options in "Maximum w/cm" Subparagraph below, revise to suit Project, or delete if in-service durability conditions are benign and limits on w/c ratio are not required. Coordinate w/cm with compressive strength. See the Evaluations for discussion.

          - Maximum w/cm: [0.50] [0.45] [0.40] <Insert number>.

Consider deleting "Slump Limit" Subparagraph below and allow the Contractor to select a target slump based on ASTM C143/C143M, as permitted under ACI 301 (ACI 301M). If retaining "Slump Limit" Subparagraph, retain slump limit from three options in, or revise to suit Project.

          - Slump Limit: [4 inches (100 mm), plus or minus 1 inch (25 mm)] [5 inches (125 mm), plus or minus 1 inch (25 mm)] [8 inches (200 mm), plus or minus 1 inch (25 mm) for concrete with verified slump of 3 inches ((75 mm),) plus or minus 1 inch ((25 mm),)before adding high-range water-reducing admixture or plasticizing admixture at Project site] <Insert limits>.

"Slump Flow Limit" Subparagraph below is for self-consolidating concrete. Consider deleting and allow the Contractor to select a target slump flow based on ASTM C1611/C1611M, as permitted under ACI 301 (ACI 301M). If retaining "Slump Flow Limit" Subparagraph, retain slump flow limit from two options, or revise to suit Project.

          - Slump Flow Limit: [22 inches (550 mm), plus or minus 1.5 inches (40 mm)] [30 inches (762 mm), plus or minus 2.5 inches (65 mm)] <Insert limits>.

          - Air Content:

Options in first two subparagraphs are examples only. Revise to suite Project. See ACI 301 (ACI 301M), Table 4.2.2.7(b)1 for air content for additional Exposure Classes and aggregate sizes.

            - Exposure Class F1: [5.0 percent, plus or minus 1.5 percent at point of delivery for concrete containing 3/4-inch (19-mm) nominal maximum aggregate size] [4.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-inch (25-mm) nominal maximum aggregate size] [4.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-1/2-inch (38-mm) nominal maximum aggregate size].

            - Exposure Classes F2 and F3: [6 percent, plus or minus 1.5 percent at point of delivery for concrete containing 3/4-inch (19-mm) nominal maximum aggregate size] [6 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-inch (25-mm) nominal maximum aggregate size] [5.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-1/2-inch (38-mm) nominal maximum aggregate size].

Retain appropriate option in subparagraph below for chloride limits. Percentages below repeat ACI 318 (ACI 318M) limits. First option is for Exposure Class C0; second option is for Exposure Class C1; third option is for Exposure Class C2. ACI 301 (ACI 301M) and ACI 318 (ACI 318M) express this percentage by weight of cement, not cementitious material.

          - Limit water-soluble, chloride-ion content in hardened concrete to [1.00] [0.30] [0.15] <Insert number> percent by weight of cement.

        - Class [C] <Insert designation>: Normal-weight concrete used for interior slabs-on-ground.

          - Exposure Class: ACI 318 (ACI 318M) [F0] [S0] [S1] [S2] [S3] [W0] [W1] [C0] [C1] [C2].

Retain strength from first five options in "Minimum Compressive Strength" Subparagraph below, or revise to suit Project.

          - Minimum Compressive Strength: [5000 psi (34.5 MPa)] [4500 psi (31 MPa)] [4000 psi (27.6 MPa)] [3500 psi (24.1 MPa)] [3000 psi (20.7 MPa)] [As indicated] <Insert strength> at 28 days.

Retain w/cm from three options in "Maximum w/cm" Subparagraph below, revise to suit Project, or delete if in-service durability conditions are benign and limits on w/c ratio are not required. Coordinate w/cm with compressive strength. See the Evaluations for discussion.

          - Maximum w/cm: [0.50] [0.45] [0.40] <Insert number>.

Retain one of four options in "Minimum Cementitious Materials Content" Subparagraph below, or revise to suit Project. Options are based on minimum requirements set by ACI 301 (ACI 301M) for floors and relate to nominal maximum aggregate sizes 1-1/2, 1, 3/4, and 3/8 inch (38, 25, 19 mm, and 10 mm), respectively.

          - Minimum Cementitious Materials Content: [470 lb/cu. yd. (279 kg/cu. m)] [520 lb/cu. yd. (309 kg/cu. m)] [540 lb/cu. yd. (320 kg/cu. m)] [610 lb/cu. yd. (362 kg/cu. m)].

Consider deleting "Slump Limit" Subparagraph below and allow the Contractor to select a target slump based on ASTM C143/C143M, as permitted under ACI 301 (ACI 301M). If retaining "Slump Limit" Subparagraph, retain slump limit from three options, or revise to suit Project. Consider only including slump limits where slabs-on-ground are subject to special exposure conditions or injurious sulfate exposure.

          - Slump Limit: [4 inches (100 mm), plus or minus 1 inch (25 mm)] [5 inches (125 mm), plus or minus 1 inch (25 mm)] [8 inches (200 mm), plus or minus 1 inch (25 mm) for concrete with verified slump of 3 inches ((75 mm),) plus or minus 1 inch ((25 mm),)before adding high-range water-reducing admixture or plasticizing admixture at Project site] <Insert limits>.

"Slump Flow Limit" Subparagraph below is for self-consolidating concrete. Consider deleting and allow the Contractor to select a target slump flow based on ASTM C1611/C1611M, as permitted under ACI 301 (ACI 301M). If retaining "Slump Flow Limit" Subparagraph, retain slump flow limit from two options, or revise to suit Project.

          - Slump Flow Limit: [22 inches (550 mm), plus or minus 1.5 inches (40 mm)] [30 inches (762 mm), plus or minus 2.5 inches (65 mm)] <Insert limits>.

          - Air Content:

            - Do not use an air-entraining admixture or allow total air content to exceed 3 percent for concrete used in trowel-finished floors.

Retain appropriate option in first subparagraph below for chloride limits. Percentages below repeat ACI 318 (ACI 318M) limits. First option is for Exposure Class C0; second option is for Exposure Class C1; third option is for Exposure Class C2. ACI 301 (ACI 301M) and ACI 318 (ACI 318M) express this percentage by weight of cement, not cementitious material.

          - Limit water-soluble, chloride-ion content in hardened concrete to [1.00] [0.30] [0.15] <Insert number> percent by weight of cement.

Retain "Steel-Fiber Reinforcement" Subparagraph below if steel-fiber reinforcement is used. Indicate location, on Drawings, of concrete using steel fiber. Revise application rate to suit Project.

          - Steel-Fiber Reinforcement: Add to concrete mixture, in accordance with manufacturer's written instructions, at a rate of [50 lb/cu. yd. (29.7 kg/cu. m)] <Insert weight>.

Synthetic-micro-fiber dosage rates in "Synthetic Micro-Fiber" Subparagraph below reflect typical recommendations of manufacturers. Retain first option for minimum dosage of synthetic micro-fiber used for reducing plastic shrinkage cracking. Retain second option or increase dosage for synthetic micro-fiber used for improving hardened concrete properties.

          - Synthetic Micro-Fiber: Uniformly disperse in concrete mixture at manufacturer's recommended rate, but not less than a rate of [1.0 lb/cu. yd. (0.60 kg/cu. m)] [1.5 lb/cu. yd. (0.90 kg/cu. m)] <Insert dosage>.

Synthetic-macro-fiber dosage rates in "Synthetic Macro-Fiber" Subparagraph below are examples only; verify minimum dosage rates with manufacturer.

          - Synthetic Macro-Fiber: Uniformly disperse in concrete mixture at manufacturer's recommended rate, but not less than a rate of [4.0 lb/cu. yd. (2.4 kg/cu. m)] [5 lb/cu. yd. (3 kg/cu. m)] <Insert dosage>.

Retain "Class D" Paragraph below if normal-weight concrete is used. Suspended slabs include formed concrete slabs, post-tensioned concrete slabs, and composite or noncomposite concrete slabs on metal deck, classified by ACI 302.1R as single-course floors or base slabs of two-course floors. If Project has more than one type of suspended slab with different properties, indicate location of each on Drawings.

        - Class [D] <Insert designation>: Normal-weight concrete used for interior suspended slabs.

          - Exposure Class: ACI 318 (ACI 318M) [F0] [S0] [S1] [S2] [S3] [W0] [W1] [C0] [C1] [C2].

Retain strength from first five options in "Minimum Compressive Strength" Subparagraph below, or revise to suit Project.

          - Minimum Compressive Strength: [5000 psi (34.5 MPa)] [4500 psi (31 MPa)] [4000 psi (27.6 MPa)] [3500 psi (24.1 MPa)] [3000 psi (20.7 MPa)] <Insert strength> [As indicated] at 28 days.

Retain w/cm from three options in "Maximum w/cm" Subparagraph below, revise to suit Project, or delete if in-service durability conditions are benign and limits on w/cm are not required. Coordinate w/cm with compressive strength. See the Evaluations for discussion.

          - Maximum w/cm: [0.50] [0.45] [0.40] <Insert number>.

Retain one of four options in "Minimum Cementitious Materials Content" Subparagraph below, or revise to suit Project. Options are based on minimum requirements set by ACI 301 (ACI 301M) for floors and relate to nominal maximum aggregate sizes 1-1/2, 1, 3/4, and 3/8 inch (38, 25, 19 mm, and 10 mm), respectively.

          - Minimum Cementitious Materials Content: [470 lb/cu. yd. (279 kg/cu. m)] [520 lb/cu. yd. (309 kg/cu. m)] [540 lb/cu. yd. (320 kg/cu. m)] [610 lb/cu. yd. (362 kg/cu. m)].

Consider deleting "Slump Limit" Subparagraph below and allow the Contractor to select a target slump based on ASTM C143/C143M, as permitted under ACI 301 (ACI 301M). If retaining "Slump Limit" Subparagraph, retain slump limit from three options in, or revise to suit Project. Consider only including slump limits where suspended slabs are subject to special exposure conditions or injurious sulfate exposure.

          - Slump Limit: [4 inches (100 mm), plus or minus 1 inch (25 mm)] [5 inches (125 mm), plus or minus 1 inch (25 mm)] [8 inches (200 mm), plus or minus 1 inch (25 mm) for concrete with verified slump of 3 inches ((75 mm),) plus or minus 1 inch ((25 mm),)before adding high-range water-reducing admixture or plasticizing admixture at Project site] <Insert limits>.

"Slump Flow" Subparagraph below is for self-consolidating concrete. Consider deleting and allow the Contractor to select a target slump flow based on ASTM C1611/C1611M, as permitted under ACI 301 (ACI 301M). If retaining "Slump Flow Limit" Subparagraph, retain slump flow limit from two options, or revise to suit Project.

          - Slump Flow Limit: [22 inches (550 mm), plus or minus 1.5 inches (40 mm)] [30 inches (762 mm), plus or minus 2.5 inches (65 mm)] <Insert limits>.

          - Air Content:

            - Do not use an air-entraining admixture or allow total air content to exceed 3 percent for concrete used in trowel-finished floors.

Retain appropriate option in first subparagraph below for chloride limits. Percentages below repeat ACI 318 (ACI 318M) limits. First option is for Exposure Class C0; second option is for Exposure Class C1; third option is for Exposure Class C2. ACI 301 (ACI 301M) and ACI 318 (ACI 318M) express this percentage by weight of cement, not cementitious material.

          - Limit water-soluble, chloride-ion content in hardened concrete to [1.00] [0.30] [0.15] <Insert number> percent by weight of cement.

Retain "Steel-Fiber Reinforcement" Subparagraph below if steel-fiber reinforcement is used. Indicate location, on Drawings, of concrete using steel fiber. Revise application rate to suit Project.

          - Steel-Fiber Reinforcement: Add to concrete mixture, in accordance with manufacturer's written instructions, at a rate of [50 lb/cu. yd. (29.7 kg/cu. m)] <Insert weight>.

Synthetic-micro-fiber dosage rates in "Synthetic Micro-Fiber" Subparagraph below reflect typical recommendations of manufacturers. Retain first option for minimum dosage of synthetic micro-fiber used for reducing plastic shrinkage cracking. Retain second option or increase dosage for synthetic micro-fiber used for improving hardened concrete properties.

          - Synthetic Micro-Fiber: Uniformly disperse in concrete mixture at manufacturer's recommended rate, but not less than a rate of [1.0 lb/cu. yd. (0.60 kg/cu. m)] [1.5 lb/cu. yd. (0.90 kg/cu. m)] <Insert dosage>.

Synthetic-macro-fiber dosage rates in "Synthetic Macro-Fiber" Subparagraph below are examples only; verify minimum dosage rates by structural analysis and with manufacturer.

          - Synthetic Macro-Fiber: Uniformly disperse in concrete mixture at manufacturer's recommended rate, but not less than a rate of [4.0 lb/cu. yd. (2.4 kg/cu. m)] [5 lb/cu. yd. (3 kg/cu. m)] <Insert dosage>.

Retain "Class E" Paragraph below if normal-weight structural concrete is used. Coordinate requirements with lightweight aggregate supplier, structural engineer, and, if applicable, UL design limits.

        - Class [E] <Insert designation>: Structural lightweight concrete used for interior suspended slabs.

          - Exposure Class: ACI 318 (ACI 318M) [F0] [S0] [S1] [S2] [S3] [W0] [W1] [C0] [C1] [C2].

Retain strength from first five options in "Minimum Compressive Strength" Subparagraph below, or revise to suit Project.

          - Minimum Compressive Strength: [5000 psi (34.5 MPa)] [4500 psi (31 MPa)] [4000 psi (27.6 MPa)] [3500 psi (24.1 MPa)] [3000 psi (20.7 MPa)] <Insert strength> [As indicated] at 28 days.

Retain one of three options in "Calculated Equilibrium Unit Weight" Subparagraph below, or revise values or unit weight terminology. "Calculated equilibrium unit weight" is the basis preferred by the Expanded Shale Clay and Slate Institute rather than "oven dry density," which is included in ACI 301 (ACI 301M) for measuring unit weight.

          - Calculated Equilibrium Unit Weight: [115 lb/cu. ft. (1842 kg/cu. m)] [110 lb/cu. ft. (1762 kg/cu. m)] [105 lb/cu. ft. (1682 kg/cu. m)], plus or minus 3 lb/cu. ft. (48.1 kg/cu. m) as determined by ASTM C567/C567M.

Consider deleting "Slump Limit" Subparagraph below and allow the Contractor to select a target slump based on ASTM C143/C143M, as permitted under ACI 301 (ACI 301M). If retaining "Slump Limit" Subparagraph, retain slump limit from three options, or revise to suit Project.

          - Slump Limit: [4 inches (100 mm), plus or minus 1 inch (25 mm)] [5 inches (125 mm), plus or minus 1 inch (25 mm)] [8 inches (200 mm), plus or minus 1 inch (25 mm) for concrete with verified slump of 3 inches ((75 mm),) plus or minus 1 inch ((25 mm),)before adding high-range water-reducing admixture or plasticizing admixture at Project site] <Insert limits>.

"Slump Flow Limit" Subparagraph below is for self-consolidating concrete. Consider deleting and allow the Contractor to select a target slump flow based on ASTM C1611/C1611M, as permitted under ACI 301 (ACI 301M). If retaining "Slump Flow Limit" Subparagraph, retain slump flow limit from two options, or revise to suit Project.

          - Slump Flow Limit: [22 inches (550 mm), plus or minus 1.5 inches (40 mm)] [30 inches (762 mm), plus or minus 2.5 inches (65 mm)] <Insert limits>.

          - Air Content:

            - Do not use an air-entraining admixture or allow total air content to exceed 3 percent for concrete used in trowel-finished floors.

Retain appropriate option in first subparagraph below for chloride limits. Percentages below repeat ACI 318 (ACI 318M) limits. First option is for Exposure Class C0; second option is for Exposure Class C1; third option is for Exposure Class C2. ACI 301 (ACI 301M) and ACI 318 (ACI 318M) express this percentage by weight of cement, not cementitious material.

          - Limit water-soluble, chloride-ion content in hardened concrete to [1.00] [0.30] [0.15] <Insert number> percent by weight of cement.

Retain "Steel-Fiber Reinforcement" Subparagraph below if steel-fiber reinforcement is used. Indicate location, on Drawings, of concrete using steel fiber. Revise application rate to suit Project.

          - Steel-Fiber Reinforcement: Add to concrete mixture, in accordance with manufacturer's written instructions, at a rate of [50 lb/cu. yd. (29.7 kg/cu. m)] <Insert weight>.

Synthetic-micro-fiber dosage rates in "Synthetic Micro-Fiber" Subparagraph below reflect typical recommendations of manufacturers. Retain first option for minimum dosage of synthetic micro-fiber used for reducing plastic shrinkage cracking. Retain second option or increase dosage for synthetic micro-fiber used for improving hardened concrete properties.

          - Synthetic Micro-Fiber: Uniformly disperse in concrete mixture at manufacturer's recommended rate, but not less than a rate of [1.0 lb/cu. yd. (0.60 kg/cu. m)] [1.5 lb/cu. yd. (0.90 kg/cu. m)] <Insert dosage>.

Synthetic-macro-fiber dosage rates in "Synthetic Macro-Fiber" Subparagraph below are examples only; verify minimum dosage rates by structural analysis and with manufacturer.

          - Synthetic Macro-Fiber: Uniformly disperse in concrete mixture at manufacturer's recommended rate, but not less than a rate of [4.0 lb/cu. yd. (2.4 kg/cu. m)] [5 lb/cu. yd. (3 kg/cu. m)] <Insert dosage>.

Retain "Class F" Paragraph below for concrete toppings or concrete underbeds on a base concrete slab or on structural precast concrete. For emery-aggregate and iron-aggregate concrete floor toppings, see Section 035300 "Concrete Topping."

        - Class [F] <Insert designation>: Normal-weight concrete used for concrete toppings.

          - Exposure Class: ACI 318 (ACI 318M) [F0] [F1] [F2] [F3] [S0] [S1] [S2] [S3] [W0] [W1] [C0] [C1] [C2].

Retain strength from first five options in "Minimum Compressive Strength" Subparagraph below, or revise to suit Project.

          - Minimum Compressive Strength: [5000 psi (34.5 MPa)] [4500 psi (31 MPa)] [4000 psi (27.6 MPa)] [3500 psi (24.1 MPa)] [3000 psi (20.7 MPa)] <Insert strength> [As indicated] at 28 days.

Retain one of three options in "Minimum Cementitious Materials Content" Subparagraph below, or revise to suit Project. Options are based on minimum requirements set by ACI 301 (ACI 301M) for floors and relate to nominal maximum aggregate sizes 1-1/2, 1, and 3/4 inch (38, 25, and 19 mm), respectively.

          - Minimum Cementitious Materials Content: [470 lb/cu. yd. (279 kg/cu. m)] [520 lb/cu. yd. (309 kg/cu. m)] [540 lb/cu. yd. (320 kg/cu. m)].

Consider deleting "Slump Limit" Subparagraph below and allow the Contractor to select a target slump based on ASTM C143/C143M, as permitted under ACI 301 (ACI 301M). If retaining "Slump Limit" Subparagraph, retain slump limit from two options, or revise to suit Project.

          - Slump Limit: [4 inches (100 mm)] [5 inches (125 mm)], plus or minus 1 inch (25 mm).

          - Air Content:

Options in first two subparagraphs are examples only. Revise to suite Project. See ACI 301 (ACI 301M), Table 4.2.2.7(b)1 for air content for additional Exposure Classes and aggregate sizes.

            - Exposure Class F1: [5.0 percent, plus or minus 1.5 percent at point of delivery for concrete containing 3/4-inch (19-mm) nominal maximum aggregate size] [4.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-inch (25-mm) nominal maximum aggregate size] [4.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-1/2-inch (38-mm) nominal maximum aggregate size].

            - Exposure Classes F2 and F3: [6 percent, plus or minus 1.5 percent at point of delivery for concrete containing 3/4-inch (19-mm) nominal maximum aggregate size] [6 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-inch (25-mm) nominal maximum aggregate size] [5.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-1/2-inch (38-mm) nominal maximum aggregate size].

Retain appropriate option in first subparagraph below for chloride limits. Percentages below repeat ACI 318 (ACI 318M) limits. First option is for Exposure Class C0; second option is for Exposure Class C1; third option is for Exposure Class C2. ACI 301 (ACI 301M) and ACI 318 (ACI 318M) express this percentage by weight of cement, not cementitious material.

          - Limit water-soluble, chloride-ion content in hardened concrete to [1.00] [0.30] [0.15] <Insert number> percent by weight of cement.

            - Do not use an air-entraining admixture or allow total air content to exceed 3 percent for concrete used in trowel-finished toppings.

Retain "Steel-Fiber Reinforcement" Subparagraph below if steel-fiber reinforcement is used. Indicate location, on Drawings, of concrete using steel fiber. Revise application rate to suit Project.

          - Steel-Fiber Reinforcement: Add to concrete mixture, in accordance with manufacturer's written instructions, at a rate of [50 lb/cu. yd. (29.7 kg/cu. m)] <Insert weight>.

Synthetic-micro-fiber dosage rates in "Synthetic Micro-Fiber" Subparagraph below reflect typical recommendations of manufacturers. Retain first option for minimum dosage of synthetic micro-fiber used for reducing plastic shrinkage cracking. Retain second option or increase dosage for synthetic micro-fiber used for improving hardened concrete properties.

          - Synthetic Micro-Fiber: Uniformly disperse in concrete mixture at manufacturer's recommended rate, but not less than a rate of [1.0 lb/cu. yd. (0.60 kg/cu. m)] [1.5 lb/cu. yd. (0.90 kg/cu. m)] <Insert dosage>.

Synthetic-macro-fiber dosage rates in "Synthetic Macro-Fiber" Subparagraph below are examples only; verify minimum dosage rates with manufacturer.

          - Synthetic Macro-Fiber: Uniformly disperse in concrete mixture at manufacturer's recommended rate, but not less than a rate of [4.0 lb/cu. yd. (2.4 kg/cu. m)] [5 lb/cu. yd. (3 kg/cu. m)] <Insert dosage>.

        - Class [G] <Insert designation>: Normal-weight concrete used for building frame members.

          - Exposure Class: ACI 318 (ACI 318M) [F0] [F1] [F2] [F3] [S0] [S1] [S2] [S3] [W0] [W1] [C0] [C1] [C2].

Retain strength from first five options in "Minimum Compressive Strength" Subparagraph below, or revise to suit Project. Coordinate compressive strength with w/cm if concrete is subject to special exposure conditions or sulfate exposure, as identified in ACI 318 (ACI 318M).

          - Minimum Compressive Strength: [5000 psi (34.5 MPa)] [4500 psi (31 MPa)] [4000 psi (27.6 MPa)] [3500 psi (24.1 MPa)] [3000 psi (20.7 MPa)] <Insert strength> [As indicated] at 28 days.

Retain w/cm from three options in "Maximum w/cm" Subparagraph below, revise to suit Project, or delete if in-service durability conditions are benign and limits on w/cm are not required. Coordinate w/cm with compressive strength. See the Evaluations for discussion.

          - Maximum w/cm: [0.50] [0.45] [0.40] <Insert number>.

Consider deleting "Slump Limit" Subparagraph below and allow the Contractor to select a target slump based on ASTM C143/C143M, as permitted under ACI 301 (ACI 301M). If retaining "Slump Limit" Subparagraph, retain slump limit from three options, or revise to suit Project.

          - Slump Limit: [4 inches (100 mm), plus or minus 1 inch (25 mm)] [5 inches (125 mm), plus or minus 1 inch (25 mm)] [8 inches (200 mm), plus or minus 1 inch (25 mm) for concrete with verified slump of 3 inches ((75 mm),) plus or minus 1 inch ((25 mm),)before adding high-range water-reducing admixture or plasticizing admixture at Project site] <Insert limits>.

"Slump Flow Limit" Subparagraph below is for self-consolidating concrete. Consider deleting and allow the Contractor to select a target slump flow based on ASTM C1611/C1611M, as permitted under ACI 301 (ACI 301M). If retaining "Slump Flow Limit" Subparagraph, retain slump flow limit from two options, or revise to suit Project.

          - Slump Flow Limit: [22 inches (550 mm), plus or minus 1.5 inches (40 mm)] [30 inches (762 mm), plus or minus 2.5 inches (65 mm)] <Insert limits>.

          - Air Content:

Options in first two subparagraphs are examples only. Revise to suite Project. See ACI 301 (ACI 301M), Table 4.2.2.7(b)1 for air content for additional Exposure Classes and aggregate sizes.

            - Exposure Class F1: [5.0 percent, plus or minus 1.5 percent at point of delivery for concrete containing 3/4-inch (19-mm) nominal maximum aggregate size] [4.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-inch (25-mm) nominal maximum aggregate size] [4.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-1/2-inch (38-mm) nominal maximum aggregate size].

            - Exposure Classes F2 and F3: [6 percent, plus or minus 1.5 percent at point of delivery for concrete containing 3/4-inch (19-mm) nominal maximum aggregate size] [6 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-inch (25-mm) nominal maximum aggregate size] [5.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-1/2-inch (38-mm) nominal maximum aggregate size].

Retain appropriate option in subparagraph below for chloride limits. Percentages below repeat ACI 318 (ACI 318M) limits. First option is for Exposure Class C0; second option is for Exposure Class C1; third option is for Exposure Class C2. ACI 301 (ACI 301M) and ACI 318 (ACI 318M) express this percentage by weight of cement, not cementitious material.

          - Limit water-soluble, chloride-ion content in hardened concrete to [1.00] [0.30] [0.15] <Insert number> percent by weight of cement.

        - Class [H] <Insert designation>: Normal-weight concrete used for building walls.

          - Exposure Class: ACI 318 (ACI 318M) [F0] [F1] [F2] [F3] [S0] [S1] [S2] [S3] [W0] [W1] [C0] [C1] [C2].

Retain strength from first five options in "Minimum Compressive Strength" Subparagraph below, or revise to suit Project. Coordinate compressive strength with w/cm if concrete is subject to special exposure conditions or sulfate exposure, as identified in ACI 318 (ACI 318M).

          - Minimum Compressive Strength: [5000 psi (34.5 MPa)] [4500 psi (31 MPa)] [4000 psi (27.6 MPa)] [3500 psi (24.1 MPa)] [3000 psi (20.7 MPa)] <Insert strength> [As indicated] at 28 days.

Retain w/cm from three options in "Maximum w/cm" Subparagraph below, revise to suit Project, or delete if in-service durability conditions are benign and limits on w/cm are not required. Coordinate w/cm with compressive strength. See the Evaluations for discussion.

          - Maximum w/cm: [0.50] [0.45] [0.40] <Insert number>.

Consider deleting "Slump Limit" Subparagraph below and allow the Contractor to select a target slump based on ASTM C143/C143M, as permitted under ACI 301 (ACI 301M). If retaining "Slump Limit" Subparagraph, retain slump limit from three options, or revise to suit Project.

          - Slump Limit: [4 inches (100 mm), plus or minus 1 inch (25 mm)] [5 inches (125 mm), plus or minus 1 inch (25 mm)] [8 inches (200 mm), plus or minus 1 inch (25 mm) for concrete with verified slump of 3 inches ((75 mm),) plus or minus 1 inch ((25 mm),)before adding high-range water-reducing admixture or plasticizing admixture at Project site] <Insert limits>.

"Slump Flow Limit" Subparagraph below is for self-consolidating concrete. Consider deleting and allow the Contractor to select a target slump flow based on ASTM C1611/C1611M, as permitted under ACI 301 (ACI 301M). If retaining "Slump Flow Limit" Subparagraph, retain slump flow limit from two options, or revise to suit Project.

          - Slump Flow Limit: [22 inches (550 mm), plus or minus 1.5 inches (40 mm)] [30 inches (762 mm), plus or minus 2.5 inches (65 mm)] <Insert limits>.

          - Air Content:

Options in first two subparagraphs are examples only. Revise to suite Project. See ACI 301 (ACI 301M), Table 4.2.2.7(b)1 for air content for additional Exposure Classes and aggregate sizes.

            - Exposure Class F1: [5.0 percent, plus or minus 1.5 percent at point of delivery for concrete containing 3/4-inch (19-mm) nominal maximum aggregate size] [4.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-inch (25-mm) nominal maximum aggregate size] [4.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-1/2-inch (38-mm) nominal maximum aggregate size].

            - Exposure Classes F2 and F3: [6 percent, plus or minus 1.5 percent at point of delivery for concrete containing 3/4-inch (19-mm) nominal maximum aggregate size] [6 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-inch (25-mm) nominal maximum aggregate size] [5.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-1/2-inch (38-mm) nominal maximum aggregate size].

Retain appropriate option in subparagraph below for chloride limits. Percentages below repeat ACI 318 (ACI 318M) limits. First option is for Exposure Class C0; second option is for Exposure Class C1; third option is for Exposure Class C2. ACI 301 (ACI 301M) and ACI 318 (ACI 318M) express this percentage by weight of cement, not cementitious material.

          - Limit water-soluble, chloride-ion content in hardened concrete to [1.00] [0.30] [0.15] <Insert number> percent by weight of cement.

        - Class [I] <Insert designation>: Normal-weight concrete used for interior metal pan stairs and landings:

          - Exposure Class: ACI 318 (ACI 318M) [F0] [F1] [F2] [F3] [S0] [S1] [S2] [S3] [W0] [W1] [C0] [C1] [C2].

          - Minimum Compressive Strength: [3000 psi (20.7 MPa)] <Insert strength> [As indicated] at 28 days.

Retain w/cm from three options in "Maximum w/cm" Subparagraph below, revise to suit Project, or delete if in-service durability conditions are benign and limits on w/cm are not required. Coordinate w/cm with compressive strength. See the Evaluations for discussion.

          - Maximum w/cm: [0.53] [0.45] [0.40] <Insert number>.

          - Minimum Cementitious Materials Content: 470 lb/cu. yd. (279 kg/cu. m).

          - Maximum Size Aggregate: 1/2 inch (13 mm).

Retain slump limit from two options in "Slump Limit" Subparagraph below, or revise to suit Project.

          - Slump Limit: 3 inches (75 mm), plus 1 inch (25 mm) or minus 2 inches (50 mm).

          - Air Content: [0] <Insert number> percent, plus or minus 0.5 percent at point of delivery.

Retain appropriate option in first subparagraph below for chloride limits. Percentages below repeat ACI 318 (ACI 318M) limits. First option is for Exposure Class C0; second option is for Exposure Class C1; third option is for Exposure Class C2. ACI 301 (ACI 301M) and ACI 318 (ACI 318M) express this percentage by weight of cement, not cementitious material.

          - Limit water-soluble, chloride-ion content in hardened concrete to [1.00] [0.30] [0.15] <Insert number> percent by weight of cement.

          - Retarding Admixture: Not allowed.

          - Accelerating Admixture: Not allowed.

        - Class [J] <Insert designation>: Normal-weight concrete used for exterior retaining walls.

          - Exposure Class: ACI 318 (ACI 318M) [F0] [F1] [F2] [F3] [S0] [S1] [S2] [S3] [W0] [W1] [C0] [C1] [C2].

Retain strength from five options in "Minimum Compressive Strength" Subparagraph below, or revise to suit Project. Coordinate compressive strength with w/cm if concrete is subject to special exposure conditions or sulfate exposure as identified in ACI 318 (ACI 318M).

          - Minimum Compressive Strength: [5000 psi (34.5 MPa)] [4500 psi (31 MPa)] [4000 psi (27.6 MPa)] [3500 psi (24.1 MPa)] [3000 psi (20.7 MPa)] <Insert strength> [As indicated] at 28 days.

Retain w/cm from three options in "Maximum w/cm" Subparagraph below, revise to suit Project, or delete if in-service durability conditions are benign and limits on w/cm are not required. Coordinate w/cm with compressive strength. See the Evaluations for discussion.

          - Maximum w/cm: [0.50] [0.45] [0.40] <Insert number>.

Consider deleting "Slump Limit" Subparagraph below and allow the Contractor to select a target slump based on ASTM C143/C143M, as permitted under ACI 301. If retaining "Slump Limit" Subparagraph, retain slump limit from first three options, or revise to suit Project.

          - Slump Limit: [4 inches (100 mm), plus or minus 1 inch (25 mm)] [5 inches (125 mm), plus or minus 1 inch (25 mm)] [8 inches (200 mm), plus or minus 1 inch (25 mm) for concrete with verified slump of 3 inches ((75 mm),) plus or minus 1 inch ((25 mm),)before adding high-range water-reducing admixture or plasticizing admixture at Project site] <Insert limits>.

"Slump Flow Limit" Subparagraph below is for self-consolidating concrete. Consider deleting and allow the Contractor to select a target slump flow based on ASTM C1611/C1611M, as permitted under ACI 301 (ACI 301M). If retaining "Slump Flow Limit" Subparagraph, retain slump flow limit from two options, or revise to suit Project.

          - Slump Flow Limit: [22 inches (550 mm), plus or minus 1.5 inches (40 mm)] [30 inches (762 mm), plus or minus 2.5 inches (65 mm)] <Insert limits>.

          - Air Content:

Options in first two subparagraphs are examples only. Revise to suite Project. See ACI 301 (ACI 301M), Table 4.2.2.7(b)1 for air content for additional Exposure Classes and aggregate sizes.

            - Exposure Class F1: [5.0 percent, plus or minus 1.5 percent at point of delivery for concrete containing 3/4-inch (19-mm) nominal maximum aggregate size] [4.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-inch (25-mm) nominal maximum aggregate size] [4.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-1/2-inch (38-mm) nominal maximum aggregate size].

            - Exposure Classes F2 and F3: [6 percent, plus or minus 1.5 percent at point of delivery for concrete containing 3/4-inch (19-mm) nominal maximum aggregate size] [6 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-inch (25-mm) nominal maximum aggregate size] [5.5 percent, plus or minus 1.5 percent at point of delivery for concrete containing 1-1/2-inch (38-mm) nominal maximum aggregate size].

Retain appropriate option in subparagraph below for chloride limits. Percentages below repeat ACI 318 (ACI 318M) limits. First option is for Exposure Class C0; second option is for Exposure Class C1; third option is for Exposure Class C2. ACI 301 (ACI 301M) and ACI 318 (ACI 318M) express this percentage by weight of cement, not cementitious material.

          - Limit water-soluble, chloride-ion content in hardened concrete to [1.00] [0.30] [0.15] <Insert number> percent by weight of cement.

      - CONCRETE MIXING

Retain option in "Ready-Mixed Concrete" Paragraph below if steel or synthetic fibers are required.

        - Ready-Mixed Concrete: Measure, batch, mix, and deliver concrete in accordance with ASTM C94/C94M[ and ASTM C1116/C1116M], and furnish batch ticket information.

Retain "Project-Site Mixing" Paragraph below if Project-site mixing is permitted. ACI 301 (ACI 301M) applies measuring, batching, and mixing requirements from ASTM C94/C94M to Project-site mixing.

        - Project-Site Mixing: Measure, batch, and mix concrete materials and concrete in accordance with ASTM C94/C94M. Mix concrete materials in appropriate drum-type batch machine mixer.

          - For mixer capacity of 1 cu. yd. (0.76 cu. m) or smaller, continue mixing at least 1-1/2 minutes, but not more than five minutes after ingredients are in mixer, before any part of batch is released.

          - For mixer capacity larger than 1 cu. yd. (0.76 cu. m), increase mixing time by 15 seconds for each additional 1 cu. yd. (0.76 cu. m).

          - Provide batch ticket for each batch discharged and used in the Work, indicating Project identification name and number, date, mixture type, mixture time, quantity, and amount of water added. Record approximate location of final deposit in structure.

- EXECUTION

      - EXAMINATION

        - Verification of Conditions:

          - Before placing concrete, verify that installation of concrete forms, accessories, and reinforcement, and embedded items is complete and that required inspections have been performed.

          - Do not proceed until unsatisfactory conditions have been corrected.

      - PREPARATION

        - Provide reasonable auxiliary services to accommodate field testing and inspections, acceptable to testing agency, including the following:

          - Daily access to the Work.

          - Incidental labor and facilities necessary to facilitate tests and inspections.

          - Secure space for storage, initial curing, and field curing of test samples, including source of water and continuous electrical power at Project site during site curing period for test samples.

          - Security and protection for test samples and for testing and inspection equipment at Project site.

      - INSTALLATION OF EMBEDDED ITEMS

Specify embedded items and anchorage devices for other Work attached to or supported by cast-in-place concrete. Insert specific requirements for installing embedded items, if any, that are part of the Work.

        - Place and secure anchorage devices and other embedded items required for adjoining Work that is attached to or supported by cast-in-place concrete.

          - Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

          - Install anchor rods, accurately located, to elevations required and complying with tolerances in Section 7.5 of ANSI/AISC 303.

Retain applicable subparagraph below, and insert others if required. Revise to suit Project.

          - Install reglets to receive waterproofing and to receive through-wall flashings in outer face of concrete frame at exterior walls, where flashing is shown at lintels, shelf angles, and other conditions.

      - INSTALLATION OF VAPOR RETARDER

        - Sheet Vapor Retarders: Place, protect, and repair sheet vapor retarder in accordance with ASTM E1643 and manufacturer's written instructions.

          - Install vapor retarder with longest dimension parallel with direction of concrete pour.

          - Face laps away from exposed direction of concrete pour.

          - Lap vapor retarder over footings and grade beams not less than 6 inches (150 mm), sealing vapor retarder to concrete.

          - Lap joints 6 inches (150 mm) and seal with manufacturer's recommended tape.

          - Terminate vapor retarder at the top of floor slabs, grade beams, and pile caps, sealing entire perimeter to floor slabs, grade beams, foundation walls, or pile caps.

          - Seal penetrations in accordance with vapor retarder manufacturer's instructions.

          - Protect vapor retarder during placement of reinforcement and concrete.

            - Repair damaged areas by patching with vapor retarder material, overlapping damages area by 6 inches (150 mm) on all sides, and sealing to vapor retarder.

        - Bituminous Vapor Retarders: Place, protect, and repair bituminous vapor retarder in accordance with manufacturer's written instructions.

      - JOINTS

Coordinate joint types, description, and location with Drawings. Joint types are consolidated in this article for consistency rather than for strict sequence of installation.

        - Construct joints true to line, with faces perpendicular to surface plane of concrete.

Revise criteria for locating construction joints in "Construction Joints" Paragraph below to suit Project.

        - Construction Joints: Coordinate with floor slab pattern and concrete placement sequence.

          - Install so strength and appearance of concrete are not impaired, at locations indicated on Drawings or as approved by Architect.

          - Place joints perpendicular to main reinforcement.

            - Continue reinforcement across construction joints unless otherwise indicated.

            - Do not continue reinforcement through sides of strip placements of floors and slabs.

Retain first subparagraph below if keyed joints are used. Keyed joints are used in walls and floors and between walls and slabs or footings. ACI 302.1R recommends limiting keyed joints to lightly trafficked floors, because keys may fail and lips may chip after concrete shrinks.

          - Form keyed joints as indicated. Embed keys at least 1-1/2 inches (38 mm) into concrete.

          - Locate joints for beams, slabs, joists, and girders at third points of spans. Offset joints in girders a minimum distance of twice the beam width from a beam-girder intersection.

          - Locate horizontal joints in walls and columns at underside of floors, slabs, beams, and girders and at the top of footings or floor slabs.

Insert spacing of construction joints in first subparagraph below if preferred.

          - Space vertical joints in walls [as indicated on Drawings] <Insert spacing>. Unless otherwise indicated on Drawings, locate vertical joints beside piers integral with walls, near corners, and in concealed locations where possible.

Retain one of two subparagraphs below only if a bonding material is permitted. Verify acceptance of use with structural engineer.

          - Use a bonding agent at locations where fresh concrete is placed against hardened or partially hardened concrete surfaces.

          - Use epoxy-bonding adhesive at locations where fresh concrete is placed against hardened or partially hardened concrete surfaces.

Insert spacing of control joints here or on Drawings if required. Control joint spacings vary with slab thickness, aggregate size, and slump based on PCA's recommendations. Depth of joint may be varied to suit cutting method or if steel-fiber reinforcement is used.

        - Control Joints in Slabs-on-Ground: Form weakened-plane control joints, sectioning concrete into areas as indicated. Construct control joints for a depth equal to at least [one-fourth] <Insert depth> of concrete thickness as follows:

Retain type of joint-forming method from "Grooved Joints" and "Sawed Joints" subparagraphs below, or retain both subparagraphs as Contractor's option. Insert joint spacing if not indicated on Drawings.

          - Grooved Joints: Form control joints after initial floating by grooving and finishing each edge of joint to a radius of 1/8 inch (3.2 mm). Repeat grooving of control joints after applying surface finishes. Eliminate groover tool marks on concrete surfaces.

Retain "Sawed Joints" Subparagraph below if saw cutting is permitted. Description does not distinguish conventional wet- and dry-cut saws from early-entry dry-cut saws. Timing is critical to sawed joints. Early-entry dry-cut saws are used within one to two hours of finishing concrete. To leave concrete undamaged from sawing, conventional saw cutting must be delayed, usually four to 12 hours, but not so long that uncontrolled cracking of concrete could occur.

          - Sawed Joints: Form control joints with power saws equipped with shatterproof abrasive or diamond-rimmed blades. Cut 1/8-inch- (3.2-mm-) wide joints into concrete when cutting action does not tear, abrade, or otherwise damage surface and before concrete develops random cracks.

        - Isolation Joints in Slabs-on-Ground: After removing formwork, install joint-filler strips at slab junctions with vertical surfaces, such as column pedestals, foundation walls, grade beams, and other locations, as indicated.

Retain one or both of first two subparagraphs below. If both are required, indicate location of each on Drawings.

          - Extend joint-filler strips full width and depth of joint, terminating flush with finished concrete surface unless otherwise indicated on Drawings.

          - Terminate full-width joint-filler strips not less than 1/2 inch (13 mm) or more than 1 inch (25 mm) below finished concrete surface, where joint sealants, specified in Section 079200 "Joint Sealants," are indicated.

          - Install joint-filler strips in lengths as long as practicable. Where more than one length is required, lace or clip sections together.

Retain "Doweled Joints" Paragraph below if doweled control or expansion joints are used; revise if precoated dowels are required.

        - Doweled Joints:

          - Install dowel bars and support assemblies at joints where indicated on Drawings.

          - Lubricate or asphalt coat one-half of dowel bar length to prevent concrete bonding to one side of joint.

Retain "Doweled Plates" Paragraph below if doweled control or expansion joints are used.

        - Dowel Plates: Install dowel plates at joints where indicated on Drawings.

      - CONCRETE PLACEMENT

        - Before placing concrete, verify that installation of formwork, reinforcement, embedded items, and vapor retarder is complete and that required inspections are completed.

          - Immediately prior to concrete placement, inspect vapor retarder for damage and deficient installation, and repair defective areas.

          - Provide continuous inspection of vapor retarder during concrete placement and make necessary repairs to damaged areas as Work progresses.

        - Notify Architect and testing and inspection agencies 24 hours prior to commencement of concrete placement.

Retain one of first two paragraphs and associated subparagraphs below. ACI 301 (ACI 301M) permits water to be added to concrete mixture on-site to adjust slump, up to amount allowed in design mixture.

        - Do not add water to concrete during delivery, at Project site, or during placement unless approved by Architect in writing, but not to exceed the amount indicated on the concrete delivery ticket.

Retain subparagraph below if high-range water-reducing admixtures are permitted.

          - Do not add water to concrete after adding high-range water-reducing admixtures to mixture.

        - Before test sampling and placing concrete, water may be added at Project site, subject to limitations of ACI 301 (ACI 301M), but not to exceed the amount indicated on the concrete delivery ticket.

Retain subparagraph below if high-range water-reducing admixtures are permitted.

          - Do not add water to concrete after adding high-range water-reducing admixtures to mixture.

        - Deposit concrete continuously in one layer or in horizontal layers of such thickness that no new concrete is placed on concrete that has hardened enough to cause seams or planes of weakness.

          - If a section cannot be placed continuously, provide construction joints as indicated.

          - Deposit concrete to avoid segregation.

          - Deposit concrete in horizontal layers of depth not to exceed formwork design pressures and in a manner to avoid inclined construction joints.

          - Consolidate placed concrete with mechanical vibrating equipment in accordance with ACI 301 (ACI 301M).

            - Do not use vibrators to transport concrete inside forms.

            - Insert and withdraw vibrators vertically at uniformly spaced locations to rapidly penetrate placed layer and at least 6 inches (150 mm) into preceding layer.

            - Do not insert vibrators into lower layers of concrete that have begun to lose plasticity.

            - At each insertion, limit duration of vibration to time necessary to consolidate concrete, and complete embedment of reinforcement and other embedded items without causing mixture constituents to segregate.

        - Deposit and consolidate concrete for floors and slabs in a continuous operation, within limits of construction joints, until placement of a panel or section is complete.

          - Do not place concrete floors and slabs in a checkerboard sequence.

          - Consolidate concrete during placement operations, so concrete is thoroughly worked around reinforcement and other embedded items and into corners.

          - Maintain reinforcement in position on chairs during concrete placement.

          - Screed slab surfaces with a straightedge and strike off to correct elevations.

          - Level concrete, cut high areas, and fill low areas.

          - Slope surfaces uniformly to drains where required.

          - Begin initial floating using bull floats or darbies to form a uniform and open-textured surface plane, before excess bleedwater appears on the surface.

          - Do not further disturb slab surfaces before starting finishing operations.

      - FINISHING FORMED SURFACES

Retain types of formed finishes required in this article. Coordinate finishes retained with Drawing Room Finish Schedule, or indicate location of each finish on Drawings.

        - As-Cast Surface Finishes:

          - ACI 301 (ACI 301M) Surface Finish SF-1.0: As-cast concrete texture imparted by form-facing material.

            - Patch voids larger than 1-1/2 inches (38 mm) wide or 1/2 inch (13 mm) deep.

            - Remove projections larger than 1 inch (25 mm).

            - Tie holes do not require patching.

            - Surface Tolerance: ACI 117 (ACI 117M) Class D.

            - Apply to concrete surfaces [not exposed to public view] <Insert locations>.

          - ACI 301 (ACI 301M) Surface Finish SF-2.0: As-cast concrete texture imparted by form-facing material, arranged in an orderly and symmetrical manner with a minimum of seams.

            - Patch voids larger than 3/4 inch (19 mm) wide or 1/2 inch (13 mm) deep.

            - Remove projections larger than 1/4 inch (6 mm).

            - Patch tie holes.

            - Surface Tolerance: ACI 117 (ACI 117M) Class B.

Revise locations in "Locations" Subparagraph below to suit Project, or delete subparagraph and indicate locations on Drawings. Retain second option if additional finishing is required.

            - Locations: Apply to concrete surfaces [exposed to public view,] [to receive a rubbed finish,] [or to be covered with a coating or covering material applied directly to concrete] <Insert locations>.

          - ACI 301 (ACI 301M) Surface Finish SF-3.0:

            - Patch voids larger than 3/4 inch (19 mm) wide or 1/2 inch (13 mm) deep.

            - Remove projections larger than 1/8 inch (3 mm).

            - Patch tie holes.

            - Surface Tolerance: ACI 117 (ACI 117M) Class A.

Revise locations in "Locations" Subparagraph below to suit Project, or delete subparagraph and indicate locations on Drawings. Retain second option if additional finishing is required.

            - Locations: Apply to concrete surfaces [exposed to public view,] [to receive a rubbed finish,] [or to be covered with a coating or covering material applied directly to concrete] <Insert locations>.

If retaining "Rubbed Finish" Paragraph below, retain "ACI 301 (ACI 301M) Surface Finish SF-2.0" or "ACI 301 (ACI 301M) Surface Finish SF-3.0" subparagraphs above.

        - Rubbed Finish: Apply the following to as cast surface finishes where indicated on Drawings:

Retain one or more rubbed finishes in "Smooth-Rubbed Finish," "Grout-Cleaned Rubbed Finish," and "Cork-Floated Finish" subparagraphs below.

          - Smooth-Rubbed Finish:

            - Perform no later than one day after form removal.

            - Moisten concrete surfaces and rub with carborundum brick or another abrasive until producing a uniform color and texture.

            - If sufficient cement paste cannot be drawn from the concrete by the rubbing process, use a grout made from the same cementitious materials used in the in-place concrete.

            - Maintain required patterns or variances as shown on Drawings or to match [design reference sample] [field sample panels] [mockups].

          - Grout-Cleaned Rubbed Finish:

            - Clean concrete surfaces after contiguous surfaces are completed and accessible.

            - Do not clean concrete surfaces as Work progresses.

            - Mix 1 part portland cement to 1-1/2 parts fine sand, complying with ASTM C144 or ASTM C404, by volume, with sufficient water to produce a mixture with the consistency of thick paint. Add white portland cement in amounts determined by trial patches, so color of dry grout matches adjacent surfaces.

            - Wet concrete surfaces.

            - Scrub grout into voids and remove excess grout. When grout whitens, rub surface with clean burlap, and keep surface damp by fog spray for at least 36 hours.

            - Maintain required patterns or variances as shown on Drawings or to match [design reference sample] [field sample panels] [mockups].

          - Cork-Floated Finish:

            - Mix 1 part portland cement to 1 part fine sand, complying with ASTM C144 or ASTM C404, by volume, with sufficient water to produce a mixture with the consistency of thick paint.

            - Mix 1 part portland cement and 1 part fine sand with sufficient water to produce a mixture of stiff grout. Add white portland cement in amounts determined by trial patches, so color of dry grout matches adjacent surfaces.

            - Wet concrete surfaces.

            - Compress grout into voids by grinding surface.

            - In a swirling motion, finish surface with a cork float.

            - Maintain required patterns or variances as shown on Drawings or to match [design reference sample] [field sample panels] [mockups].

Retain "Scrubbed Finish" Subparagraph below if scrubbed finish, which is usually applied to surfaces treated with a surface retarder, is required.

          - Scrubbed Finish: After concrete has achieved a compressive strength of from 1000 to 1500 psi (6.9 to 10.3 MPa), apply scrubbed finish.

            - Wet concrete surfaces thoroughly and scrub with stiff fiber or wire brushes, using water freely, until top mortar surface is removed and aggregate is uniformly exposed.

            - Rinse scrubbed surfaces with clean water.

            - Maintain continuity of finish on each surface or area of Work.

            - Remove only enough concrete mortar from surfaces to match [design reference sample] [field sample panels] [mockups].

Before retaining "Abrasive-Blast Finish" Paragraph below, consider Contractor's ability to comply with OSHA's "Respirable Crystalline Silica Standard for Construction."

        - Abrasive-Blast Finish: Apply the following to as-cast surface finishes where indicated on Drawings:

          - Perform abrasive blasting after compressive strength of concrete exceeds 2000 psi (13.8 MPa).

          - Coordinate with formwork removal to ensure that surfaces to be abrasive blasted are treated at the same age.

          - Surface Continuity:

            - Perform abrasive-blast finishing as continuous operation, maintaining continuity of finish on each surface or area of Work.

            - Maintain required patterns or variances in depths of blast to match [design reference sample] [field sample panels] [mockups].

          - Abrasive Blasting:

            - Abrasive-blast corners and edges of patterns carefully, using backup boards to maintain uniform corner and edge lines.

            - Determine type of nozzle pressure and blasting techniques required to match field sample.

            - Depth of Cut: Use an abrasive grit of proper type and gradation to expose aggregate and surrounding matrix surfaces to match field sample, as follows:

Texture in first four subparagraphs below is for example. Revise to suit Project.

              - Brush Texture: Remove cement matrix to dull surface sheen and expose face of fine aggregate, with no significant reveal.

              - Light Texture: Expose fine aggregate with occasional exposure of coarse aggregate and uniform color, with maximum reveal of 1/16 inch (1.5 mm).

              - Medium Texture: Generally, expose coarse aggregate with slight reveal and with a maximum reveal of 1/4 inch (6 mm).

              - Heavy Texture: Expose and reveal coarse aggregate to a maximum projection of one-third its diameter, with reveal range of 1/4 to 1/2 inch (6 to 13 mm).

            - Maintain required patterns or variances in reveal projection to match [design reference sample] [field sample panels] [mockups].

        - High-Pressure Water-Jet Finish: Apply the following to as-cast surface finishes where indicated on Drawings:

          - Perform high-pressure water jetting on concrete that has achieved a minimum compressive strength of 4500 psi (31 MPa).

          - Coordinate with formwork removal to ensure that surfaces to be high-pressure water-jet finished are treated at same age for uniform results.

          - Surface Continuity: Perform high-pressure water-jet finishing in as continuous an operation as possible, maintaining continuity of finish on each surface or area of Work.

          - Maintain required patterns or variances in reveal projection to match [design reference sample] [field sample panels] [mockups].

Retain "Bushhammer Finish" Paragraph below if required. ACI 301 (ACI 301M) requires that concrete have a minimum compressive strength of 4500 psi (31 MPa). Before retaining, consider Contractor's ability to comply with OSHA's "Respirable Crystalline Silica Standard for Construction."

        - Bushhammer Finish: Apply the following to as-cast surface finishes where indicated on Drawings:

          - Perform bushhammer finish to concrete that has achieved a minimum compressive strength of 4500 psi (31 MPa).

          - Surface Continuity:

            - Perform bushhammer finishing in as continuous an operation as possible, maintaining continuity of finish on each surface or area of Work.

          - Surface Cut:

            - Maintain required depth of cut and general aggregate exposure.

            - Use power tool with hammer attachments for large, flat surfaces, and use hand hammers for small areas, at corners and edges, and for restricted locations where power tools cannot reach.

          - Remove impressions of formwork and form facings with exception of tie holes.

          - Maintain required patterns or variances of cut as shown on Drawings or to match [design reference sample] [field sample panels] [mockups].

          - Maintain control of concrete chips, dust, and debris in each Work area, limiting migration of airborne materials and dust by use of tarpaulins, wind-breaks, or similar devices.

        - Related Unformed Surfaces:

          - At tops of walls, horizontal offsets, and similar unformed surfaces adjacent to formed surfaces, strike off smooth and finish with a color and texture matching adjacent formed surfaces.

          - Continue final surface treatment of formed surfaces uniformly across adjacent unformed surfaces unless otherwise indicated.

      - FINISHING FLOORS AND SLABS

        - Comply with ACI 302.1R recommendations for screeding, restraightening, and finishing operations for concrete surfaces. Do not wet concrete surfaces.

Retain one or more of "Scratch Finish," "Float Finish," "Trowel Finish," "Trowel and Fine-Broom Finish," "Broom Finish," and "Slip-Resistive Finish" paragraphs below for types of slab finishes required. Coordinate slab finishes retained with finish schedule, or indicate location of each finish on Drawings.

        - Scratch Finish:

          - While still plastic, texture concrete surface that has been screeded and bull-floated or darbied.

          - Use stiff brushes, brooms, or rakes to produce a profile depth of 1/4 inch (6 mm) in one direction.

Revise locations of scratch finish in subparagraph below to suit Project, or delete subparagraph and indicate locations on Drawings.

          - Apply scratch finish to surfaces [to receive concrete floor toppings] [to receive mortar setting beds for bonded cementitious floor finishes] <Insert locations>.

        - Float Finish:

          - When bleedwater sheen has disappeared and concrete surface has stiffened sufficiently to permit operation of specific float apparatus, consolidate concrete surface with power-driven floats or by hand floating if area is small or inaccessible to power-driven floats.

          - Repeat float passes and restraightening until surface is left with a uniform, smooth, granular texture and complies with ACI 117 (ACI A117M) tolerances for conventional concrete.

Revise locations of float finish in subparagraph below to suit Project, or delete subparagraph and indicate locations on Drawings.

          - Apply float finish to surfaces [to receive trowel finish] [and] [to be covered with fluid-applied or sheet waterproofing, built-up or membrane roofing, or sand-bed terrazzo] <Insert locations>.

        - Trowel Finish:

          - After applying float finish, apply first troweling and consolidate concrete by hand or power-driven trowel.

          - Continue troweling passes and restraighten until surface is free of trowel marks and uniform in texture and appearance.

          - Grind smooth any surface defects that would telegraph through applied coatings or floor coverings.

          - Do not add water to concrete surface.

          - Do not apply hard-troweled finish to concrete, which has a total air content greater than 3 percent.

Revise locations of trowel finish in first subparagraph below to suit Project, or delete subparagraph and indicate locations on Drawings.

          - Apply a trowel finish to surfaces [exposed to view] [or] [to be covered with resilient flooring, carpet, ceramic or quarry tile set over a cleavage membrane, paint, or another thin-film-finish coating system] <Insert locations>.

          - Finish surfaces to the following tolerances, in accordance with ASTM E1155 (ASTM E1155M), for a randomly trafficked floor surface:

            - Slabs on Ground:

ACI 301 (ACI 301M) suggests that all residential floors and nonresidential floors less than 10,000 sq. ft. (929 sq. m) be measured by straightedge method and that other nonresidential floors be measured by F-number system. Retain first subparagraph below for floor areas less than 10,000 sq. ft. (929 sq. m). Fourth option is requirement for gauged porcelain tile.

              - Finish and measure surface so gap at any point between concrete surface and an unleveled, freestanding, 10-ft.- (3.05-m-) long straightedge resting on two high spots and placed anywhere on the surface does not exceed [1/4 inch (6 mm)] [3/16 inch (4.8 mm)] [1/8 inch (3 mm)] [1/8 inch (3 mm) and also no more than 1/16 inch (1.6 mm) in2 feet (610 mm)].

Retain first subparagraph below for floor areas 10,000 sq. ft. (929 sq. m) and larger. Retain floor flatness (FF) and floor levelness (FL) values required for Project from first four subparagraphs below, or revise values to suit type of floor. ACI 302.1R suggests values in first subparagraph be used for carpeted slabs; those in second for thin floor coverings; and those in third for very flat floors for high-speed forklifts, air pallets, and ice and roller rinks. Those in fourth subparagraph are common for polished concrete floors.

              - Specified overall values of flatness, FF 25; and of levelness, FL 20; with minimum local values of flatness, FF 17; and of levelness, FL 15.

              - Specified overall values of flatness, FF 35; and of levelness, FL 25; with minimum local values of flatness, FF 24; and of levelness, FL 17.

              - Specified overall values of flatness, FF 45; and of levelness, FL 35; with minimum local values of flatness, FF 30; and of levelness, FL 24.

              - Specified overall values of flatness, FF 50; and of levelness, FL 25; with minimum local values of flatness, FF 40; and of levelness, FL 17.

            - Suspended Slabs:

ACI 301 (ACI 301M) suggests that all residential floors and nonresidential floors less than 10,000 sq. ft. (929 sq. m) be measured by straightedge method and that other nonresidential floors be measured by F-number system. Retain first subparagraph below for floor areas less than 10,000 sq. ft. (929 sq. m). Fourth option is requirement for gauged porcelain tile.

              - Finish and measure surface so gap at any point between concrete surface and an unleveled, freestanding, 10-ft.- (3.05-m-) long straightedge resting on two high spots and placed anywhere on the surface does not exceed [1/4 inch (6 mm)] [3/16 inch (4.8 mm)] [1/8 inch (3 mm)] [1/8 inch (3 mm) and also no more than 1/16 inch (1.6 mm) in 2 feet (610 mm)].

Retain first subparagraph below for floor areas 10,000 sq. ft. (929 sq. m) and larger. Retain floor flatness (FF) and floor levelness (FL) values required for Project from first three subparagraphs below, or revise values to suit type of floor. ACI 302.1R suggests values in first subparagraph be used for carpeted slabs; those in second for thin floor coverings; and those in third for very flat floors for high-speed forklifts, air pallets, and ice and roller rinks.

              - Specified overall values of flatness, FF 25; and of levelness, FL 20; with minimum local values of flatness, FF 17; and of levelness, FL 15.

              - Specified overall values of flatness, FF 35; and of levelness, FL 20; with minimum local values of flatness, FF 24; and of levelness, FL 15.

              - Specified overall values of flatness, FF 45; and of levelness, FL 35; with minimum local values of flatness, FF 30; and of levelness, FL 24.

        - Trowel and Fine-Broom Finish: Apply a first trowel finish to surfaces [indicated on Drawings] [where ceramic or quarry tile is to be installed by either thickset or thinset method]. While concrete is still plastic, slightly scarify surface with a fine broom perpendicular to main traffic route.

          - Coordinate required final finish with Architect before application.

          - Comply with flatness and levelness tolerances for trowel-finished floor surfaces.

Retain "Broom Finish" Paragraph below if applicable. Broom finish is generally used on exterior concrete steps and platforms, ramps, and other surfaces subject to light foot traffic.

        - Broom Finish: Apply a broom finish to exterior concrete platforms, steps, ramps, and locations indicated on Drawings.

          - Immediately after float finishing, slightly roughen trafficked surface by brooming with fiber-bristle broom perpendicular to main traffic route.

          - Coordinate required final finish with Architect before application.

Retain "Slip-Resistive Finish" Paragraph below if applicable. This finish is generally used on interior and exterior concrete treads, platforms, and ramps subject to moderate foot traffic.

        - Slip-Resistive Finish: Before final floating, apply slip-resistive [aggregate] [aluminum granule] finish to concrete stair treads, platforms, ramps as indicated on Drawings

          - Apply in accordance with manufacturer's written instructions and as follows:

            - Uniformly spread [25 lb/100 sq. ft. (12 kg/10 sq. m)] <Insert rate> of dampened slip-resistive [aggregate] [aluminum granules] over surface in one or two applications.

            - Tamp aggregate flush with surface, but do not force below surface.

Revise float finish in first subparagraph below to trowel finish if required.

            - After broadcasting and tamping, apply float finish.

            - After curing, lightly work surface with a steel wire brush or an abrasive stone and water to expose slip-resistive [aggregate] [aluminum granules].

Retain Dry-Shake Floor Hardener Finish Paragraph below if pigmented or unpigmented dry-shake floor hardener finish is required.

        - Dry-Shake Floor Hardener Finish: After initial floating, apply dry-shake floor hardener to surfaces in accordance with manufacturer's written instructions and as follows:

Consult manufacturers and revise rate of application in first subparagraph below if required. This rate is usually recommended for light traffic.

          - Uniformly apply dry-shake floor hardener at a rate of [100 lb/100 sq. ft. (49 kg/10 sq. m)] <Insert rate> unless greater amount is recommended by manufacturer.

          - Uniformly distribute approximately two-thirds of dry-shake floor hardener over surface by hand or with mechanical spreader, and embed by power floating.

          - Follow power floating with a second dry-shake floor hardener application, uniformly distributing remainder of material, and embed by power floating.

Coordinate selection of curing compounds for compatibility with dry-shake floor hardener, and revise lists of manufacturers in Part 2 accordingly if required.

          - After final floating, apply a trowel finish.

          - Cure concrete with curing compound recommended by dry-shake floor hardener manufacturer and apply immediately after final finishing.

      - INSTALLATION OF MISCELLANEOUS CONCRETE ITEMS

This article is an example only. Insert, revise, or delete items to suit Project.

        - Filling In:

          - Fill in holes and openings left in concrete structures after Work of other trades is in place unless otherwise indicated.

          - Mix, place, and cure concrete, as specified, to blend with in-place construction.

          - Provide other miscellaneous concrete filling indicated or required to complete the Work.

        - Curbs: Provide monolithic finish to interior curbs by stripping forms while concrete is still green and by steel-troweling surfaces to a hard, dense finish with corners, intersections, and terminations slightly rounded.

        - Equipment Bases and Foundations:

          - Coordinate sizes and locations of concrete bases with actual equipment provided.

          - Construct concrete bases [4 inches (100 mm)] [6 inches (150 mm)] [8 inches (200 mm)] <Insert dimension> high unless otherwise indicated on Drawings, and extend base not less than 6 inches (150 mm) in each direction beyond the maximum dimensions of supported equipment unless otherwise indicated on Drawings, or unless required for seismic anchor support.

          - Minimum Compressive Strength: [5000 psi (34.5 MPa)] [4500 psi (31 MPa)] [4000 psi (27.6 MPa)] [3500 psi (24.1 MPa)] [3000 psi (20.7 MPa)] <Insert value> at 28 days.

          - Install dowel rods to connect concrete base to concrete floor. Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around the full perimeter of concrete base.

          - For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete substrate.

          - Prior to pouring concrete, place and secure anchorage devices.

            - Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

            - Cast anchor-bolt insert into bases.

            - Install anchor bolts to elevations required for proper attachment to supported equipment.

        - Steel Pan Stairs: Provide concrete fill for steel pan stair treads, landings, and associated items.

          - Cast-in inserts and accessories, as shown on Drawings.

          - Screed, tamp, and trowel finish concrete surfaces.

      - CONCRETE CURING

        - Protect freshly placed concrete from premature drying and excessive cold or hot temperatures.

          - Comply with ACI 301 (ACI 301M) and ACI 306.1 for cold weather protection during curing.

          - Comply with ACI 301 (ACI 301M) and ACI 305.1 (ACI 305.1M) for hot-weather protection during curing.

If evaporation rate in subparagraph below is exceeded, ACI 305R states that plastic shrinkage cracking is probable. See ACI 305R for estimated moisture-loss chart relating relative humidity, air and concrete temperature, and wind velocity to rate of evaporation.

          - Maintain moisture loss no more than 0.2 lb/sq. ft. x h (1 kg/sq. m x h), calculated in accordance with ACI 305.1, before and during finishing operations.

        - Curing Formed Surfaces: Comply with ACI 308.1 (ACI 308.1M) as follows:

          - Cure formed concrete surfaces, including underside of beams, supported slabs, and other similar surfaces.

          - Cure concrete containing color pigments in accordance with color pigment manufacturer's instructions.

          - If forms remain during curing period, moist cure after loosening forms.

          - If removing forms before end of curing period, continue curing for remainder of curing period, as follows:

            - Continuous Fogging: Maintain standing water on concrete surface until final setting of concrete.

            - Continuous Sprinkling: Maintain concrete surface continuously wet.

            - Absorptive Cover: Pre-dampen absorptive material before application; apply additional water to absorptive material to maintain concrete surface continuously wet.

            - Water-Retention Sheeting Materials: Cover exposed concrete surfaces with sheeting material, taping, or lapping seams.

            - Membrane-Forming Curing Compound: Apply uniformly in continuous operation by power spray or roller in accordance with manufacturer's written instructions.

              - Recoat areas subject to heavy rainfall within three hours after initial application.

              - Maintain continuity of coating and repair damage during curing period.

        - Curing Unformed Surfaces: Comply with ACI 308.1 (ACI 308.1M) as follows:

          - Begin curing immediately after finishing concrete.

          - Interior Concrete Floors:

            - Floors to Receive Floor Coverings Specified in Other Sections: Contractor has option of the following:

              - Absorptive Cover: As soon as concrete has sufficient set to permit application without marring concrete surface, install prewetted absorptive cover over entire area of floor.

                - Lap edges and ends of absorptive cover not less than 12 inches (300 mm).

                - Maintain absorptive cover water saturated, and in place, for duration of curing period, but not less than seven days.

              - Moisture-Retaining-Cover Curing: Cover concrete surfaces with moisture-retaining cover for curing concrete, placed in widest practicable width, with sides and ends lapped at least 12 inches (300 mm), and sealed by waterproof tape or adhesive.

                - Immediately repair any holes or tears during curing period, using cover material and waterproof tape.

                - Cure for not less than seven days.

              - Ponding or Continuous Sprinkling of Water: Maintain concrete surfaces continuously wet for not less than seven days, utilizing one, or a combination of, the following:

                - Water.

                - Continuous water-fog spray.

            - Floors to Receive Penetrating Liquid Floor Treatments: Contractor has option of the following:

              - Absorptive Cover: As soon as concrete has sufficient set to permit application without marring concrete surface, install prewetted absorptive cover over entire area of floor.

                - Lap edges and ends of absorptive cover not less than 12 inches (300 mm).

                - Maintain absorptive cover water saturated, and in place, for duration of curing period, but not less than seven days.

              - Moisture-Retaining-Cover Curing: Cover concrete surfaces with moisture-retaining cover for curing concrete, placed in widest practicable width, with sides and ends lapped at least 12 inches (300 mm), and sealed by waterproof tape or adhesive.

                - Immediately repair any holes or tears during curing period, using cover material and waterproof tape.

                - Cure for not less than seven days.

              - Ponding or Continuous Sprinkling of Water: Maintain concrete surfaces continuously wet for not less than seven days, utilizing one, or a combination of, the following:

                - Water.

                - Continuous water-fog spray.

            - Floors to Receive Polished Finish: Contractor has option of the following:

              - Absorptive Cover: As soon as concrete has sufficient set to permit application without marring concrete surface, install prewetted absorptive cover over entire area of floor.

                - Lap edges and ends of absorptive cover not less than 12 inches (300 mm).

                - Maintain absorptive cover water saturated, and in place, for duration of curing period, but not less than seven days.

              - Ponding or Continuous Sprinkling of Water: Maintain concrete surfaces continuously wet for not less than seven days, utilizing one, or a combination of, the following:

                - Water.

                - Continuous water-fog spray.

            - Floors to Receive Chemical Stain:

              - As soon as concrete has sufficient set to permit application without marring concrete surface, install curing paper over entire area of floor.

              - Install curing paper square to building lines, without wrinkles, and in a single length without end joints.

              - Butt sides of curing paper tight; do not overlap sides of curing paper.

              - Leave curing paper in place for duration of curing period, but not less than 28 days.

            - Floors to Receive Urethane Flooring:

              - As soon as concrete has sufficient set to permit application without marring concrete surface, install prewetted absorptive cover over entire area of floor.

              - Rewet absorptive cover, and cover immediately with polyethylene moisture-retaining cover with edges lapped 6 inches (150 mm) and sealed in place.

              - Secure polyethylene moisture-retaining cover in place to prohibit air from circulating under polyethylene moisture-retaining cover.

              - Leave absorptive cover and polyethylene moisture-retaining cover in place for duration of curing period, but not less than 28 days.

Usually delete "Floors to Receive Curing Compound" Subparagraph for floors scheduled to receive additional floor finishes. Consult with floor finish manufacturer before retaining.

            - Floors to Receive Curing Compound:

              - Apply uniformly in continuous operation by power spray or roller in accordance with manufacturer's written instructions.

              - Recoat areas subjected to heavy rainfall within three hours after initial application.

              - Maintain continuity of coating, and repair damage during curing period.

Retain "Removal" Subparagraph below if requiring removal of curing compounds that may interfere with adhesion of floor coverings.

              - Removal: After curing period has elapsed, remove curing compound without damaging concrete surfaces by method recommended by curing compound manufacturer[ unless manufacturer certifies curing compound does not interfere with bonding of floor covering used on Project].

Curing and sealing compound is usually for floors and slabs and may act as a permanent surface finish.

            - Floors to Receive Curing and Sealing Compound:

              - Apply uniformly to floors and slabs indicated in a continuous operation by power spray or roller in accordance with manufacturer's written instructions.

              - Recoat areas subjected to heavy rainfall within three hours after initial application.

              - Repeat process 24 hours later, and apply a second coat. Maintain continuity of coating, and repair damage during curing period.

      - TOLERANCES

        - Conform to ACI 117 (ACI 117M).

      - APPLICATION OF LIQUID FLOOR TREATMENTS

        - Penetrating Liquid Floor Treatment: Prepare, apply, and finish penetrating liquid floor treatment in accordance with manufacturer's written instructions.

          - Remove curing compounds, sealers, oil, dirt, laitance, and other contaminants and complete surface repairs.

Some manufacturers state that the penetrating liquid floor treatment also functions as a curing aid. If used as a cure, delete minimum age of concrete in first subparagraph below, and revise application method to follow manufacturer's written instructions. Coordinate with "Concrete Curing" Article.

          - Do not apply to concrete that is less than [three] [seven] [14] [28] days' old.

          - Apply liquid until surface is saturated, scrubbing into surface until a gel forms; rewet; and repeat brooming or scrubbing.

          - Rinse with water; remove excess material until surface is dry.

          - Apply a second coat in a similar manner if surface is rough or porous.

Usually delete "Sealing Coat" Paragraph below if two coats of curing and sealing compound have already been applied during curing stage. Sealing coat may be used as turnover coat, independent of means of curing, to improve appearance of an exposed concrete floor at end of Project.

        - Sealing Coat: Uniformly apply a continuous sealing coat of curing and sealing compound to hardened concrete by power spray or roller in accordance with manufacturer's written instructions.

      - JOINT FILLING

Retain this article if joint filling is required.

        - Prepare, clean, and install joint filler in accordance with manufacturer's written instructions.

ACI 302.1R recommends joint filling be deferred as long as possible in concrete floors. Use of polyurea joint fillers may allow joint filling to proceed earlier; verify minimum time period with manufacturer. Typically, up to 30 percent of concrete shrinkage takes place in first month, with 80 to 90 percent during first 12 months. Revise period in first subparagraph below if too short or too long. Joints must be filled before industrial floors can be placed in service.

          - Defer joint filling until concrete has aged at least [one] [six] month(s).

          - Do not fill joints until construction traffic has permanently ceased.

        - Remove dirt, debris, saw cuttings, curing compounds, and sealers from joints; leave contact faces of joints clean and dry.

        - Install semirigid joint filler full depth in saw-cut joints and at least 2 inches (50 mm) deep in formed joints.

        - Overfill joint, and trim joint filler flush with top of joint after hardening.

      - CONCRETE SURFACE REPAIRS

This article provides basic applications for repairing concrete surfaces. Revise or delete to suit Project.

        - Defective Concrete:

          - Repair and patch defective areas when approved by Architect.

          - Remove and replace concrete that cannot be repaired and patched to Architect's approval.

        - Patching Mortar: Mix dry-pack patching mortar, consisting of 1 part portland cement to 2-1/2 parts fine aggregate passing a No. 16 (1.18-mm) sieve, using only enough water for handling and placing.

Insert provision for testing repair technique on a mockup or surface to be concealed later, before repairing surfaces.

        - Repairing Formed Surfaces: Surface defects include color and texture irregularities, cracks, spalls, air bubbles, honeycombs, rock pockets, fins and other projections on the surface, and stains and other discolorations that cannot be removed by cleaning.

          - Immediately after form removal, cut out honeycombs, rock pockets, and voids more than 1/2 inch (13 mm) in any dimension to solid concrete.

            - Limit cut depth to 3/4 inch (19 mm).

            - Make edges of cuts perpendicular to concrete surface.

            - Clean, dampen with water, and brush-coat holes and voids with bonding agent.

            - Fill and compact with patching mortar before bonding agent has dried.

            - Fill form-tie voids with patching mortar or cone plugs secured in place with bonding agent.

          - Repair defects on surfaces exposed to view by blending white portland cement and standard portland cement, so that, when dry, patching mortar matches surrounding color.

            - Patch a test area at inconspicuous locations to verify mixture and color match before proceeding with patching.

            - Compact mortar in place and strike off slightly higher than surrounding surface.

          - Repair defects on concealed formed surfaces that will affect concrete's durability and structural performance as determined by Architect.

        - Repairing Unformed Surfaces:

          - Test unformed surfaces, such as floors and slabs, for finish, and verify surface tolerances specified for each surface.

            - Correct low and high areas.

            - Test surfaces sloped to drain for trueness of slope and smoothness; use a sloped template.

          - Repair finished surfaces containing surface defects, including spalls, popouts, honeycombs, rock pockets, crazing, and cracks in excess of 0.01 inch (0.25 mm) wide or that penetrate to reinforcement or completely through unreinforced sections regardless of width, and other objectionable conditions.

          - After concrete has cured at least 14 days, correct high areas by grinding.

          - Correct localized low areas during, or immediately after, completing surface-finishing operations by cutting out low areas and replacing with patching mortar.

            - Finish repaired areas to blend into adjacent concrete.

Retain one or both of first two subparagraphs below if applicable. First subparagraph uses an underlayment; second, a topping.

          - Correct other low areas scheduled to receive floor coverings with a repair underlayment.

            - Prepare, mix, and apply repair underlayment and primer in accordance with manufacturer's written instructions to produce a smooth, uniform, plane, and level surface.

            - Feather edges to match adjacent floor elevations.

          - Correct other low areas scheduled to remain exposed with repair topping.

            - Cut out low areas to ensure a minimum repair topping depth of 1/4 inch (6 mm) to match adjacent floor elevations.

            - Prepare, mix, and apply repair topping and primer in accordance with manufacturer's written instructions to produce a smooth, uniform, plane, and level surface.

          - Repair defective areas, except random cracks and single holes 1 inch (25 mm) or less in diameter, by cutting out and replacing with fresh concrete.

            - Remove defective areas with clean, square cuts, and expose steel reinforcement with at least a 3/4-inch (19-mm) clearance all around.

            - Dampen concrete surfaces in contact with patching concrete and apply bonding agent.

            - Mix patching concrete of same materials and mixture as original concrete, except without coarse aggregate.

            - Place, compact, and finish to blend with adjacent finished concrete.

            - Cure in same manner as adjacent concrete.

          - Repair random cracks and single holes 1 inch (25 mm) or less in diameter with patching mortar.

            - Groove top of cracks and cut out holes to sound concrete, and clean off dust, dirt, and loose particles.

            - Dampen cleaned concrete surfaces and apply bonding agent.

            - Place patching mortar before bonding agent has dried.

            - Compact patching mortar and finish to match adjacent concrete.

            - Keep patched area continuously moist for at least 72 hours.

        - Perform structural repairs of concrete, subject to Architect's approval, using epoxy adhesive and patching mortar.

        - Repair materials and installation not specified above may be used, subject to Architect's approval.

      - FIELD QUALITY CONTROL

Retain "Special Inspections" or "Testing Agency" Paragraph below.

        - Special Inspections: Owner will engage a special inspector to perform field tests and inspections and prepare testing and inspection reports.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing and inspecting agency to perform tests and inspections and to submit reports.

          - Testing agency to be responsible for providing curing container for composite samples on Site and verifying that field-cured composite samples are cured in accordance with ASTM C31/C31M.

          - Testing agency to immediately report to Architect, Contractor, and concrete manufacturer any failure of Work to comply with Contract Documents.

          - Testing agency to report results of tests and inspections, in writing, to Owner, Architect, Contractor, and concrete manufacturer within 48 hours of inspections and tests.

            - Test reports to include reporting requirements of ASTM C31/C31M, ASTM C39/C39M, and ACI 301, including the following as applicable to each test and inspection:

              - Project name.

              - Name of testing agency.

              - Names and certification numbers of field and laboratory technicians performing inspections and testing.

              - Name of concrete manufacturer.

              - Date and time of inspection, sampling, and field testing.

              - Date and time of concrete placement.

              - Location in Work of concrete represented by samples.

              - Date and time sample was obtained.

              - Truck and batch ticket numbers.

              - Design compressive strength at 28 days.

              - Concrete mixture designation, proportions, and materials.

              - Field test results.

              - Information on storage and curing of samples before testing, including curing method and maximum and minimum temperatures during initial curing period.

              - Type of fracture and compressive break strengths at seven days and 28 days.

        - Batch Tickets: For each load delivered, submit three copies of batch delivery ticket to testing agency, indicating quantity, mix identification, admixtures, design strength, aggregate size, design air content, design slump at time of batching, and amount of water that can be added at Project site.

        - Inspections:

Retain first five subparagraphs below if special inspections are required. Items below are examples of special inspections and are based on IBC requirements; revise to insert other inspections or to suit requirements of other building codes.

          - Headed bolts and studs.

          - Verification of use of required design mixture.

          - Concrete placement, including conveying and depositing.

          - Curing procedures and maintenance of curing temperature.

          - Verification of concrete strength before removal of shores and forms from beams and slabs.

          - Batch Plant Inspections: On a random basis, as determined by Architect.

        - Concrete Tests: Testing of composite samples of fresh concrete obtained in accordance with ASTM C 172/C 172M to be performed in accordance with the following requirements:

Revise frequency in "Testing Frequency" Subparagraph below to suit Project.

          - Testing Frequency: Obtain one composite sample for each day's pour of each concrete mixture exceeding 5 cu. yd. (4 cu. m), but less than 25 cu. yd. (19 cu. m), plus one set for each additional 50 cu. yd. (38 cu. m) or fraction thereof.

            - When frequency of testing provides fewer than five compressive-strength tests for each concrete mixture, testing to be conducted from at least five randomly selected batches or from each batch if fewer than five are used.

          - Slump: ASTM C143/C143M:

            - One test at point of placement for each composite sample, but not less than one test for each day's pour of each concrete mixture.

            - Perform additional tests when concrete consistency appears to change.

Retain "Slump Flow" Subparagraph below for self-consolidating concrete.

          - Slump Flow: ASTM C1611/C1611M:

            - One test at point of placement for each composite sample, but not less than one test for each day's pour of each concrete mixture.

            - Perform additional tests when concrete consistency appears to change.

          - Air Content: ASTM C231/C231M pressure method, for normal-weight concrete; [ASTM C173/C173M volumetric method, for structural lightweight concrete].

            - One test for each composite sample, but not less than one test for each day's pour of each concrete mixture.

          - Concrete Temperature: ASTM C1064/C1064M:

            - One test hourly when air temperature is 40 deg F (4.4 deg C) and below or 80 deg F (27 deg C) and above, and one test for each composite sample.

Retain "Unit Weight" Subparagraph below if structural lightweight concrete is required.

          - Unit Weight: ASTM C567/C567M fresh unit weight of structural lightweight concrete.

            - One test for each composite sample, but not less than one test for each day's pour of each concrete mixture.

          - Compression Test Specimens: ASTM C31/C31M:

            - Cast and laboratory cure two sets of [two] [three] [four] 6-inch (150 mm) by 12-inch (300 mm) or 4-inch (100 mm) by 8-inch (200 mm) cylinder specimens for each composite sample.

Field-cured specimens in first subparagraph below may be required to verify adequacy of curing and protection of concrete, to verify strength for tilt-up concrete and post-tensioning concrete, or to verify strength for removal of shoring and reshoring in multistory construction. Revise number of test specimens if required.

            - Cast, initial cure, and field cure [two] <Insert number> sets of [two] [three] [four] standard cylinder specimens for each composite sample.

Coordinate the number of compression test specimens in last subparagraph above with number of compressive-strength tests in "Compressive-Strength Tests" Subparagraph below.

          - Compressive-Strength Tests: ASTM C39/C39M.

            - Test one set of [two] [three] [four] laboratory-cured specimens at seven days and one set of two specimens at 28 days.

Revise age at testing in first subparagraph below, or delete if not required. Limit field testing to concrete in designated structural elements if not required throughout Project.

            - Test one set of [two] [three] [four] field-cured specimens at seven days and one set of two specimens at 28 days.

            - A compressive-strength test to be the average compressive strength from a set of two specimens obtained from same composite sample and tested at age indicated.

Retain first subparagraph below if field-cured specimens are required.

          - When strength of field-cured cylinders is less than 85 percent of companion laboratory-cured cylinders, Contractor to evaluate operations and provide corrective procedures for protecting and curing in-place concrete.

          - Strength of each concrete mixture will be satisfactory if every average of any three consecutive compressive-strength tests equals or exceeds specified compressive strength, and no compressive-strength test value falls below specified compressive strength by more than 500 psi (3.4 MPa) if specified compressive strength is 5000 psi (34.5 MPa), or no compressive strength test value is less than 10 percent of specified compressive strength if specified compressive strength is greater than 5000 psi (34.5 MPa).

          - Nondestructive Testing: Impact hammer, sonoscope, or other nondestructive device may be permitted by Architect but will not be used as sole basis for approval or rejection of concrete.

          - Additional Tests:

            - Testing and inspecting agency to make additional tests of concrete when test results indicate that slump, air entrainment, compressive strengths, or other requirements have not been met, as directed by Architect.

            - Testing and inspecting agency may conduct tests to determine adequacy of concrete by cored cylinders complying with ASTM C42/C42M or by other methods as directed by Architect.

              - Acceptance criteria for concrete strength to be in accordance with ACI 301 (ACI 301M), Section 1.6.6.3.

          - Additional testing and inspecting, at Contractor's expense, will be performed to determine compliance of replaced or additional work with specified requirements.

          - Correct deficiencies in the Work that test reports and inspections indicate do not comply with the Contract Documents.

Retain paragraph below if measurements of floor flatness and levelness tolerances are required.

        - Measure floor and slab flatness and levelness in accordance with ASTM E1155 (ASTM E1155M) within [24] [48] [72] <Insert number> hours of completion of floor finishing and promptly report test results to Architect.

      - PROTECTION

        - Protect concrete surfaces as follows:

          - Protect from petroleum stains.

          - Diaper hydraulic equipment used over concrete surfaces.

          - Prohibit vehicles from interior concrete slabs.

          - Prohibit use of pipe-cutting machinery over concrete surfaces.

          - Prohibit placement of steel items on concrete surfaces.

          - Prohibit use of acids or acidic detergents over concrete surfaces.

          - Protect liquid floor treatment from damage and wear during the remainder of construction period. Use protective methods and materials, including temporary covering, recommended in writing by liquid floor treatments installer.

Retain subparagraph below when Project includes concrete floors scheduled to receive surface hardener of polished concrete finish.

          - Protect concrete surfaces scheduled to receive surface hardener or polished concrete finish using Floor Slab Protective Covering.

END OF SECTION 033000