Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 042613 - MASONRY VENEER

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Access Manufacturer-Provided, AIA MasterSpec-Based Sections:

<Double click here for this Section based on specific manufacturer’s products set as Basis-of-Design at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED 2009, LEED v4, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using the hypertext links.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Brick.

          - Concrete masonry units.

          - Concrete face brick.

          - Mortar materials.

          - Ties and anchors.

          - Embedded flashing.

          - Accessories.

          - Mortar mixes.

        - Products Installed but not Furnished under This Section:

          - Cast-stone trim in masonry veneer.

          - Stone trim units in unit masonry.

          - Steel lintels in masonry veneer.

          - Steel shelf angles for supporting masonry veneer.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Retain first subparagraph below if integrated exterior mockup is required and specified in Section 014339 "Mockups" instead of this Section.

          - Section 014339 "Mockups" for integrated exterior mockup requirements.

          - Section 019119.43 "Exterior Enclosure Commissioning."

Usually delete option in first subparagraph below and specify dovetail slots in concrete formwork Section.

          - Section 031000 "Concrete Forming and Accessories" for [ installing] dovetail slots or channel slots for masonry-veneer anchors.

          - Section 044200 "Exterior Stone Cladding" for stone trim secured with stone anchors.

          - Section 044313.13 "Anchored Stone Masonry Veneer" for thin stone trim set as anchored veneer.

          - Section 044313.16 "Adhered Stone Masonry Veneer" for thin stone trim set as adhered veneer.

Delete first subparagraph below if attachment of anchor sections to structural steel is included in this Section.

          - Section 051200 "Structural Steel Framing" for installing anchor sections of adjustable masonry anchors for connecting to structural steel frame.

          - Section 071900 "Water Repellents" for water repellents applied to unit masonry assemblies.

Coordinate subparagraph below with referenced Section. Metal through-wall flashing is included in this Section.

          - Section 076200 "Sheet Metal Flashing and Trim" for [ exposed] sheet metal flashing and for furnishing manufactured reglets installed in masonry joints.

      - ALLOWANCES

Retain this article if products and Work included in this Section are covered by lump-sum, unit-cost, or quantity allowances.

        - See Section 012100 "Allowances" for description of allowances affecting items specified in this Section.

      - DEFINITIONS

Retain terms that remain after this Section has been edited. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - CMU(s): Concrete masonry unit(s).

      - PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a conference.

        - Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data: For each type of product.

        - Shop Drawings: For the following:

          - Masonry Units: Indicate sizes, profiles, coursing, and locations of special shapes.

Retain "Fabricated Flashing" Subparagraph below for flashing material that is specially fabricated for corners, end dams, etc.

          - Fabricated Flashing: Detail corner units, end-dam units, and other special applications.

        - Samples for Initial Selection:

          - Clay face brick[, in the form of straps of five or more bricks].

          - Glazed brick.

          - Decorative CMUs, in the form of small-scale units.

          - Concrete face brick, in the form of small-scale units.

          - Colored mortar.

          - Weep/cavity vents.

Delete "Samples for Initial Selection" Paragraph above if colors and other characteristics are preselected and specified or scheduled. Retain "Samples for Verification" Paragraph below with or without above.

        - Samples for Verification: For each type and color of the following:

          - Clay face brick[, in the form of straps of five or more bricks].

          - Glazed brick.

          - Special brick shapes.

          - Decorative CMUs.

          - Concrete face brick.

          - [Pigmented] [and] [colored-aggregate] mortar. Make Samples using same sand and mortar ingredients to be used on Project.

          - Weep/cavity vents.

          - Cavity drainage material.

          - Accessories embedded in masonry.

        - Sustainable Design Submittals:

          - <Double click to insert sustainable design text for regional materials.>

      - INFORMATIONAL SUBMITTALS

Information submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Retain "List of Materials Used in Constructing Mockups" Paragraph below for critical work where record of mockup materials is desired.

        - List of Materials Used in Constructing Mockups: List generic product names together with manufacturers, manufacturers' product names, model numbers, lot numbers, batch numbers, source of supply, and other information as required to identify materials used. Include mix proportions for mortar and grout and source of aggregates.

          - Submittal is for information only. Receipt of list does not constitute approval of deviations from the Contract Documents unless such deviations are specifically brought to the attention of Architect and approved in writing.

Usually retain "Material Certificates" Paragraph below. Material certificates are required for all masonry constructed under TMS 402/602.

        - Material Certificates: For each type and size of the following:

          - Masonry units.

Retain second option in first subparagraph below if required by authorities having jurisdiction or if the added assurance of quality that test reports provide is desired.

            - Include [data on material properties] [material test reports substantiating compliance with requirements].

            - For brick, include size-variation data verifying that actual range of sizes falls within specified tolerances.

            - For exposed brick, include test report for efflorescence in accordance with ASTM C67/C67M.

            - For surface-coated brick, include test report for durability of surface appearance after 50 cycles of freezing and thawing in accordance with ASTM C67/C67M[ or a list of addresses of buildings in Project's area where proposed brick has been used successfully and with a history of durability].

          - Integral water repellant used in decorative CMUs.

          - Cementitious materials. Include name of manufacturer, brand name, and type.

          - Mortar admixtures.

          - Preblended, dry mortar mixes. Include description of type and proportions of ingredients.

          - Anchors, ties, and metal accessories.

Coordinate "Qualification Statements" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Statements: For [testing agency].

        - Mix Designs: For each type of mortar. Include description of type and proportions of ingredients.

          - Include test reports for mortar mixes required to comply with property specification. Test in accordance with ASTM C109/C109M for compressive strength, ASTM C1506 for water retention, and ASTM C91/C91M for air content.

        - [Cold-Weather][ and][Hot-Weather] Procedures: Detailed description of methods, materials, and equipment to be used to comply with requirements.

      - QUALITY ASSURANCE

        - Qualifications:

Include "Installers" Paragraph below if requiring IMI training for masonry flashing installers.

          - Installers: All masonry flashing installers must complete the International Masonry Institute Flashing Upgrade training course.

Retain "Testing Agency" Paragraph below if Contractor selects testing agency.

          - Testing Agency: Qualified in accordance with ASTM C1093 for testing indicated.

      - MOCKUPS

        - Sample Panels: Build sample panels to verify selections made under Sample submittals and to demonstrate aesthetic effects. Comply with requirements in Section 014000 "Quality Requirements" for mockups.

          - Build sample panels for [each type of exposed unit masonry construction] [typical exterior wall] [typical interior wall] [typical exterior and interior walls] in sizes approximately [48 inches (1219 mm)] [60 inches (1524 mm)] <Insert dimension> long by [36 inches (914 mm)] [48 inches (1219 mm)] <Insert dimension> high[ by full thickness].

          - Build sample panels facing south.

          - Where masonry is to match existing, build panels adjacent and parallel to existing surface.

          - Clean[ one-half of] exposed faces of panels with masonry cleaner indicated.

          - Protect approved sample panels from the elements with weather-resistant membrane.

          - Approval of sample panels is for color, texture, and blending of masonry units; relationship of mortar and sealant colors to masonry unit colors; tooling of joints; aesthetic qualities of workmanship; and other material and construction qualities specifically approved by Architect in writing.

            - Approval of sample panels does not constitute approval of deviations from the Contract Documents contained in sample panels unless such deviations are specifically approved by Architect in writing.

Retain last option in "Wall Mockups" Paragraph below if integrated exterior mockup is required.

        - Wall Mockups: Build mockups [to verify selections made under Sample submittals] [to demonstrate aesthetic effects] [to set quality standards for materials and execution] [and] [to set quality standards for installation]. [ See Section 014339 "Mockups" for additional construction requirements for integrated exterior mockups.]

Retain first subparagraph below for large-scale mockup or include in Section 014000 "Quality Requirements." Indicate portion of wall represented by mockup on Drawings or draw mockup as separate element.

          - Build mockup [as indicated on Drawings] <Insert mockup requirements>.

Retain first subparagraph below for limited mockups.

          - Build mockups for [each type of exposed unit masonry construction] [typical exterior wall] in sizes approximately [48 inches (1219 mm)] [60 inches (1524 mm)] [72 inches (1829 mm)] [96 inches (2438 mm)] <Insert dimension> long by [36 inches (914 mm)] [48 inches (1219 mm)] [60 inches (1524 mm)] [72 inches (1829 mm)] <Insert dimension> high by full thickness, including face and backup wythes and accessories.

            - Include a sealant-filled joint at least 16 inches (406 mm) long in [each] mockup.

            - Include lower corner of window opening[, framed with stone trim,] at upper corner of exterior wall mockup. Make opening approximately 12 inches (305 mm) wide by 16 inches (406 mm) high.

            - Include through-wall flashing installed for a 24-inch (610-mm) length in corner of exterior wall mockup approximately 16 inches (406 mm) down from top of mockup, with a 12-inch (305-mm) length of flashing left exposed to view (omit masonry above half of flashing).

            - Include [metal] [wood] studs, sheathing, [water-resistive barrier] [sheathing joint-and-penetration treatment] [air barrier], veneer anchors, flashing[, cavity drainage material], and weep holes in exterior masonry-veneer wall mockup.

          - Where masonry is to match existing, erect mockups adjacent and parallel to existing surface.

          - Clean[ one-half of] exposed faces of mockups with masonry cleaner as indicated.

          - Protect accepted mockups from the elements with weather-resistant membrane.

          - Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing.

Retain subparagraph below if the intention is to make an exception to the default requirement in Section 014000 "Quality Requirements" for demolishing and removing mockups.

          - Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

      - DELIVERY, STORAGE, AND HANDLING

        - Store masonry units on elevated platforms in a dry location. If units are not stored in an enclosed location, cover tops and sides of stacks with waterproof sheeting, securely tied. If units become wet, do not install until they are dry.

Delete first two paragraphs below if using preblended, dry mortar mix.

        - Store cementitious materials on elevated platforms, under cover, and in a dry location. Do not use cementitious materials that have become damp.

        - Store aggregates where grading and other required characteristics can be maintained and contamination avoided.

Always retain first paragraph below in case Contractor uses a preblended, dry mortar mix.

        - Deliver preblended, dry mortar mix in moisture-resistant containers. Store preblended, dry mortar mix in delivery containers on elevated platforms in a dry location or in covered weatherproof dispensing silos.

        - Store masonry accessories, including metal items, to prevent corrosion and accumulation of dirt and oil.

      - FIELD CONDITIONS

        - Protection of Masonry: During construction, cover tops of veneer, projections, and sills with waterproof sheeting at end of each day's work. Cover partially completed masonry when construction is not in progress.

Increase extent of cover in subparagraph below as needed to suit local climatic conditions.

          - Extend cover a minimum of 24 inches (610 mm) down face of veneer, and hold cover securely in place.

        - Stain Prevention: Prevent grout, mortar, and soil from staining the face of masonry. Immediately remove grout, mortar, and soil that come in contact with masonry.

          - Protect base of walls from rain-splashed mud and from mortar splatter by spreading coverings on ground and over wall surface.

          - Protect sills, ledges, and projections from mortar droppings.

          - Protect surfaces of window and door frames, as well as similar products with painted and integral finishes, from mortar droppings.

          - Turn scaffold boards near the wall on edge at the end of each day to prevent rain from splashing mortar and dirt onto completed masonry.

        - Cold-Weather Requirements: Do not use frozen materials or materials mixed or coated with ice or frost. Do not build on frozen substrates. Remove and replace unit masonry damaged by frost or by freezing conditions. Comply with cold-weather construction requirements contained in TMS 602.

          - Cold-Weather Cleaning: Use liquid cleaning methods only when air temperature is 40 deg F (4 deg C) and higher and will remain so until masonry has dried, but not less than seven days after completing cleaning.

        - Hot-Weather Requirements: Comply with hot-weather construction requirements contained in TMS 602.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - SOURCE LIMITATIONS

Retain this article to limit sources for the entire Section. Source limitations may also be specified in individual articles if desired.

        - Obtain [exposed masonry units] [cementitious mortar components] [and] [mortar aggregate] from single [source] [producer] [or] [manufacturer].

        - For [exposed masonry units] [and] [cementitious mortar components], obtain each color and grade from single source with resources to provide materials of consistent quality in appearance and physical properties.

      - UNIT MASONRY, GENERAL

        - Masonry Standard: Comply with TMS 602, except as modified by requirements in the Contract Documents.

        - Defective Units: Referenced masonry unit standards may allow a certain percentage of units to contain chips, cracks, or other defects exceeding limits stated. Do not use units where such defects will be exposed in the completed Work[ and will be within 20 ft. (6 m) vertically and horizontally of a walking surface].

See BIA Technical Notes 16B and NCMA TEK 7-1D for information on determining fire-resistance ratings of masonry walls.

        - Fire-Resistance Ratings: Comply with requirements for fire-resistance-rated assembly designs indicated.

Retain subparagraph below if required by authorities having jurisdiction. First option is typical and recommended by NCMA.

          - Where fire-resistance-rated construction is indicated, [use the equivalent thickness method for masonry units in accordance with ACI 216.1] [units are listed by UL or a qualified testing agency acceptable to authorities having jurisdiction].

      - BRICK

        - <Double click to insert sustainable design text for brick.>

        - General: Provide shapes indicated and as follows, with exposed surfaces matching finish and color of exposed faces of adjacent units.

          - For ends of sills and caps and for similar applications that would otherwise expose unfinished brick surfaces, provide units without cores or frogs and with exposed surfaces finished.

On Drawings, indicate details of special conditions and special shapes required. Revise option(s) below to suit Project.

          - Provide special shapes for applications [where stretcher units cannot accommodate special conditions, including corners, movement joints, bond beams, sashes, and lintels] [requiring brick of size, form, color, and texture on exposed surfaces that cannot be produced by sawing] [where shapes produced by sawing would result in sawed surfaces being exposed to view].

Retain third option in "Clay Face Brick" Paragraph below if hollow bricks are acceptable. Hollow bricks use less material and energy to make transport. First three options for type apply to ASTM C216 (facing brick); last three options apply to ASTM C652 (hollow brick).

        - Clay Face Brick: [Facing brick complying with ASTM C216] [or] [hollow brick complying with ASTM C652, Class H40V (void areas between 25 and 40 percent of gross cross-sectional area)], Grade [SW] [MW or SW], Type [FBX] [FBS] [FBA] [or] [HBX] [HBS] [HBA].

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Consider retaining "Initial Rate of Absorption" Subparagraph below; it eliminates the need to wet brick before laying. Before retaining, verify that brick selected complies with requirements. See the Evaluations.

          - Initial Rate of Absorption: Less than 30 g/30 sq. in. (30 g/194 sq. cm) per minute when tested in accordance with ASTM C67/C67M.

Requirement in "Efflorescence" Subparagraph below does not, by itself, prevent efflorescence. See the Evaluations.

          - Efflorescence: Provide brick that has been tested in accordance with ASTM C67/C67M and is rated "not effloresced."

Delete "Surface Coating" Subparagraph below if not using surface-coated brick.

          - Surface Coating: Brick with colors or textures produced by application of coatings withstand 50 cycles of freezing and thawing in accordance with ASTM C67/C67M with no observable difference in the applied finish when viewed from 10 ft. (3 m)[ or have a history of successful use in Project's area].

Retain pertinent size selections in "Size (Actual Dimensions)" Subparagraph below. Coordinate with coursing and verify availability of sizes with manufacturer.

          - Size (Actual Dimensions): [2-3/4 inches (70 mm)] [3 inches (76 mm)] [3-1/2 inches (89 mm)] [3-5/8 inches (92 mm)] <Insert dimension> wide by [2-1/4 inches (57 mm)] [2-3/4 inches (70 mm)] [2-5/8 inches (67 mm)] [2-13/16 inches (71 mm)] [3-1/2 inches (89 mm)] [3-5/8 inches (92 mm)] [7-1/2 inches (190 mm)] [7-5/8 inches (194 mm)] <Insert dimension> high by [7-1/2 inches (190 mm)] [7-5/8 inches (194 mm)] [8 inches (203 mm)] [9-5/8 inches (244 mm)] [11-1/2 inches (292 mm)] [11-5/8 inches (295 mm)] <Insert dimension> long.

          - Application: Use where brick is exposed unless otherwise indicated.

          - [Where shown to "match existing," ]provide clay face brick matching color range, texture, and size of existing adjacent brickwork.

            - <Insert information on existing brick if known>.

Delete "Color and Texture" Subparagraph below if brick is specified by product name. First three options are examples of descriptive requirements for appearance where proprietary specifications and allowances cannot be used. Retain last option if using allowance.

          - Color and Texture: [Medium brown, wire cut] [Full-range red, sand molded] [Buff, velour] [Match Architect's samples] [As selected by Architect].

Retain applicable options in "Glazed Brick" Paragraph below. Hollow brick requires less material and energy to make and transport. First two options for grade apply to ASTM C216 (facing brick) and ASTM C652 (hollow brick); last two options for grade apply to ASTM C1405. First three options for type apply to ASTM C216 (facing brick); next three options for type apply to ASTM C652 (hollow brick), and the last two options for class apply to ASTM C1405 only.

        - Glazed Brick: [Facing brick complying with ASTM C216, with glaze complying with ASTM C126;] [Single-fired glazed brick complying with ASTM C1405, Division Solid] [Hollow brick complying with ASTM C652, Class H40V (void areas between 25 and 40 percent of gross cross-sectional area), with glaze complying with ASTM C126] [or] [Single-fired glazed brick complying with ASTM C1405, Division H40V (void areas between 25 and 40 percent of gross cross-sectional area)], Grade [SW] [MW or SW] [S (Select)] [SS (Select Sized)], Type [FBX] [FBS] [FBA] [or] [HBX] [HBS] [HBA] [, Exterior Class] [, Interior Class].

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Verify availability of sizes with local suppliers, and revise to suit Project.

          - Size (Actual Dimensions): 3-5/8 inches (92 mm) wide by [2-1/4 inches (57 mm)] [2-3/4 inches (70 mm)] [3-5/8 inches (92 mm)] [7-5/8 inches (194 mm)] high by [7-5/8 inches (194 mm)] [8 inches (203 mm)] [11-5/8 inches (295 mm)] long.

Retain first subparagraph below if units with two opposite exposed faces are required.

          - Provide Type I (single-faced units) where only one finished face is exposed when units are installed, and Type II (double-faced units) where two opposite finished faces are exposed when units are installed.

          - Application: Use where [brick is exposed unless otherwise indicated] [indicated].

Retain one of three options in "Colors" Subparagraph below; otherwise, retain second subparagraph below.

          - Colors: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range].

          - [Where shown to "match existing," ]provide glazed brick matching color range, texture, and size of existing adjacent brickwork.

            - <Insert information on existing brick if known>.

      - CONCRETE MASONRY UNITS

        - <Double click to insert sustainable design text for regional materials.>

        - Shapes: Provide shapes indicated and as follows, with exposed surfaces matching exposed faces of adjacent units unless otherwise indicated.

          - Provide special shapes for lintels, corners, jambs, sashes, movement joints, headers, bonding, and other special conditions.

Retain "Integral Water Repellant" Paragraph below for increased water resistance of units if required. If retaining, also retain water-repellent mortar admixture.

        - Integral Water Repellent: Provide units made with integral water repellent [for exposed units] [and] [where indicated].

          - Integral Water Repellent: Liquid polymeric, integral water-repellent admixture that does not reduce flexural bond strength. Units made with integral water repellent, when tested in accordance with ASTM E514/E514M as a wall assembly made with mortar containing integral water-repellent manufacturer's mortar additive, with test period extended to 24 hours, will show no visible water or leaks on the back of test specimen.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Decorative CMUs: ASTM C90, [normal weight] [medium weight] [lightweight].

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Size (Width): Manufactured to dimensions 3/8 inch (10 mm) less than nominal dimensions.

Retain one of six options in "Pattern and Texture" Subparagraph below, and revise to suit Project. Retain last option if appearance is critical.

          - Pattern and Texture: [Standard pattern, ground-face finish] [Standard pattern, split-face finish] [Standard pattern, split-ribbed finish] [Scored vertically to appear square in stacked bond, standard finish] [Triple scored vertically to appear as soldier courses in stacked bond, standard finish] <Insert pattern>. [ Match Architect's samples.]

          - Colors: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range].

Retain "Special Aggregate" Subparagraph below if special aggregate is required to match sample.

          - Special Aggregate: Provide units made with aggregate matching aggregate in Architect's sample.

        - Concrete Face Brick: ASTM C1634, [normal weight] [medium weight] [lightweight].

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Size (Actual Dimensions): 3-5/8 inches (92 mm) wide by [2-1/4 inches (57 mm)] [2-3/4 inches (70 mm)] [3-5/8 inches (92 mm)] high by [7-5/8 inches (194 mm)] [11-5/8 inches (295 mm)] [15-5/8 inches (397 mm)] long.

          - Texture: [Split-face] [Ground-face] finish <Insert description>.[ Match Architect's samples]

          - Colors: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's full range].

Retain "Special Aggregate" Subparagraph below if special aggregate is required to match sample.

          - Special Aggregate: Provide units made with aggregate matching aggregate in Architect's sample.

      - MORTAR MATERIALS

Coordinate requirements in this article with those in "Mortar Mixes" Article.

        - <Double click to insert sustainable design text for mortar and grout.>

        - Portland Cement: ASTM C150/C150M, Type I or II, except Type III may be used for cold-weather construction. Provide natural color or white cement as required to produce mortar color indicated.

Requirement in subparagraph below can help reduce the likelihood of efflorescence.

          - Alkali content will not be more than 0.1 percent when tested in accordance with ASTM C114.

        - Hydrated Lime: ASTM C207, Type S.

Mix in "Portland Cement-Lime Mix" Paragraph below allows better control of color than job-mixed, portland cement-lime mortar. If retaining below, also retain "Portland Cement" and "Hydrated Lime" paragraphs above.

        - Portland Cement-Lime Mix: Packaged blend of portland cement and hydrated lime containing no other ingredients.

ASTM C91/C91M does not require masonry cement to comply with any performance tests for flexural bond strength; confirm Project requirements. See the Evaluations.

        - Masonry Cement: ASTM C91/C91M.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Mortar Cement: ASTM C1329/C1329M.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Mortar Pigments" Paragraph below for colored cement or for pigments added at Project site.

        - Mortar Pigments: Natural and synthetic iron oxides and chromium oxides, compounded for use in mortar mixes and complying with ASTM C979/C979M. Use only pigments with a record of satisfactory performance in masonry mortar.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Mixes in "Colored Cement Products" Paragraph below allow better control of color than job-mixed colored mortar. If retaining, also retain paragraphs above that specify materials included in the mixes retained below.

        - Colored Cement Products: Packaged blend made from [portland cement and hydrated lime] [masonry cement] [or] [mortar cement] and mortar pigments, all complying with specified requirements, and containing no other ingredients.

          - Colored Portland Cement-Lime Mix:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Colored Masonry Cement:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Formulate blend as required to produce color indicated or, if not indicated, as selected from manufacturer's standard colors.

Retain one or both subparagraphs below to suit types of cement retained above. Percentages are for pigments containing only metallic oxides. If using pigments containing carbon black, carbon black must be limited to 2 percent of portland cement by weight or 1 percent of masonry or mortar cement.

          - Pigments do not exceed 10 percent of portland cement by weight.

          - Pigments do not exceed 5 percent of [masonry cement] [or] [mortar cement] by weight.

Mixes in "Preblended Dry Mortar Mix" Paragraph below allow better control over quality and produce less waste than job-mixed mortar. If retaining, also retain paragraphs above that specify materials included in the mixes retained below.

        - Preblended Dry Mortar Mix: Packaged blend made from [portland cement and hydrated lime] [masonry cement] [or] [mortar cement], sand, [mortar pigments,] [water repellents,] and admixtures and complying with ASTM C1714/C1714M.

          - Preblended Dry Portland Cement Mortar Mix:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Preblended Dry Masonry Cement Mortar Mix

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Aggregate for Mortar: ASTM C144.

          - For mortar that is exposed to view, use washed aggregate consisting of natural sand or crushed stone.

          - For joints less than 1/4 inch (6.4 mm) thick, use aggregate graded with 100 percent passing the No. 16 (1.18-mm) sieve.

          - White-Mortar Aggregates: Natural white sand or crushed white stone.

          - Colored-Mortar Aggregates: Natural sand or crushed stone of color necessary to produce required mortar color.

Retain first option in "Cold-Weather Admixture" Paragraph below for products complying with ASTM C494/C494M, intended for concrete admixtures; however, many available products comply with this standard. Retain second option for products complying with ASTM C1384. Appendix X1 in ASTM C270 and BIA Technical Notes 8 generally recommend not using admixtures unless they are known to have no adverse effects. Before approving the use of cold-weather admixtures, verify their acceptability by laboratory testing with mortar mix used.

        - Cold-Weather Admixture: Nonchloride, noncorrosive, accelerating admixture complying with [ASTM C494/C494M, Type C] [ASTM C1384], and recommended by manufacturer for use in masonry mortar of composition indicated.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Water-Repellant Admixture" Paragraph below if integral water repellent is used in CMUs.

        - Water-Repellent Admixture: Liquid water-repellent mortar admixture intended for use with CMUs containing integral water repellent from same manufacturer.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Water: Potable.

      - TIES AND ANCHORS

        - General: Ties and anchors extend at least 1-1/2 inches (38 mm) into veneer but with at least a 5/8-inch (16-mm) cover on outside face.

        - Materials: Provide ties and anchors specified in this article that are made from materials that comply with the following unless otherwise indicated:

"Mill-Galvanized, Carbon-Steel Wire" Subparagraph below is not allowed by TMS 402 for anchors and ties in exterior walls or interior walls where humidity exceeds 75 percent.

          - Mill-Galvanized, Carbon-Steel Wire: ASTM A1064/A1064M, with ASTM A641/A641M, Class 1 coating.

          - Hot-Dip Galvanized, Carbon-Steel Wire: ASTM A1064/A1064M, with ASTM A153/A153M, Class B-2 coating.

Retain first option in "Stainless Steel Wire" Subparagraph below unless higher corrosion resistance of Type 316 is required.

          - Stainless Steel Wire: ASTM A580/A580M, [Type 304] [Type 316].

"Galvanized-Steel Sheet" Subparagraph below is not allowed by TMS 402 for anchors and ties in exterior walls or interior walls where humidity exceeds 75 percent.

          - Galvanized-Steel Sheet: ASTM A653/A653M, Commercial Steel, G60 (Z180) zinc coating.

          - Steel Sheet, Galvanized after Fabrication: ASTM A1008/A1008M, Commercial Steel, with ASTM A153/A153M, Class B coating.

Retain first option in "Stainless Steel Sheet" Subparagraph below unless higher corrosion resistance of Type 316 is required.

          - Stainless Steel Sheet: ASTM A240/A240M or ASTM A666, [Type 304] [Type 316].

TMS 402 requires corrugated-metal veneer ties be at least 0.030 inch (0.76 mm) thick and requires closer spacing for veneer ties less than 0.060 inch (1.5 mm) thick. Corrugated metal ties are typically only used with wood stud backing in residential applications; most backings require adjustable anchors.

        - Corrugated-Metal Ties: Metal strips not less than 7/8 inch (22 mm) wide with corrugations having a wavelength of 0.3 to 0.5 inch (7.6 to 13 mm) and an amplitude of 0.06 to 0.10 inch (1.5 to 2.5 mm) made from [0.0336-inch- (0.85-mm-) thick, steel sheet, galvanized after fabrication] [0.0635-inch- (1.61-mm-) thick, steel sheet, galvanized after fabrication] [0.0312-inch- (0.79-mm-) thick, stainless steel sheet] [0.0625-inch- (1.59-mm-) thick, stainless steel sheet].

        - Adjustable Anchors for Connecting to Structural Steel Framing: Provide anchors that allow vertical or horizontal adjustment but resist tension and compression forces perpendicular to plane of wall.

          - Anchor Section for Welding to Steel Frame: Crimped 1/4-inch- (6.4-mm-) diameter, [hot-dip galvanized steel] [stainless steel] wire.[ Mill-galvanized wire may be used at interior walls unless otherwise indicated.]

          - Tie Section: Triangular-shaped wire tie made from [0.187-inch- (4.76-mm-)] [0.25-inch- (6.4-mm-)] diameter, [hot-dip galvanized steel] [stainless steel] wire.[ Mill-galvanized wire may be used at interior walls unless otherwise indicated.]

        - Adjustable Anchors for Connecting to Concrete: Provide anchors that allow vertical or horizontal adjustment but resist tension and compression forces perpendicular to plane of wall.

Retain "Connector Section" and "Tie Section" subparagraphs below; otherwise, retain "Corrugated-Metal Ties" Subparagraph below.

          - Connector Section: [Dovetail] [Channel] tabs for inserting into [dovetail] [channel] slots in concrete and attached to tie section; formed from [0.060-inch- (1.52-mm-) thick, steel sheet, galvanized after fabrication] [0.105-inch- (2.66-mm-) thick, steel sheet, galvanized after fabrication] [0.062-inch- (1.59-mm-) thick, stainless steel sheet] [0.109-inch- (2.78-mm-) thick, stainless steel sheet].

            - [0.064-inch- (1.63-mm-)] [0.108-inch- (2.74-mm-)] thick, galvanized-steel sheet may be used at interior walls unless otherwise indicated.

          - Tie Section: Triangular-shaped wire tie made from [0.187-inch- (4.76-mm-)] [0.25-inch- (6.4-mm-)] diameter, [hot-dip galvanized steel] [stainless steel] wire.[ Mill-galvanized wire may be used at interior walls unless otherwise indicated.]

          - Corrugated-Metal Ties: Metal strips not less than 7/8 inch (22 mm) wide with corrugations having a wavelength of 0.3 to 0.5 inch (7.6 to 13 mm) and an amplitude of 0.06 to 0.10 inch (1.5 to 2.5 mm) made from [0.0635-inch- (1.61-mm-) thick steel sheet, galvanized after fabrication] [0.0785-inch- (1.99-mm-) thick steel sheet, galvanized after fabrication] [0.1084-inch- (2.75-mm-) thick steel sheet, galvanized after fabrication] [0.0625-inch- (1.59-mm-) thick, stainless steel sheet] [0.0781-inch- (1.98-mm-) thick, stainless steel sheet] [0.1094-inch- (2.78-mm-) thick, stainless steel sheet] with [dovetail] [channel] tabs for inserting into dovetail slots in concrete.

            - [0.064-inch- (1.63-mm-)] [0.079-inch- (2.01-mm-)] [0.108-inch- (2.74-mm-)] thick, galvanized sheet may be used at interior walls unless otherwise indicated.

        - Adjustable Masonry-Veneer Anchors:

          - General: Provide anchors that allow vertical adjustment but resist a 100 lbf (445 N) load in both tension and compression perpendicular to plane of wall without deforming or developing play in excess of 1/16 inch (1.6 mm).

          - Fabricate sheet metal anchor sections and other sheet metal parts from [0.0785-inch- (1.99-mm-) thick steel sheet, galvanized after fabrication] [0.1084-inch- (2.75-mm-) thick steel sheet, galvanized after fabrication] [0.0781-inch- (1.98-mm-) thick, stainless steel sheet] [0.1094-inch- (2.78-mm-) thick, stainless steel sheet].

          - Fabricate wire ties from [0.187-inch- (4.76-mm-)] [0.25-inch- (6.4-mm-)] diameter, [hot-dip galvanized steel] [stainless steel] wire unless otherwise indicated.

Usually retain "Contractors Option" Subparagraph below along with the acceptable types of anchors.

          - Contractor's Option: Unless otherwise indicated, provide any of the adjustable masonry-veneer anchors specified.

          - Masonry-Veneer Anchors; Vertical Slotted L-Plate: Rib-stiffened, sheet metal anchor section with screw holes at top and bottom, projecting vertical leg with slotted hole for wire tie[ and washer at face of insulation].

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Masonry-Veneer Anchors; Double-Pintle Plate: Rib-stiffened, sheet metal anchor section with screw holes at top and bottom, projecting horizontal leg with slots for vertical legs of double pintle wire tie.[ Provide with seismic tie, clip, and continuous wire in veneer.]

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Masonry-Veneer Anchors; Slotted Plate: Sheet metal anchor section, with screw holes at top and bottom; and raised rib-stiffened strap, stamped into center to provide a slot between strap and base for wire tie.[ Use self-adhering tape to seal penetration behind anchor plate.]

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Masonry-Veneer Anchors; Slotted Plate with Prongs: Sheet metal anchor section, with screw holes at top and bottom; top and bottom ends bent to form pronged legs of length to match thickness of insulation; and raised rib-stiffened strap, stamped into center to provide a slot between strap and base for wire tie.[ Use self-adhering tape to seal penetration behind anchor plate.]

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Masonry-Veneer Anchors; Single-Barrel Screw: Self-drilling, single-barrel screw designed to receive wire tie. Screw has a smooth barrel the same thickness as insulation[ with factory-installed gasketed washer to seal at face of insulation and sheathing] [ and a coating to reduce thermal conductivity].[ Provide with seismic tie, clip, and continuous wire in veneer.]

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Masonry-Veneer Anchors; Single-Barrel Screw with Double-Pintle Wingnut: Self-drilling, single-barrel screw with [wingnut head] [thermally resistant wingnut head] [thermally resistant clip] designed to receive double-pintle wire tie. Screw has a smooth barrel the same thickness as insulation[ with factory-installed gasketed washer to seal at face of insulation and sheathing] [ and a coating to reduce thermal conductivity].[ Provide with seismic tie, clip, and continuous wire in veneer.]

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Masonry-Veneer Anchors; Seismic-Pintle Plate: Rib-stiffened, sheet metal anchor section with screw holes at top and bottom, projecting leg with slotted hole for vertical leg of seismic pintle tie. Tie is rib-stiffened, sheet metal bent plate with down-turned leg to fit in anchor slot and with integral tabs to hold continuous wire in veneer.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Fasteners in "Polymer-Coated, Steel Drill Screws for Steel Studs" Subparagraph below are for steel studs from 0.033 to 0.112 inch (0.8 to 2.8 mm) thick.

          - Polymer-Coated, Steel Drill Screws for Steel Studs: ASTM C954 except manufactured with hex washer head and neoprene or EPDM washer, No. 10 (4.83 mm) diameter by length required to penetrate steel stud flange with not less than three exposed threads, and with organic polymer coating with salt-spray resistance to red rust of more than 800 hours in accordance with ASTM B117.

See the Evaluations and BIA Technical Notes 28B for use of stainless steel screws.

          - Stainless Steel Drill Screws for Steel Studs: ASTM C954 except manufactured with hex washer head and neoprene or EPDM washer, No. 10 (4.83 mm) diameter by length required to penetrate steel stud flange with not less than three exposed threads; either made from Type 410 stainless steel or made with a carbon-steel drill point and 300 Series stainless steel shank.

      - EMBEDDED FLASHING

See the Evaluations for discussion of flashing materials before revising this article.

        - Metal Flashing: Provide metal flashing complying with SMACNA's "Architectural Sheet Metal Manual" and as follows:

Insert terne-coated stainless steel or lead-coated copper if required.

          - Stainless Steel: ASTM A240/A240M or ASTM A666, [Type 304] [Type 316], 0.016 inch (0.40 mm) thick.

          - Copper: [ASTM B370, Temper H00, cold-rolled copper sheet, 16 oz./sq. ft. (4.9 kg/sq. m) weight or 0.0216 inch (0.55 mm) thick] [or] [ASTM B370, Temper H01, high-yield copper sheet, 12 oz./sq. ft. (3.7 kg/sq. m) weight or 0.0162 inch (0.41 mm) thick].

          - Fabricate continuous flashings in sections 96 inches (2438 mm) long minimum, but not exceeding 12 ft. (3.7 m). Provide splice plates at joints of formed, smooth metal flashing.

Delete first subparagraph below if plain (flat) sheet metal flashing is acceptable.

          - Fabricate through-wall metal flashing embedded in masonry from [stainless steel] [copper], with ribs at 3-inch (76-mm) intervals along length of flashing to provide an integral mortar bond.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Delete first subparagraph below if not required.

          - Fabricate through-wall flashing with snaplock receiver on exterior face where indicated to receive counterflashing.

Usually retain one or both of first two subparagraphs below if metal through-wall flashing is used. See the Evaluations.

          - Fabricate through-wall flashing with drip edge [where] [unless otherwise] indicated. Fabricate by extending flashing 1/2 inch (13 mm) out from wall, with outer edge bent down 30 degrees[ and hemmed].

          - Fabricate through-wall flashing with sealant stop [where] [unless otherwise] indicated. Fabricate by bending metal back on itself 3/4 inch (19 mm) at exterior face of wall and down into joint 1/4 inch (6.4 mm) to form a stop for retaining sealant backer rod.

Retain first subparagraph below if either of last two subparagraphs above is used with sawtooth metal flashing.

          - Fabricate metal [drip edges] [and] [sealant stops] for sawtooth metal flashing from plain metal flashing of same metal as sawtooth flashing and extending at least 3 inches (76 mm) into wall with hemmed inner edge to receive sawtooth flashing and form a hooked seam. Form hem on upper surface of metal so that completed seam sheds water.

Retain one or both of first two subparagraphs below for use with flexible flashing if required. See the Evaluations.

          - Fabricate metal drip edges from stainless steel. Extend at least 3 inches (76 mm) into wall and 1/2 inch (13 mm) out from wall, with outer edge bent down 30 degrees[ and hemmed].

          - Fabricate metal sealant stops from stainless steel. Extend at least 3 inches (76 mm) into wall and out to exterior face of wall. At exterior face of wall, bend metal back on itself for 3/4 inch (19 mm) and down into joint 1/4 inch (6.4 mm) to form a stop for retaining sealant backer rod.

          - Fabricate metal expansion-joint strips from [stainless steel] [copper] to shapes indicated.

          - Solder metal items at corners.

Delete "Flexible Flashing" Paragraph below if only metal flashing is allowed. Flexible flashing is fully concealed. If concealed metal flashing is required at certain locations, indicate those locations on Drawings or revise paragraph.

        - Flexible Flashing: Use[ one of] the following unless otherwise indicated:

          - Copper Fabric Flashing: [3- oz./sq. ft. (0.9 kg/sq. m)] [5 oz./sq. ft. (1.5 kg/sq. m)] [7 oz./sq. ft. (2 kg/sq. m)] [self-adhesive] copper sheet bonded between two layers of glass-fiber cloth. Use only where flashing is fully concealed in masonry.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Type 316 stainless steel is available from some manufacturers for use in high-corrosion areas.

          - Stainless Steel Fabric Flashing: Composite, flashing product consisting of 2 mil (0.05 mm) of [Type 304] [Type 316] stainless steel sheet, bonded to a layer of polymeric fabric, to produce an overall thickness of 40 mil (1.0 mm).

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

The 10-mil (0.25-mm) products are typically used at door and window flashing locations and are available in smaller widths, only a few manufactures make the 40-mil (1.0-mm) product.

          - Self-Adhering, Stainless Steel Fabric Flashing: Composite, flashing product consisting of 2 mil (0.05 mm) of [Type 304] [Type 316] stainless steel sheet, bonded to a layer of polymeric fabric with a [butyl adhesive] [permanent, clear adhesive], to produce an overall thickness of [10 mil (0.25 mm)] [40 mil (1.0 mm)].

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Applications: Use 10-mil- (0.25-mm-) thick flashing at windows, doors, and small wall penetrations; not at base of walls.[ Use 40-mil- (1.0-mm-) thick flashing at base of walls.]

BIA recommends 30 mil (0.76 mm) as a minimum thickness for rubberized asphalt flashing. The most common thickness available is 40 mil (1.0 mm); 60 mil (1.5 mm) is used for heavy-duty applications. Rubberized asphalt is incompatible with most weather barriers and sealants.

          - Rubberized-Asphalt Flashing: Composite flashing product consisting of a pliable, adhesive rubberized-asphalt compound, bonded to a high-density, cross-laminated polyethylene film to produce an overall thickness of not less than [30 mil (0.76 mm)] [40 mil (1.0 mm)] [60 mil (1.5 mm)].

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Accessories: Provide preformed corners, end dams, other special shapes, and seaming materials produced by flashing manufacturer.

Self-adhesive flashing using butyl rubber is more expensive than rubberized asphalt and must not be used in contact with asphalt.

          - Butyl Rubber Flashing: Composite, self-adhesive, flashing product consisting of a pliable, butyl rubber compound, bonded to a high-density polyethylene film, aluminum foil, or spunbonded polyolefin to produce an overall thickness of not less than [35 mil (0.89 mm)] [40 mil (1.0 mm)].

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Accessories: Provide preformed corners, end dams, other special shapes, and seaming materials produced by flashing manufacturer.

          - Elastomeric Thermoplastic Flashing: Composite flashing product consisting of a polyester-reinforced ethylene interpolymer alloy.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Monolithic Sheet" or "Self-Adhesive Sheet" Subparagraph below, or indicate on Drawings where each is required.

            - Monolithic Sheet: Elastomeric thermoplastic flashing, 40 mil (1.0 mm) thick.

            - Self-Adhesive Sheet: Elastomeric thermoplastic flashing, 25 mil (0.64 mm) thick, with a 15-mil- (0.38-mm-) thick coating of adhesive.

              - Color: [Gray] [White] [Tan/buff] [Black].

            - Accessories: Provide preformed corners, end dams, other special shapes, and seaming materials produced by flashing manufacturer.

          - EPDM Flashing: Sheet flashing product made from ethylene-propylene-diene terpolymer, complying with ASTM D4637/D4637M, 40 mil (1.0 mm) thick.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Drainage plane flashing combines flexible flashing membranes with drainage material in one unit and may also include other accessory items.

        - Drainage Plane Flashing: Fabricate from [stainless steel] [copper] [rubberized asphalt] [elastomeric membrane] and drainage membrane to shapes indicated[, including weep tabs, termination bar and drip edge]. Provide flashing materials as follows:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Stainless Steel: ASTM A240/A240M or ASTM A666, [Type 304] [Type 316], 0.016 inch (0.40 mm) thick.

          - Copper: [3 oz./sq. ft. (0.9 kg/sq. m)] [5 oz./sq. ft. (1.5 kg/sq. m)] thick.

          - Rubberized Asphalt: [40 mil (1.0 mm)] [60 mils (1.5 mm)] thick.

          - Elastomeric Membrane: [EPDM complying with ASTM D4637/D4637M] [PVC] [PVC with Elvaloy Kee] [TPO], [40 mil (1.0 mm)] [60 mils (1.5 mm)].

          - Fabricate continuous flashings in sections 60 inches (1524 mm) long, minimum.

          - Accessories: Provide preformed corners, end dams, other special shapes, and seaming materials produced by flashing manufacturer.

        - Solder and Sealants for Sheet Metal Flashings:[ As specified in Section 076200 "Sheet Metal Flashing and Trim."]

Retain option in "Solder and Sealants for Sheet Metal Flashing" Paragraph above or one or more of "Solder for Stainless Steel," "Solder for Copper," and "Elastomeric Sealant" subparagraphs below. Grade Sn60 solder is 40 percent lead; Grade Sn96 is 0.10 percent lead; and Grade Sn50 is 50 percent lead.

          - Solder for Stainless Steel: ASTM B32, [Grade Sn60] [Grade Sn96], with acid flux of type recommended by stainless steel sheet manufacturer.

          - Solder for Copper: ASTM B32, [Grade Sn50] [with maximum lead content of 0.2 percent].

Revise "Elastomeric Sealant" Subparagraph below if sealant of specific type, grade, class, and use is required.

          - Elastomeric Sealant: ASTM C920, chemically curing [urethane] [polysulfide] [silicone] sealant; of type, grade, class, and use classifications required to seal joints in sheet metal flashing and remain watertight.

        - Adhesives, Primers, and Seam Tapes for Flashings: Flashing manufacturer's standard products or products recommended by flashing manufacturer for bonding flashing sheets to each other and to substrates.

Mortar will corrode aluminum if not protected by paint.

        - Termination Bars for Flexible Flashing: [Aluminum] [Stainless steel] [Rigid PVC] steel bars [0.075 inch by 1 inch (1.9 mm by 25 mm)] [1/8 inch by 1 inch (3.2 mm by 25 mm)] [1/8 inch by 1-1/8 inch (3.2 mm by 29 mm)].

        - Termination Bars for Flexible Flashing, Flanged: [Stainless steel sheet 0.019 inch by 1-1/2 inches (0.48 mm by 38 mm)] [Aluminum sheet 0.064 inch by 1-1/2 inches (1.63 mm by 38 mm)] with a 3/8-inch (10-mm) flange at top [and bottom].

      - ACCESSORIES

        - Compressible Filler: Premolded filler strips complying with ASTM D1056, Grade 2A1; compressible up to 35 percent; of width and thickness indicated; formulated from [neoprene] [urethane] [or] [PVC].

        - Weep/Vent Products: Use[ one of] the following unless otherwise indicated:

Retain one or more of "Wicking Material," "Round Plastic Weep/Vent Tubing," "Rectangular Plastic Weep/Vent Tubing," "Cellular Plastic Weep/Vent," "Mesh Weep/Vent," and "Vinyl Weep Hole/Vent" subparagraphs below; delete all if open-head joints are used.

          - Wicking Material: Absorbent rope, made from cotton, 1/4 to 3/8 inch (6.4 to 10 mm) in diameter, in length required to produce 2-inch (51-mm) exposure on exterior and 18 inches (457 mm) in cavity. Use only for weeps.

          - Round Plastic Weep/Vent Tubing: Medium-density polyethylene, 3/8-inch (10-mm) OD by 4 inches (102 mm) long.

          - Rectangular Plastic Weep/Vent Tubing: Clear butyrate, 3/8 by 1-1/2 by 3-1/2 inches (10 by 38 by 89 mm) long.

          - Cellular Plastic Weep/Vent: One-piece, flexible extrusion made from UV-resistant polypropylene copolymer, full height and width of head joint and depth 1/8 inch (3.2 mm) less than depth of outer wythe, in color selected from manufacturer's standard.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Mesh Weep/Vent: Free-draining mesh; made from polyethylene strands, full height and width of head joint and depth 1/8 inch (3.2 mm) less than depth of outer wythe; in color selected from manufacturer's standard.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Vinyl Weep Hole/Vent: Units made from flexible PVC, designed to fit into a head joint and consisting of a louvered vertical leg, flexible wings to seal against ends of masonry units, and a top flap to keep mortar out of the head joint; in color selected by Architect.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Products described in "Cavity Drainage Material" Paragraph below can be used to keep weep holes clear. See the Evaluations.

        - Cavity Drainage Material: Free-draining mesh, made from polymer strands that will not degrade within the wall cavity.

          - Mortar Deflector: Strips, [full depth of cavity] [3/4 inch (19 mm) thick] [1 inch (25 mm)] [1-1/2 inches (38 mm) thick] [2 inches (51 mm)] <Insert thickness> and [10 inches (254 mm)] [16 inches (406 mm)] <Insert thickness> high, with [dovetail-shaped notches] [dimpled surface] that prevent clogging with mortar droppings.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Rainscreen Drainage Mat: Sheets or strips not less than [full depth of cavity] [3/4 inch (19 mm)] [1 inch (25 mm)] [1-1/2 inches (38 mm) thick] [2 inches (51 mm)] <Insert thickness> thick and installed to full height of cavity, [with additional strips 4 inches (102 mm) high at weep holes and thick enough to fill entire depth of cavity] to prevent weep holes from clogging with mortar.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Offset Angle Supports: Steel plate brackets anchored to structure, allowing continuous insulation behind shelf angle supporting veneer. Component and anchor size and spacing engineered by manufacturer.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Verify acceptability of cleaner for cleaning masonry with pigmented mortar joints and for types of masonry units specified.

        - Proprietary Acidic Masonry Cleaner: Manufacturer's standard-strength cleaner designed for removing mortar/grout stains, efflorescence, and other new construction stains from new masonry without discoloring or damaging masonry surfaces. Use product expressly approved for intended use by cleaner manufacturer and manufacturer of masonry units being cleaned.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

      - MORTAR MIXES

        - General: Do not use admixtures, including pigments, air-entraining agents, accelerators, retarders, water-repellent agents, antifreeze compounds, or other admixtures unless otherwise indicated.

          - Do not use calcium chloride in mortar or grout.

Retain one or more of first three subparagraphs below to indicate acceptable mortar types.

          - Use [portland cement-lime] [masonry cement] [or] [mortar cement] mortar unless otherwise indicated.

          - For exterior masonry, use [portland cement-lime] [masonry cement] [or] [mortar cement] mortar.

          - For reinforced masonry, use [portland cement-lime] [masonry cement] [or] [mortar cement] mortar.

          - Add cold-weather admixture (if used) at same rate for all mortar that will be exposed to view, regardless of weather conditions, to ensure that mortar color is consistent.

Preblended, dry mortar mix can help ensure uniformity.

        - Preblended, Dry Mortar Mix: Furnish dry mortar ingredients in form of a preblended mix. Measure quantities by weight to ensure accurate proportions, and thoroughly blend ingredients before delivering to Project site.

        - Mortar for Unit Masonry: Comply with ASTM C270, [Proportion] [Property] Specification. Use Type N unless another type is indicated.

Before retaining mortar types in subparagraph below, see Appendix X1 in ASTM C270 and BIA Technical Notes 8 and 8B for recommendations; coordinate with requirements for masonry compressive strengths.

          - For masonry below grade or in contact with earth, use [Type M] [Type S].

        - Pigmented Mortar: Use colored cement product[ or select and proportion pigments with other ingredients to produce color required. Do not add pigments to colored cement products].

Retain first three subparagraphs below if retaining option in "Pigmented Mortar" Paragraph above. Percentages in first two subparagraphs below are for pigments containing only metallic oxides. If pigments containing carbon black are used, carbon black must be limited to 2 percent of portland cement by weight or 1 percent of masonry cement or mortar cement.

          - Pigments do not exceed 10 percent of portland cement by weight.

          - Pigments do not exceed 5 percent of [masonry cement] [or] [mortar cement] by weight.

          - Mix to match Architect's sample.

          - Application: Use pigmented mortar for exposed mortar joints.

        - Colored-Aggregate Mortar: Produce required mortar color by using colored aggregates and natural color or white cement as necessary to produce required mortar color.

Insert materials and proportions used for sample in first subparagraph below if known.

          - Mix to match Architect's sample.

          - Application: Use colored-aggregate mortar for exposed mortar joints.

- EXECUTION

      - EXAMINATION

        - Examine conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

          - For the record, prepare written report, endorsed by Installer, listing conditions detrimental to performance of the Work.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION, GENERAL

        - Leave openings for equipment to be installed before completing masonry. After installing equipment, complete masonry to match the construction immediately adjacent to opening.

        - Use full-size units without cutting if possible. If cutting is required to provide a continuous pattern or to fit adjoining construction, cut units with motor-driven saws; provide clean, sharp, unchipped edges. Allow units to dry before laying unless wetting of units is specified. Install cut units with cut surfaces and, where possible, cut edges concealed.

        - Select and arrange units for exposed unit masonry to produce a uniform blend of colors and textures. Mix units from several pallets or cubes as they are placed.

        - Matching Existing Masonry: Match coursing, bonding, color, and texture of existing masonry.

Retain "Wetting of Brick" Paragraph below for high-suction brick. A simple test to determine if wetting is required consists of drawing a circle the size of a quarter on a brick and placing 20 drops of water in the circle; if water is absorbed within 1-1/2 minutes, the brick requires wetting.

        - Wetting of Brick: Wet brick before laying if initial rate of absorption exceeds 30 g/30 sq. in. (30 g/194 sq. cm) per minute when tested in accordance with ASTM C67/C67M. Allow units to absorb water so they are damp but not wet at time of laying.

      - TOLERANCES

        - Dimensions and Locations of Elements:

          - For dimensions in cross section or elevation, do not vary by more than plus 1/2 inch (13 mm) or minus 1/4 inch (6.4 mm).

          - For location of elements in plan, do not vary from that indicated by more than plus or minus 1/2 inch (13 mm).

          - For location of elements in elevation, do not vary from that indicated by more than plus or minus 1/4 inch (6.4 mm) in a story height or 1/2 inch (13 mm) total.

        - Lines and Levels:

          - For bed joints and top surfaces of bearing walls, do not vary from level by more than 1/4 inch in 10 ft. (6.4 mm in 3 m), or 1/2-inch (13-mm) maximum.

          - For conspicuous horizontal lines, such as lintels, sills, parapets, and reveals, do not vary from level by more than 1/8 inch in 10 ft. (3.2 mm in 3 m), 1/4 inch in 20 ft. (6.4 mm in 6 m), or 1/2-inch (13-mm) maximum.

          - For vertical lines and surfaces, do not vary from plumb by more than 1/4 inch in 10 ft. (6.4 mm in 3 m), 3/8 inch in 20 ft. (10 mm in 6 m), or 1/2-inch (13-mm) maximum.

          - For conspicuous vertical lines, such as external corners, door jambs, reveals, and expansion and control joints, do not vary from plumb by more than 1/8 inch in 10 ft. (3.2 mm in 3 m), 1/4 inch in 20 ft. (6.4 mm in 6 m), or 1/2-inch (13-mm) maximum.

          - For lines and surfaces, do not vary from straight by more than 1/4 inch in 10 ft. (6.4 mm in 3 m), 3/8 inch in 20 ft. (10 mm in 6 m), or 1/2-inch (13-mm) maximum.

          - For vertical alignment of exposed head joints, do not vary from plumb by more than 1/4 inch in 10 ft. (6.4 mm in 3 m), or 1/2-inch (13-mm) maximum.

If using Type FBS Rough brick or Type FBA brick, revise tolerance in subparagraph below to allow for variation in brick size.

          - For faces of adjacent exposed masonry units, do not vary from flush alignment by more than 1/16 inch (1.6 mm) except due to warpage of masonry units within tolerances specified for warpage of units.

        - Joints:

If using Type FBS Rough brick or Type FBA brick, revise tolerances in five subparagraphs below to allow for variation in brick size. Consider restricting tolerances if Type FBX brick is used.

          - For bed joints, do not vary from thickness indicated by more than plus or minus 1/8 inch (3.2 mm), with a maximum thickness limited to 1/2 inch (13 mm).

          - For exposed bed joints, do not vary from bed-joint thickness of adjacent courses by more than 1/8 inch (3.2 mm).

          - For head and collar joints, do not vary from thickness indicated by more than plus 3/8 inch (10 mm) or minus 1/4 inch (6.4 mm).

          - For exposed head joints, do not vary from thickness indicated by more than plus or minus 1/8 inch (3.2 mm).[ Do not vary from adjacent bed-joint and head-joint thicknesses by more than 1/8 inch (3.2 mm).]

          - For exposed bed joints and head joints of stacked bond, do not vary from a straight line by more than 1/16 inch (1.6 mm) from one masonry unit to the next.

      - LAYING MASONRY WALLS

        - Lay out walls in advance for accurate spacing of surface bond patterns with uniform joint thicknesses and for accurate location of openings, movement-type joints, returns, and offsets. Avoid using less-than-half-size units, particularly at corners, jambs, and, where possible, at other locations.

Pattern is usually running bond. If other bond patterns are required, specify in "Bond Pattern for Exposed Masonry" Paragraph below or indicate on Drawings.

        - Bond Pattern for Exposed Masonry: Unless otherwise indicated, lay exposed masonry in [running bond] [stack bond] [one-third running bond] [Flemish bond] [English bond] [bond pattern indicated on Drawings]; do not use units with less-than-nominal 4-inch (102-mm) horizontal face dimensions at corners or jambs.

        - Stopping and Resuming Work: Stop work by stepping back units in each course from those in course below; do not tooth. When resuming work, clean masonry surfaces that are to receive mortar, remove loose masonry units and mortar, and wet brick if required before laying fresh masonry.

        - Built-in Work: As construction progresses, build in items specified in this and other Sections. Fill in solidly with masonry around built-in items.

Revise paragraph below if flexible perimeter joint or thermal break is required.

        - Fill space between steel frames and masonry solidly with mortar unless otherwise indicated.

      - MORTAR BEDDING AND JOINTING

        - Lay[ solid] masonry units with completely filled bed and head joints; butter ends with sufficient mortar to fill head joints and shove into place. Do not deeply furrow bed joints or slush head joints.

        - Lay [hollow brick] [and] [CMUs] with face shells fully bedded in mortar and with head joints of depth equal to bed joints. At starting course, fully bed entire units, including area under cells.

          - At anchors and ties, fully bed units and fill cells with mortar as needed to fully embed anchors and ties in mortar.

        - Set [stone] [cast-stone] trim units in full bed of mortar with full vertical joints.

          - Clean soiled surfaces with fiber brush and soap powder and rinse thoroughly with clear water.

          - Allow cleaned surfaces to dry before setting.

Retain last subparagraph above for relatively impervious stones, such as granite; retain first subparagraph below for absorptive stones, such as limestone, sandstone, and cast stone.

          - Wet joint surfaces thoroughly before applying mortar.

          - Rake out mortar joints for pointing with sealant.

If another joint profile is used, revise paragraph below or indicate on Drawings.

        - Tool exposed joints slightly concave when thumbprint hard, using a jointer larger than joint thickness unless otherwise indicated.

          - For glazed masonry units, use a nonmetallic jointer 3/4 inch (19 mm) or more in width.

      - ANCHORED MASONRY VENEERS

        - Anchor masonry veneers to [wall framing] [and] [concrete and masonry backup] with[ seismic] masonry-veneer anchors to comply with the following requirements:

          - Fasten [screw-attached] [and] [seismic] anchors [through sheathing to wall framing] [and] [to concrete and masonry backup] with metal fasteners of type indicated. Use two fasteners unless anchor design only uses one fastener.

          - Embed [tie sections] [connector sections and continuous wire] in masonry joints.

          - Locate anchor sections to allow maximum vertical differential movement of ties up and down.

Retain one of three subparagraphs below to suit Project. First subparagraph below is BIA recommendation for metal-stud construction. Second subparagraph below is based on TMS 402 requirement for less than 40 psf (1.92 kPa) wind load. First option is for adjustable two-piece anchors, wire anchors 0.148 inch (3.8 mm) in diameter, and corrugated sheet metal anchors; second is for all other anchors. Third subparagraph below is based on TMS 402 requirement for 40 to 55 psf (1.92 to 2.63 kPa) wind load for adjustable two-piece anchors, wire anchors 0.148 inch (3.8 mm) in diameter, and corrugated sheet metal anchors. Revise spacing to suit coursing, comply with requirements of authorities having jurisdiction, or comply with structural requirements imposed by wind or seismic forces.

          - Space anchors as indicated, but not more than 18 inches (457 mm) o.c. vertically and 24 inches (610 mm) o.c. horizontally, with not less than one anchor for each 2 sq. ft. (0.2 sq. m) of wall area. Install additional anchors within 12 inches (305 mm) of openings and at intervals, not exceeding 8 inches (203 mm), around perimeter.

          - Space anchors as indicated, but not more than 16 inches (406 mm) o.c. vertically and 25 inches (635 mm) o.c. horizontally, with not less than one anchor for each [2.67 sq. ft. (0.25 sq. m)] [3.5 sq. ft. (0.33 sq. m)] of wall area. Install additional anchors within 12 inches (305 mm) of openings and at intervals, not exceeding 36 inches (914 mm), around perimeter.

          - Space anchors as indicated, but not more than 18 inches (457 mm) o.c. vertically and horizontally. Install additional anchors within 12 inches (305 mm) of openings and at intervals, not exceeding 24 inches (610 mm), around perimeter.

BIA Technical Notes 28B recommends 2 inches (51 mm) of airspace. Wider airspaces require closer tie spacing.

        - Provide not less than [2 inches (51 mm)] [1 inch (25 mm)] <Insert distance> of airspace between back of masonry veneer and face of [sheathing] [insulation].

          - Keep airspace clean of mortar droppings and other materials during construction. Bevel beds away from airspace, to minimize mortar protrusions into airspace. Do not attempt to trowel or remove mortar fins protruding into airspace.

      - ANCHORING MASONRY TO STRUCTURAL STEEL AND CONCRETE

        - Anchor masonry to structural steel and concrete, where masonry abuts or faces structural steel or concrete to comply with the following:

          - Provide an open space not less than [1/2 inch (13 mm)] [1 inch (25 mm)] [2 inches (51 mm)] wide between masonry and structural steel or concrete unless otherwise indicated. Keep open space free of mortar and other rigid materials.

          - Anchor masonry with anchors embedded in masonry joints and attached to structure.

          - Space anchors as indicated, but not more than 24 inches (610 mm) o.c. vertically and 36 inches (914 mm) o.c. horizontally.

      - EXPANSION JOINTS

        - General: Install expansion-joint materials in unit masonry as masonry progresses. Do not allow materials to span expansion joints without provision to allow for in-plane wall or partition movement.

Indicate locations of joints on Drawings.

        - Form expansion joints as follows:

Retain one or more of first three subparagraphs below.

          - Build flanges of metal expansion strips into masonry. Lap each joint 4 inches (102 mm) in direction of water flow. Seal joints below grade and at junctures with horizontal expansion joints if any.

          - Build flanges of factory-fabricated, expansion-joint units into masonry.

          - Build in compressible joint fillers where indicated.

          - Form open joint full depth of brick wythe and of width indicated, but not less than [3/8 inch (10 mm)] [1/2 inch (13 mm)] <Insert minimum width> for installation of sealant and backer rod specified in Section 079200 "Joint Sealants."

        - Provide horizontal, pressure-relieving joints by either leaving an airspace or inserting a compressible filler of width required for installing sealant and backer rod specified in Section 079200 "Joint Sealants," but not less than [3/8 inch (10 mm)] <Insert minimum width>.

Revise subparagraph below to suit Project. Indicate locations of joints on Drawings.

          - Locate horizontal, pressure-relieving joints beneath shelf angles supporting masonry.

      - LINTELS

        - Install steel lintels where indicated.

        - Provide offset angle supports where indicate and where openings of more than 12 inches (305 mm) for brick-size units and 24 inches (610 mm) for block-size units are indicated without structural steel or other supporting lintels.

Delete paragraph below if bearing is shown on Drawings.

        - Provide minimum bearing of 8 inches (203 mm) at each jamb unless otherwise indicated.

      - FLASHING, WEEP HOLES, AND VENTS

Retain option in "General" Paragraph below if wall is designed on rain-screen principle with vents acting to equalize air-pressure differential between cavity and exterior. Indicate spacing of vents and blocking on Drawings. See the Evaluations.

        - General: Install embedded flashing and weep holes in masonry at shelf angles, lintels, ledges, other obstructions to downward flow of water in wall, and where indicated.[ Install vents at shelf angles, ledges, and other obstructions to upward flow of air in cavities, and where indicated.]

        - Install flashing as follows unless otherwise indicated:

Retain option in first subparagraph below for manufactured flashing; delete if only metal flashing is used.

          - Prepare masonry surfaces so they are smooth and free from projections that could puncture flashing. Where flashing is within mortar joint, place through-wall flashing on sloping bed of mortar and cover with mortar. Before covering with mortar, seal penetrations in flashing with adhesive, sealant, or tape[ as recommended by flashing manufacturer].

          - Extend flashing through veneer, across airspace behind veneer, and up face of sheathing at least 8 inches (203 mm); with upper edge tucked under [water-resistive barrier] [air barrier], lapping at least 4 inches (102 mm).[ Fasten upper edge of flexible flashing to sheathing through termination bar.]

          - At lintels and shelf angles, extend flashing 6 inches (152 mm) minimum[, to edge of next full unit] at each end. At heads and sills, extend flashing 6 inches (152 mm) minimum[, to edge of next full unit] and turn ends up not less than 2 inches (51 mm) to form end dams.

          - Interlock end joints of sawtooth sheet metal flashing by overlapping ribs not less than 1-1/2 inches (38 mm) or as recommended by flashing manufacturer, and seal lap with elastomeric sealant complying with requirements in Section 079200 "Joint Sealants" for application indicated.

          - Install metal [drip edges] [and] [sealant stops] with sawtooth sheet metal flashing by interlocking hemmed edges to form hooked seam. Seal seam with elastomeric sealant complying with requirements in Section 079200 "Joint Sealants" for application indicated.

Retain one of three subparagraphs below if flexible flashing materials are used. See the Evaluations.

          - Install metal drip edges beneath flexible flashing at exterior face of wall. Stop flexible flashing 1/2 inch (13 mm) back from outside face of wall, and adhere flexible flashing to top of metal drip edge.

          - Install metal flashing termination beneath flexible flashing at exterior face of wall. Stop flexible flashing 1/2 inch (13 mm) back from outside face of wall, and adhere flexible flashing to top of metal flashing termination.

          - Cut flexible flashing off flush with face of wall after masonry wall construction is completed.

        - Install reglets and nailers for flashing and other related construction where they are indicated to be built into masonry.

        - Install weep holes in veneers in head joints of first course of masonry immediately above embedded flashing.

          - Use [specified weep/cavity vent products] [or] [open-head joints] to form weep holes.

          - Use wicking material to form weep holes above flashing under brick sills. Turn wicking down at lip of sill to be as inconspicuous as possible.

          - Space weep holes 24 inches (610 mm) o.c. unless otherwise indicated.

Retain last subparagraph above if weep holes other than plastic tubing or wicking are used. Retain first subparagraph below if plastic tubing or wicking is used.

          - Space weep holes formed from [plastic tubing] [or] [wicking material] 16 inches (406 mm) o.c.

          - Cover cavity side of weep holes with plastic insect screening at cavities insulated with loose-fill insulation.

          - Trim wicking material flush with outside face of wall after mortar has set.

        - Place cavity drainage material in airspace behind veneers to comply with configuration requirements for cavity drainage material in "Accessories" Article.

Retain paragraph below if wall is designed with vents acting to equalize air-pressure differential between cavity and exterior. Indicate spacing of vents and blocking on Drawings. See the Evaluations.

        - Install vents in head joints in exterior wythes at spacing indicated. Use [specified weep/cavity vent products] [or] [open-head joints] to form vents.

          - Close cavities off vertically and horizontally with blocking in manner indicated. Install through-wall flashing and weep holes above horizontal blocking.

      - FIELD QUALITY CONTROL

Retain first option in "Testing Agency" Paragraph below if Owner hires an independent testing agency.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections. Allow inspectors access to scaffolding and work areas as needed to perform tests and inspections. Retesting of materials that fail to comply with specified requirements will be at Contractor's expense.

Level 2 special inspections are required for masonry veneer in essential facilities.

        - Inspections: Special inspections in accordance with Level 2 in TMS 402.

Revise subparagraph below to suit level of inspection required, based on occupancy category and design method.

          - Begin masonry construction only after inspectors have verified proportions of site-prepared mortar.

Retain "Testing Prior to Construction" Paragraph below for masonry veneer in essential facilities.

        - Testing Prior to Construction: One set of tests.

Retain "Clay Masonry Unit Test" and "Concrete Masonry Unit Test" paragraphs below, as applicable.

        - Clay Masonry Unit Test: For each type of unit provided, in accordance with ASTM C67/C67M for compressive strength.

        - Concrete Masonry Unit Test: For each type of unit provided, in accordance with ASTM C140/C140M for compressive strength.

TMS 402 requires verification of compliance of proportions for site-prepared mortar. Mortar aggregate ratio test in "Mortar Aggregate Ratio Test (Proportion Specification)" Paragraph below verifies ratio of aggregate to cementitious materials but does not indicate what cementitious materials are used. Observation of actual mortar mixing procedures as part of inspection program would provide better quality control.

        - Mortar Aggregate Ratio Test (Proportion Specification): For each mix provided, in accordance with ASTM C780.

"Mortar Test (Property Specification)" Paragraph below may be deleted if mortar is specified to comply with proportion specification. Testing for compressive strength is required if the property specification for mortar is used. Note that ASTM C780 states, "Strength values for mortars obtained through these testing procedures are not required, nor expected, to meet strength requirements of laboratory Specification C 270 mortars."

        - Mortar Test (Property Specification): For each mix provided, in accordance with ASTM C780. Test mortar for [mortar air content] [and] [compressive strength].

      - REPAIRING, POINTING, AND CLEANING

        - Remove and replace masonry units that are loose, chipped, broken, stained, or otherwise damaged or that do not match adjoining units. Install new units to match adjoining units; install in fresh mortar, pointed to eliminate evidence of replacement.

        - Pointing: During the tooling of joints, enlarge voids and holes, except weep holes, and completely fill with mortar. Point up joints, including corners, openings, and adjacent construction, to provide a neat, uniform appearance. Prepare joints for sealant application, where indicated.

        - In-Progress Cleaning: Clean unit masonry as work progresses by dry brushing to remove mortar fins and smears before tooling joints.

        - Final Cleaning: After mortar is thoroughly set and cured, clean exposed masonry as follows:

          - Remove large mortar particles by hand with wooden paddles and nonmetallic scrape hoes or chisels.

          - Test cleaning methods on sample wall panel; leave one-half of panel uncleaned for comparison purposes. Obtain Architect's approval of sample cleaning before proceeding with cleaning of masonry.

Delete first two subparagraphs below if cleaners are not specified in Part 2 or if cleaners are not allowed.

          - Protect adjacent stone and nonmasonry surfaces from contact with cleaner by covering them with liquid strippable masking agent or polyethylene film and waterproof masking tape.

          - Wet wall surfaces with water before applying cleaners; remove cleaners promptly by rinsing surfaces thoroughly with clear water.

          - Clean brick by bucket-and-brush hand-cleaning method described in BIA Technical Notes 20.

Retain last subparagraph above or subparagraph below. Coordinate with products retained in Part 2. If high-pressure water cleaning or other methods are acceptable, delete or revise subparagraph below and insert applicable requirements.

          - Clean masonry with a proprietary acidic cleaner applied according to manufacturer's written instructions.

      - MASONRY WASTE DISPOSAL

        - Salvageable Materials: Unless otherwise indicated, excess masonry materials are Contractor's property. At completion of unit masonry work, remove from Project site.

Retain "Waste Disposal as Fill Material" Paragraph below if clean masonry waste can be used as fill in footing trenches, etc. This diverts some material from waste stream, conserving landfill space and energy required to haul waste away.

        - Waste Disposal as Fill Material: Dispose of clean masonry waste, including excess or soil-contaminated sand, waste mortar, and broken masonry units, by crushing and mixing with fill material as fill is placed.

          - Crush masonry waste to less than 4 inches (102 mm) in each dimension.

          - Mix masonry waste with at least two parts of specified fill material for each part of masonry waste. Fill material is specified in Section 312000 "Earth Moving."

Generally, retain subparagraph below. If required, increase limit if acid-soil plants are used for foundation plantings.

          - Do not dispose of masonry waste as fill within 18 inches (457 mm) of finished grade.

        - Excess Masonry Waste: Remove excess clean masonry waste that cannot be used as fill, as described above or recycled, and other masonry waste, and legally dispose of off Owner's property.

END OF SECTION 042613