Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 071413 - HOT FLUID-APPLIED RUBBERIZED ASPHALT WATERPROOFING

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED 2009, LEED v4, LEED v4.1, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using the hypertext links.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Hot fluid-applied, rubberized-asphalt waterproofing membrane.

          - Molded-sheet drainage panels.

          - Insulation.

          - Plaza-deck pavers.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 075556 "Fluid-Applied Protected Membrane Roofing" for hot fluid-applied, rubberized-asphalt roofing.

          - Section 079100 "Preformed Joint Seals" for foundation-wall expansion joints that interface with waterproofing.

          - Section 079200 "Joint Sealants" for joint sealants, joint fillers, and joint preparation.

          - Section 079513.19 "Parking Deck Expansion Joint Cover Assemblies" for plaza expansion-joint assemblies that interface with waterproofing.

          - Section 321400 "Unit Paving" for plaza-deck pavers set on setting beds.

      - PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a conference.

        - Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

Retain subparagraph below if additional requirements are necessary; include information about conference.

          - Review waterproofing requirements, including surface preparation, substrate condition and pretreatment, minimum curing period, forecasted weather conditions, special details and sheet flashings, installation procedures, testing and inspection procedures, and protection and repairs.

If needed, insert list of conference participants not mentioned in Section 013100 "Project Management and Coordination."

      - ACTION SUBMITTALS

        - Product Data: For each type of product. Include manufacturer's written instructions for evaluating, preparing, and treating substrate, technical data, and tested physical and performance properties of waterproofing.

        - Shop Drawings: Show locations and extent of waterproofing. Include details for substrate joints and cracks, sheet flashings, penetrations, inside and outside corners, tie-ins to adjoining waterproofing, and other termination conditions.

Retain subparagraph below if using pedestal-supported concrete pavers on plaza decks over waterproofing.

          - Include setting drawings showing layout, sizes, sections, profiles, and joint details of pedestal-supported concrete pavers.

        - Sustainable Design Submittals:

          - <Double click to insert sustainable design text for moisture control>

        - Samples: For plaza-deck pavers[, full sized] in each color and texture required.

      - INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Data: For [Installer] [and] [testing agency].

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

        - Sample Warranties: For special warranties.

      - QUALITY ASSURANCE

Retain "Installer Qualifications" Paragraph below if applicable. For warranty purposes, manufacturer may qualify an installer. Coordinate paragraph with qualifications manufacturer requires of Installer.

        - Installer Qualifications: An authorized representative who is trained and approved by manufacturer.

        - Mockups: Install waterproofing to [100 sq. ft. (9.3 sq. m)] <Insert value> of [deck] [wall] to demonstrate surface preparation, crack and joint treatment, corner treatment, thickness, texture, and execution quality.[ Install pavers and paver supports to demonstrate aesthetic effects, and set quality standards for materials and execution.]

Retain first subparagraph below if mockups are not only for establishing appearance factors.

          - Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing.

Retain subparagraph below if the intention is to make an exception to the default requirement in Section 014000 "Quality Requirements" for demolishing and removing mockups.

          - Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

      - DELIVERY, STORAGE, AND HANDLING

        - Store liquid materials in their original undamaged containers in a clean, dry, protected location and within the temperature range required by waterproofing manufacturer.

        - Remove and replace liquid materials that cannot be applied within their stated shelf life.

        - Protect stored materials from direct sunlight.

      - FIELD CONDITIONS

        - Weather Limitations: Apply waterproofing within the range of ambient and substrate temperatures recommended by waterproofing manufacturer. Do not apply waterproofing to a damp or wet substrate, or when temperature is below zero deg F (minus 18 deg C).

          - Do not apply waterproofing in snow, rain, fog, or mist.

        - Maintain adequate ventilation during application and curing of waterproofing materials.

      - WARRANTY

When warranties are required, verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws. Example in "Special Warranty" Paragraph below is a labor-and-material warranty. Verify coverage with manufacturers. Manufacturers' warranties customarily do not include costs of excavating and exposing the waterproofing membrane as well as backfilling and restoring affected construction in vertical applications.

        - Special Warranty: Manufacturer agrees to repair or replace waterproofing and sheet flashings that do not comply with requirements or that fail to remain watertight within specified warranty period.

In addition to special warranty covering waterproofing and sheet flashings above, some manufacturers offer total-system warranties for plaza decks that include insulation and pavers. These warranties may include the costs of removing and reinstalling readily removable construction overlaying waterproofing. Verify coverage with manufacturers.

          - Warranty includes removing and reinstalling protection board, drainage panels, insulation, pedestals, and pedestal-mounted pavers on plaza decks.

          - Warranty insulation retains 80 percent of original published thermal value.

          - Warranty pavers do not dish or warp and do not crack, split, or disintegrate in freeze-thaw conditions.

Verify available warranties and warranty periods. Fabric-reinforced, hot fluid-applied waterproofing may qualify for 10-year warranties from some manufacturers.

          - Warranty Period: [Five] [10] <Insert number> years from date of Substantial Completion.

Retain "Special Installer's Warranty" Paragraph below if a separate special installer's warranty is required and if it is an accepted practice locally. Usually retain "Special Warranty" Paragraph above with "Special Installer's Warranty" Paragraph. Coordinate requirements of both special warranties to clarify responsibilities. If a specific installer's warranty form is required, see low-slope roofing Sections for examples that can be revised for waterproofing.

        - Special Installer's Warranty: Specified form[, on warranty form at end of this Section,] signed by Installer, covering Work of this Section, for warranty period of [two] <Insert number> years.

Retain subparagraph below for plaza decks if applicable; revise if required.

          - Warranty includes removing and reinstalling protection board, drainage panels, insulation, pedestals, and pedestal-mounted pavers on plaza decks.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - SOURCE LIMITATIONS

Retain products from options in "Source Limitations" Paragraph below if a total-system warranty is required from single manufacturer.

        - Source Limitations: Obtain waterproofing materials [sheet flashings] [protection course] [molded-sheet drainage panels] [insulation] [pavers] [and] [pedestals] from single source from single manufacturer.

      - WATERPROOFING MEMBRANE

        - Hot Fluid-Applied, Rubberized-Asphalt Waterproofing Membrane: Single component; 100 percent solids; hot fluid-applied, rubberized asphalt.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Insert product physical and performance properties below if required. Manufacturers still report properties in accordance with withdrawn CAN/CGSB-37.50, "Hot Applied, Rubberized Asphalt for Roofing and Waterproofing." See Evaluations for discussion and a listing of these properties.

      - ACCESSORIES

        - General: Accessory materials recommended by waterproofing manufacturer for intended use and compatible with waterproofing.

Revise primer and adhesives in this article to manufacturer-approved, VOC-conforming products when VOC limits apply.

        - Primer: ASTM D41/D41M, asphaltic primer.

Retain "Elastomeric Sheet" Paragraph below if used to reinforce joints, cracks, and terminations or for flashings. Revise or insert proprietary materials, such as self-adhering, rubberized asphalt with fabric facer or modified bituminous sheet, if not subject to hydrostatic head or frequent immersion in water.

        - Elastomeric Sheet: 50-mil- (1.3-mm-) minimum, uncured sheet neoprene[ with manufacturer's recommended contact adhesives] as follows:

          - Tensile Strength: 1400 psi (9.6 MPa) minimum; ASTM D412, Die C.

          - Elongation: 300 percent minimum; ASTM D412.

          - Tear Resistance: 125 psi (860 kPa) minimum; ASTM D624, Die C.

          - Brittleness: Does not break at minus 30 deg F (minus 34 deg C); ASTM D2137.

Retain "Metal Termination Bars" Paragraph below if required by manufacturer to fasten top edge of elastomeric flashing sheet against wall at expansion or moving joints.

        - Metal Termination Bars: Manufacturer's standard, predrilled stainless steel or aluminum termination bars; approximately 1 by 1/8 inch (25 by 3 mm) thick; with stainless steel anchors.

        - Sealants and Accessories: Manufacturer's recommended sealants and accessories.

Retain "Reinforcing Fabric" Paragraph below for joint-reinforcing fabric strips and for reinforced waterproofing membrane.

        - Reinforcing Fabric: Manufacturer's recommended, spun-bonded polyester fabric.

Retain "Asphaltic Protection Course" or "Rubberized Sheet Protection Course" Paragraph below, or revise to insert other protection materials. Distinguish locations, such as plaza-deck and foundation walls, if more than one type of protection course is required.

        - Asphaltic Protection Course: ASTM D6506, semirigid sheets of fiberglass or mineral-reinforced-asphaltic core, pressure laminated between two asphalt-saturated fibrous liners and as follows:

          - Thickness: [1/8 inch (3 mm), nominal] [1/4 inch (6 mm), nominal] [1/8 inch (3 mm), nominal, for vertical applications; 1/4 inch (6 mm), nominal, elsewhere].

        - Rubberized Sheet Protection Course: Manufacturer's standard, 80- to 90-mil- (2.0- to 2.3-mm-) thick, fiberglass-reinforced rubberized asphalt or modified bituminous sheet.

      - MOLDED-SHEET DRAINAGE PANELS

Retain this article if drainage panels are required. Retain "Nonwoven-Geotextile-Faced, Molded-Sheet Drainage Panel" Paragraph below if specifying nonwoven-geotextile-faced drainage panels, usually for foundation walls.

        - Nonwoven-Geotextile-Faced, Molded-Sheet Drainage Panel: Manufactured composite subsurface drainage panels consisting of a nonwoven, needle-punched geotextile facing with an apparent opening size not exceeding No. 70 (0.21 mm) sieve, laminated to one side [with] [or] [without] a polymeric film bonded to the other side of a studded, nonbiodegradable, molded-plastic-sheet drainage core, with a vertical flow rate of 9 to 15 gpm/ft. (112 to 188 L/min. per m).

Retain "Woven-Geotextile-Faced, Molded-Sheet Drainage Panel" Paragraph below if specifying woven-geotextile-faced drainage panels, usually for plaza decks.

        - Woven-Geotextile-Faced, Molded-Sheet Drainage Panel: Manufactured composite subsurface drainage panels consisting of a woven-geotextile facing with an apparent opening size not exceeding No. 40 (0.43 mm) sieve, laminated to one side [with] [or] [without] a polymeric film bonded to the other side of a studded, nonbiodegradable, molded-plastic-sheet drainage core, with a horizontal flow rate not less than 2.8 gpm/ft. (35 L/min. per m).

      - INSULATION

Retain "Board Insulation" Paragraph below if board insulation is required over waterproofing and if board insulation forms the first layer beneath an insulation drainage panel. Type IV and Type VI insulation are usually limited to vertical applications. Type VII and Type V insulation, with higher compressive resistances, are used on plaza decks.

        - Board Insulation: Extruded-polystyrene board insulation complying with ASTM C578, [Type IV, 25 psi (173-kPa)] [Type VI, 40 psi (276 kPa)] [Type VII, 60 psi (414 kPa)] [Type V, 100 psi (690 kPa)] minimum compressive resistance, [square] [or] [shiplap] edged.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Unfaced Wall Insulation Drainage Panels" Paragraph below for unfaced insulation drainage panels for foundation wall applications. DiversiFoam's "CertiFoam 25 Drainage Board" and Dow's "Perimate" are Type IV. DiversiFoam's "CertiFoam 40 Drainage Board" is Type VI.

        - Unfaced Wall Insulation Drainage Panels: Extruded-polystyrene board insulation complying with ASTM C578, [Type IV, 25 psi (173 kPa)] [or] [Type VI, 40 psi (276 kPa)] minimum compressive resistance; unfaced; fabricated with shiplap or channel edges and with one side having grooved drainage channels.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Geotextile-Faced Wall Insulation Drainage Panels" Paragraph below for geotextile-faced insulation drainage panels for foundation wall applications. Owens Corning's "Insul-Drain" and T. Clear's "Thermadry 750" are Type IV; T. Clear's "Thermadry 1250" is Type VI.

        - Geotextile-Faced Wall Insulation Drainage Panels: Extruded-polystyrene board insulation complying with ASTM C578, [Type IV, 25 psi (173 kPa)] [or] [Type VI, 40 psi (276 kPa)] minimum compressive resistance; fabricated with tongue-and-groove edges and with one side having grooved drainage channels faced with a nonwoven, geotextile filter fabric.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Unfaced Plaza-Deck Insulation Drainage Panels" Paragraph below for plaza-deck applications if an unfaced insulation drainage panel with ribbed drainage channels is required. Retain Type VI insulation for limited, intermittent pedestrian traffic or Type VII for heavier pedestrian traffic. Dow's "Styrofoam Ribbed Roofmate" and Owens Corning's "Foamular 404 RB" are Type VI; DiversiFoam's "CertiFoam Plaza Deck" and Owens Corning's "Foamular 604 RB" are Type VII.

        - Unfaced Plaza-Deck Insulation Drainage Panels: Extruded-polystyrene board insulation complying with ASTM C578, [Type VI, 40 psi (276 kPa)] [Type VII, 60 psi (414 kPa)] minimum compressive resistance; unfaced; fabricated with shiplapped or channel edges and with one side having ribbed drainage channels.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Geotextile-Faced Plaza-Deck Insulation Drainage Panels" Paragraph below if Type VII geotextile-faced insulation is required for heavy pedestrian traffic.

        - Geotextile-Faced Plaza-Deck Insulation Drainage Panels: Extruded-polystyrene board insulation complying with ASTM C578, Type VII, 60 psi (414 kPa) minimum compressive resistance; fabricated with tongue-and-groove edges and with one side having grooved drainage channels faced with a nonwoven, geotextile filter fabric.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

      - PLAZA-DECK PAVERS

Retain this article for plaza-deck pavers supported on pedestals.

        - Plaza-Deck Pavers: [Brick] [Concrete] [Asphalt-block] [Granite] [Limestone] [Marble] [Quartz-based stone] [Slate] [Travertine] pavers specified in Section 321400 "Unit Paving."

"Concrete Plaza-Deck Pavers" Paragraph below describes concrete pavers commonly used in pedestal-set applications over insulation and waterproofing. Limit pedestal systems to pedestrian plazas. Verify availability of deck pavers with characteristics retained.

        - Concrete Plaza-Deck Pavers: Heavyweight, hydraulically pressed, concrete units, [square edged] [with top edges beveled 3/16 inch (5 mm)], manufactured for use as plaza-deck pavers; minimum compressive strength [7500 psi (52 MPa)] [6500 psi (45 MPa)] <Insert value>, ASTM C140; absorption not greater than 5 percent, ASTM C140; no breakage and maximum 1 percent mass loss when tested for freeze-thaw resistance in accordance with ASTM C67.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain one thickness and one face size from options in "Thickness" and "Face Size" subparagraphs below. Include special paver sizes and insert descriptions of custom pavers, such as stair tread and riser units, coping or curbed termination pavers, and oversize pavers.

          - Thickness: [1-5/8 inches (41 mm)] [1-3/4 inches (45 mm)] [2 inches (51 mm)] [2-3/8 inches (60 mm)] <Insert dimension>.

          - Face Size: [8-7/8 inches (225 mm) square] [9 inches (229 mm) square] [9 by 18 inches (229 by 457 mm)] [12 inches (305 mm) square] [12 by 24 inches (305 by 610 mm)] [18 inches (457 mm) square] [24 inches (610 mm) square] [As indicated] <Insert dimensions and shape>.

          - Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color>.

Retain "Paver Supports" Paragraph below if using pedestal systems for paver supports.

        - Paver Supports: Paver manufacturer's standard SBR rubber, high-density polyethylene, or polyurethane paver support assembly, including [fixed-height] [adjustable or stackable] pedestals, shims, and spacer tabs for joint spacing of [1/8 inch (3 mm)] [3/16 inch (5 mm)] [1/8 to 3/16 inch (3 to 5 mm)].

Retain "Concrete Fill" Subparagraph below if specifying Wausau's "Terr-Adjust" tilting and telescoping pedestals.

          - Concrete Fill: ACI 301, compressive strength of 5000 psi (34 MPa) at 28 days, and air content of 6 percent.

- EXECUTION

      - EXAMINATION

        - Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

          - Verify that concrete has cured and aged for minimum time period recommended by waterproofing manufacturer.

          - Verify that substrate is visibly dry and free of moisture. Test for capillary moisture by plastic sheet method in accordance with ASTM D4263.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - PREPARATION

        - Clean and prepare substrates according to manufacturer's written instructions. Provide clean, dust-free, and dry substrate for waterproofing application.

        - Mask off adjoining surfaces not receiving waterproofing to prevent spillage and overspray affecting other construction.

        - Close off deck drains and other deck penetrations to prevent spillage and migration of waterproofing fluids.

        - Remove grease, oil, form-release agents, paints, curing compounds, and other penetrating contaminants or film-forming coatings from concrete.

Retain subparagraph below if required for waterproofing adhesion. Verify substrate acceptability with manufacturers.

          - Abrasive blast clean concrete surfaces uniformly to expose top surface of fine aggregate in accordance with ASTM D4259 with a self-contained, recirculating, blast-cleaning apparatus. Remove material to provide a sound surface free of laitance, glaze, efflorescence, curing compounds, concrete hardeners, or form-release agents. Remove remaining loose material and clean surfaces in accordance with ASTM D4258.

        - Remove fins, ridges, and other projections, and fill honeycomb, aggregate pockets, and other voids.

      - JOINTS, CRACKS, AND TERMINATIONS

        - Prepare and treat substrates to receive waterproofing membrane, including joints and cracks, deck drains, corners, and penetrations according to manufacturer's written instructions.

          - Rout and fill joints and cracks in substrate. Before filling, remove dust and dirt in accordance with ASTM D4258.

Usually retain two subparagraphs below. Retain first for reinforcing strips over moving or large joints and cracks.

          - Adhere strip of elastomeric sheet to substrate in a layer of hot rubberized asphalt. Extend elastomeric sheet a minimum of 6 inches (150 mm) on each side of moving joints and cracks or joints and cracks exceeding 1/8 inch (3 mm) thick, and beyond deck drains and penetrations. Apply second layer of hot fluid-applied, rubberized asphalt over elastomeric sheet.

Retain subparagraph below for reinforcing strips over nonmoving joints and cracks not exceeding 1/8 inch (3 mm) thick.

          - Embed strip of reinforcing fabric into a layer of hot rubberized asphalt. Extend reinforcing fabric a minimum of 6 inches (150 mm) on each side of nonmoving joints and cracks not exceeding 1/8 inch (3 mm) thick, and beyond roof drains and penetrations.

Retain subparagraph below with fabric-reinforced joints for unreinforced waterproofing membrane.

            - Apply second layer of hot fluid-applied, rubberized asphalt over reinforcing fabric.

Revise or delete paragraph below if using expansion-joint gaskets or expansion-joint cover assemblies. Do not use modified bituminous flashing sheets for this condition.

        - At expansion joints and discontinuous deck-to-wall or deck-to-deck joints, bridge joints with elastomeric sheet extended a minimum of 6 inches (150 mm) on each side of joints and adhere to substrates in a layer of hot rubberized asphalt. Apply second layer of hot fluid-applied, rubberized asphalt over elastomeric sheet.

      - INSTALLATION OF FLASHING

        - Install elastomeric sheets at terminations of waterproofing membrane according to manufacturer's written instructions.

Retain first paragraph below for smooth surfaces of masonry and concrete walls and parapets.

        - Prime substrate with asphalt primer.

        - Install elastomeric sheet and adhere to deck and wall substrates in a layer of hot rubberized asphalt.

Revise dimensions in first paragraph below if required. Verify minimum and maximum height limits with manufacturers if required.

        - Extend elastomeric sheet up walls or parapets a minimum of 8 inches (200 mm) above plaza-deck pavers and 6 inches (150 mm) onto deck to be waterproofed.

Verify, with manufacturer, need for termination bars and mechanical fastening. Paragraph below is an example only.

        - Install termination bars and mechanically fasten to top of elastomeric flashing sheet at terminations and perimeter of waterproofing.

      - INSTALLATION OF HOT FLUID-APPLIED, RUBBERIZED ASPHALT WATERPROOFING MEMBRANE

        - Apply primer, at manufacturer's recommended rate, over prepared substrate and allow it to dry.

        - Heat and apply rubberized asphalt according to manufacturer's written instructions.

          - Heat rubberized asphalt in an oil- or air-jacketed melter with mechanical agitator specifically designed for heating rubberized asphalt.

Retain first paragraph below if applicable.

        - Start application with manufacturer's authorized representative present.

Retain "Unreinforced Membrane" or "Reinforced Membrane" Paragraph below, or both. If retaining both, indicate location of each system on Drawings.

        - Unreinforced Membrane: Apply hot rubberized asphalt to substrates and adjoining surfaces indicated. Spread to form a uniform, unreinforced, seamless membrane, [180-mil (4.5-mm) minimum thickness] [180-mil (4.5-mm) average thickness, but not less than 125 mils (3.2 mm) thick].

        - Reinforced Membrane: Apply hot rubberized asphalt to substrates and adjoining surfaces indicated. Spread to a thickness of 90 mils (2.3 mm); embed reinforcing fabric, overlapping sheets 2 inches (50 mm); spread another 125-mil- (3.2-mm-) thick layer to provide a uniform, reinforced, seamless membrane 215 mils (5.5 mm) thick.

        - Apply waterproofing over prepared joints and up wall terminations and vertical surfaces to heights indicated or required by manufacturer.

Protection course also prevents insulation from sticking to membrane. Retain first option in paragraph below for foundation wall applications and second option for horizontal applications.

        - Cover waterproofing with protection course with overlapped joints before membrane is subject to [backfilling] [construction or vehicular traffic].

      - INSTALLATION OF MOLDED-SHEET DRAINAGE PANELS

        - Place and secure molded-sheet drainage panels, with geotextile facing away from wall or deck substrate according to manufacturer's written instructions. Use methods that do not penetrate waterproofing. Lap edges and ends of geotextile to maintain continuity. Protect installed molded-sheet drainage panels during subsequent construction.

Retain subparagraph below if board insulation or protection course is installed before installing molded-sheet drainage panels.

          - For vertical applications, install [board insulation] [protection course] before installing drainage panels.

      - INSTALLATION OF INSULATION

        - Install [one or more layers of board insulation to achieve required thickness] [and] [insulation drainage panels] over waterproofed surfaces. Cut and fit to within 3/4 inch (19 mm) of projections and penetrations.

Retain first paragraph below if support is required during backfilling.

        - On vertical surfaces, set insulation units into rubberized asphalt according to manufacturer's written instructions.

        - On horizontal surfaces, loosely lay insulation units according to manufacturer's written instructions. Stagger end joints and tightly abut insulation units.

      - INSTALLATION OF PLAZA-DECK PAVERS

        - Install concrete pavers according to manufacturer's written instructions.

Retain first two paragraphs below if setting pavers on paving pedestals.

        - Accurately install [fixed] [adjustable]-height paver pedestals and accessories to elevations required. Adjust for final level and slope with shims.

Retain subparagraph below if using Wausau's "Terr-Adjust" tilting and telescoping paver pedestals.

          - Fill paver pedestal with concrete mix, strike smooth with top of pedestal, and cure in accordance with ACI 301.

        - Loosely lay pavers on pedestals, maintaining a uniform open joint width. Tightly seat pavers against spacers to eliminate lateral movement or drift of paving assembly. Align joint patterns parallel in each direction.

Revise subparagraph below to suit Project. Consider paved area layout, paver module, and construction tolerances when imposing limits. Verify minimum dimensions with paver manufacturer. Minimum pedestal dimensions may also govern. Custom-dimensioned pavers or pavers scored to repeat module may be available.

          - Lay out pavers to avoid less-than-half-width pavers at perimeter or other terminations.

Insert special installation requirements below. Examples might include tread/riser units on tabs or treatment of pavers at plaza/building expansion joints.

        - Install pavers to not vary more than 1/16 inch (1.6 mm) in elevation between adjacent pavers or more than 1/16 inch (1.6 mm) from surface plane elevation of individual paver.

        - Limit variation in paving installation to within [1/4 inch in 10 feet (6 mm in 3 m)] <Insert dimensions> of surface plane in any direction; noncumulative.

      - FIELD QUALITY CONTROL

Retain first paragraph below if a manufacturer's site representative is required. Manufacturer may also require this as a warranty condition.

        - Engage a full-time site representative qualified by waterproofing membrane manufacturer to inspect substrate conditions; surface preparation; and application of membrane, flashings, protection, and drainage components; furnish daily reports to Architect.

          - Site representative is to measure membrane thickness with pin tester or other suitable device at least once for every 100 sq. ft. (10 sq. m) and include measurements in reports.

Retain "Testing Agency" Paragraph below to identify who performs tests and inspections. If retaining second option in "Testing Agency" Paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to inspect substrate conditions, surface preparation, waterproofing application, protection, and drainage components, and to furnish reports to Architect.

Delete "Flood Testing" Subparagraph if waterproofing is limited to vertical applications. Revise below by identifying particular areas on Project to flood test when applicable. Limit water depth to not exceed load capacity of deck.

          - Flood Testing: Flood test each deck area for leaks, in accordance with recommendations in ASTM D5957, after completing and protecting waterproofing but before overlaying construction is placed. Install temporary containment assemblies, plug or dam drains, and flood with potable water. Testing agency is to observe flood testing.

            - Flood to an average depth of 2-1/2 inches (65 mm) with a minimum depth of 1 inch (25 mm) and not exceeding a depth of 4 inches (100 mm). Maintain 2 inches (50 mm) of clearance from top of sheet flashings.

ASTM D5957 sets 24 hours as the minimum and 72 hours as the maximum duration for flood testing.

            - Flood each area for [24] [48] [72] hours.

            - After flood testing, repair leaks, repeat flood tests, and make further repairs until waterproofing installation is watertight.

Retain "Electric Field Vector Mapping (EFVM)" Subparagraph below only if Contractor is required to hire testing agency to perform this testing.

          - Electric Field Vector Mapping (EFVM): Testing agency is to survey entire waterproofing area for potential leaks using EFVM.

      - CLEANING AND PROTECTION

        - Protect waterproofing from damage and wear during remainder of construction period.

Retain first paragraph below when board insulation or insulation drainage panels are required and may be exposed for a period on plaza decks.

        - Protect installed [board insulation] [insulation drainage panels] from damage due to UV light, harmful weather exposures, physical abuse, and other causes. Provide temporary coverings where insulation is subject to abuse and cannot be concealed and protected by permanent construction immediately after installation.

        - Clean spillage and soiling from adjacent construction using cleaning agents and procedures recommended by manufacturer of affected construction.

Insert Special Installer's Warranty Form below if required.

END OF SECTION 071413