Copyright 2022 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 079513.16 - EXTERIOR EXPANSION JOINT COVER ASSEMBLIES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Access Manufacturer-Provided, AIA MasterSpec-Based Sections:

<Double click here for this Section based on specific manufacturer’s products set as Basis-of-Design at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Exterior expansion joint covers.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 077129 "Manufactured Roof Expansion Joints" for factory-fabricated roof expansion joint cover assemblies.

          - Section 079100 "Preformed Joint Seals" for preformed foam and extruded-silicone joint seals.

          - Section 079513.19 "Parking Deck Expansion Joint Cover Assemblies" for expansion joint cover assemblies subject to vehicular traffic.

      - ACTION SUBMITTALS

        - Product Data: Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for expansion joint cover assemblies.

          - Exterior expansion joint covers.

        - Shop Drawings: For each expansion joint cover assembly.

          - Include plans, elevations, sections, details, splices, block-out requirement, attachments to other work, and line diagrams showing entire route of each expansion joint.

          - Where expansion joint cover assemblies change planes, provide isometric or clearly detailed drawing depicting how components interconnect.

Retain "Samples" Paragraph below for single-stage Samples, with a subordinate list if applicable. Retain "Samples for Initial Selection" and "Samples for Verification" paragraphs for two-stage Samples.

        - Samples: For each exposed expansion joint cover assembly and for each color and texture specified, full width by 6 inches (150 mm) long in size.

        - Samples for Initial Selection: For each type of exposed finish.

          - Include manufacturer's color charts showing the full range of colors and finishes available for each exposed metal and elastomeric seal material.

        - Samples for Verification: For each type of expansion joint cover assembly, full width by 6 inches (150 mm) long in size.

Retain "Expansion Joint Cover Assembly Schedule" Paragraph below for large and complex projects or projects with multiple expansion joint cover assemblies.

        - Expansion Joint Cover Assembly Schedule: Prepared by or under the supervision of the supplier. Include the following information in tabular form:

          - Manufacturer and model number for each expansion joint cover assembly.

          - Expansion joint cover assembly location cross-referenced to Drawings.

          - Nominal, minimum, and maximum joint width.

          - Movement direction.

          - Materials, colors, and finishes.

          - Product options.

Retain subparagraph below if fire-resistance-rated expansion joint cover assemblies are included in Project.

          - Fire-resistance ratings.

      - INFORMATIONAL SUBMITTALS

        - Product Test Reports: For each fire-resistance-rated expansion joint cover assembly, for tests performed by [manufacturer and witnessed by a qualified testing agency] [a qualified testing agency].

      - MOCKUPS

        - Build mockups to demonstrate aesthetic effects and to set quality standards for materials and execution.

          - Build mockup of typical expansion joint cover assembly as shown on Drawings.

          - Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing.

Retain subparagraph below if the intention is to make an exception to the default requirement in Section 014000 "Quality Requirements" for demolishing and removing mockups.

          - Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - ASSEMBLY DESCRIPTION

        - Furnish units in longest practicable lengths to minimize field splicing.

        - Include factory-fabricated closure materials and transition pieces, T-joints, corners, curbs, cross-connections, and other accessories as required to provide continuous expansion joint cover assemblies.

      - PERFORMANCE REQUIREMENTS

Retain "Seismic Performance" Paragraph below for projects requiring seismic design. Delete paragraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

        - Seismic Performance: Expansion joint cover assemblies shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain "Fire-Resistance Ratings" Paragraph below only if products specified are part of a fire-resistance-rated assembly. See the Evaluations for discussion of fire-resistance test methods.

        - Fire-Resistance Ratings: Provide expansion joint cover assemblies with fire barriers identical to those of systems tested for fire resistance according to [UL 2079] [or] [ASTM E1966] by a qualified testing agency.

Retain "Hose Stream Test" Subparagraph below if Project contains wall-to-wall or wall-to-soffit assemblies.

          - Hose Stream Test: Wall-to-wall and wall-to-soffit assemblies shall be subjected to hose stream testing.

Each Project expansion joint may require multiple expansion joint cover assemblies as it traverses multiple spaces and planes; however, the design criteria for each joint typically remains the same for the entire length of the joint. Copy, revise, and insert drawing designations in "Expansion Joint Design Criteria" Paragraph below for each expansion joint on the Project; then copy, revise, and insert drawing designations for one or more corresponding expansion joint cover assemblies in "Exterior Expansion Joint Covers" Article as required.

        - Expansion Joint Design Criteria <Insert drawing designation>:

Retain "Type of Movement" or "Seismic Movement" Subparagraph below. See "Building Movement" and "Movement Capability" articles in the Evaluations for a discussion of joint movement.

          - Type of Movement: [Thermal] [Wind sway].

            - Nominal Joint Width: [As indicated on Drawings] <Insert width>.

            - Minimum Joint Width: [As indicated on Drawings] <Insert width>.

            - Maximum Joint Width: [As indicated on Drawings] <Insert width>.

If retaining "Seismic Movement" Subparagraph below, indicate on Drawings horizontal, lateral, and vertical movement capability required for each expansion joint.

          - Seismic Movement:

            - Joint Movement: As indicated on Drawings.

      - EXTERIOR EXPANSION JOINT COVERS

See the Evaluations for descriptions and illustrations of types of expansion joint cover assemblies in paragraphs below.

Copy paragraphs below and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Exterior Metal-Plate Joint Cover <Insert drawing designation>: Assembly consisting of sliding metal cover plate in continuous contact with gaskets mounted on metal frames fixed to sides of joint gap.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Application: [Wall to wall] [Wall to soffit] [Soffit to soffit].

          - Installation: Surface mounted.

          - Fire-Resistance Rating: Not less than [that indicated on Drawings] [that of adjacent construction] [1 hour] [2 hours] <Insert rating>.

          - Exposed Metal:

            - Aluminum: [Mill] [Clear anodic, Class I] [Clear anodic, Class II] [Color anodic, Class I] [Color anodic, Class II] [Manufacturer's standard] <Insert finish>.

Retain "Color" Subparagraph below if retaining color anodic aluminum in "Aluminum" Subparagraph above.

              - Color: [Light bronze] [Dark bronze] [Match Architect's sample] [As selected by Architect from full range of industry colors and color densities] <Insert color>.

            - Stainless Steel: [No. 2B] [No. 4] [Manufacturer's standard] <Insert finish>.

            - Bronze: [Mill] [Manufacturer's standard] <Insert finish>.

            - Brass: [Mill] [Manufacturer's standard] <Insert finish>.

        - Exterior Elastomeric-Seal Joint Cover <Insert drawing designation>: Assembly consisting of elastomeric seal anchored to surface-mounted frames fixed to sides of joint gap.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Application: [Wall to wall] [Wall to soffit] [Soffit to soffit].

          - Installation: [Surface-mounted] [Recessed].

          - Fire-Resistance Rating: Not less than [that indicated on Drawings] [that of adjacent construction] [1 hour] [2 hours] <Insert rating>.

          - Exposed Metal:

            - Aluminum: [Mill] [Clear anodic, Class I] [Clear anodic, Class II] [Color anodic, Class I] [Color anodic, Class II] [Manufacturer's standard] <Insert finish>.

Retain "Color" Subparagraph below if retaining color anodic aluminum in "Aluminum" Subparagraph above.

              - Color: [Light bronze] [Dark bronze] [Match Architect's sample] [As selected by Architect from full range of industry colors and color densities] <Insert color>.

            - Stainless Steel: [No. 2B] [No. 4] [Manufacturer's standard] <Insert finish>.

            - Bronze: [Mill] [Manufacturer's standard] <Insert finish>.

            - Brass: [Mill] [Manufacturer's standard] <Insert finish>.

          - Seal: Preformed elastomeric membrane or extrusion.

            - Color: [Black] [Gray] [As selected by Architect from manufacturer's full range] <Insert color>.

        - Preformed Foam Joint Seals: Manufacturer's standard joint seal manufactured from urethane or EVA (ethylene vinyl acetate) foam with minimum density of 10 lb/cu. ft. (160 kg/cu. m) and impregnated with a nondrying, water-repellent agent. Factory produce in precompressed sizes in roll or stick form to fit joint widths based on design criteria indicated, with factory- or field-applied adhesive for bonding to substrates.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Design Criteria:

            - Nominal Joint Width: [As indicated on Drawings] <Insert dimension>.

If retaining "Minimum Joint Width" and "Maximum Joint Width" subparagraphs below, delete "Movement Capability" Subparagraph below.

            - Minimum Joint Width: [As indicated on Drawings] <Insert dimension>.

            - Maximum Joint Width: [As indicated on Drawings] <Insert dimension>.

"-25 percent/+25 percent" option in "Movement Capability" Subparagraph below is an example only; if retaining, revise as required. See Evaluations for explanation of movement capability.

            - Movement Capability: [As indicated on Drawings] [-25 percent/+25 percent] <Insert percentage>.

          - Joint Seal Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from full range of industry colors] <Insert color>.

      - MATERIALS

        - Aluminum: ASTM B221 (ASTM B221M), Alloy 6063-T5 for extrusions; ASTM B209 (ASTM B209M), Alloy 6061-T6 for sheet and plate.

          - Apply manufacturer's standard protective coating on aluminum surfaces to be placed in contact with cementitious materials.

        - Stainless Steel: ASTM A240/A240M or ASTM A666, Type 304 for plates, sheet, and strips.

In "Brass" and "Bronze" paragraphs below, the term "brass" refers to copper alloys that have a brassy-yellow color, and the term "bronze" refers to alloys that are darker in color, similar to "architectural bronze"; neither is true tin-bronze.

        - Brass: ASTM B36/B36M, UNS Alloy C26000 for half hard sheet and coil.

        - Bronze: ASTM B455, Alloy C38500 for extrusions; Alloy C23000 red brass for plates.

        - Elastomeric Seals: Manufacturer's standard preformed elastomeric membranes or extrusions to be installed in metal frames.

        - Fire Barriers: Any material or material combination, when fire tested after cycling, designated to resist the passage of flame and hot gases through a movement joint and to comply with performance criteria for required fire-resistance rating.

        - Moisture Barrier: Manufacturer's standard, flexible elastomeric material.

      - ALUMINUM FINISHES

If retaining more than one finish, indicate location of each on Drawings or by inserts.

        - Mill finish.

Retain one of two options in "Clear Anodic Finish" Paragraph below. Verify availability with manufacturers.

        - Clear Anodic Finish: AAMA 611, [AA-M12C22A41, Class I, 0.018 mm] [AA-M12C22A31, Class II, 0.010 mm] or thicker.

Retain one of two options in "Color Anodic Finish" Paragraph below. Verify availability with manufacturers.

        - Color Anodic Finish: AAMA 611, [AA-M12C22A42/A44, Class I, 0.018 mm] [AA-M12C22A32/A34, Class II, 0.010 mm] or thicker.

      - STAINLESS STEEL FINISHES

        - Surface Preparation: Remove tool and die marks and stretch lines, or blend into finish.

        - Polished Finishes: Grind and polish surfaces to produce uniform finish, free of cross scratches.

Retain first subparagraph below for directional finishes.

          - Run grain of directional finishes with long dimension of each piece.

          - When polishing is completed, passivate and rinse surfaces. Remove embedded foreign matter and leave surfaces chemically clean.

          - Directional Satin Finish: No. 4.

Retain "Bright, Cold-Rolled, Unpolished Finish" Paragraph below for nondirectional finish.

        - Bright, Cold-Rolled, Unpolished Finish: No. 2B.

      - COPPER-ALLOY FINISHES

Retain this article for brass or bronze finishes. Many manufacturers do not publish data indicating compliance with "Buffed Finish" or "Medium-Satin Finish" paragraphs in this article. Confirm available finishes with manufacturers before revising.

        - Buffed Finish: M21 (Mechanical Finish: buffed, smooth specular).

        - Medium-Satin Finish: M32 (Mechanical Finish: directionally textured, medium satin).

      - ACCESSORIES

Retain "Moisture Barriers" Paragraph below if required as secondary seal for exterior expansion joint cover assemblies. Indicate locations on Drawings.

        - Moisture Barriers: Manufacturer's standard continuous, waterproof membrane within joint and attached to substrate on sides of joint.

          - Provide where indicated on Drawings.

        - Manufacturer's [standard] [stainless steel] attachment devices. Include anchors, clips, fasteners, set screws, spacers, and other accessories compatible with material in contact, as indicated or required for complete installations.

- EXECUTION

      - EXAMINATION

        - Examine surfaces where expansion joint cover assemblies will be installed for installation tolerances and other conditions affecting performance of the Work.

        - Notify Architect where discrepancies occur that will affect proper expansion joint cover assembly installation and performance.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - PREPARATION

        - Prepare substrates according to expansion joint cover assembly manufacturer's written instructions.

        - Coordinate and furnish anchorages, setting drawings, and instructions for installing expansion joint cover assemblies. Provide fasteners of metal, type, and size to suit type of construction indicated and to provide for secure attachment of expansion joint cover assemblies.

      - INSTALLATION

        - Comply with manufacturer's written instructions for storing, handling, and installing expansion joint cover assemblies and materials unless more stringent requirements are indicated.

        - Metal Frames: Perform cutting, drilling, and fitting required to install expansion joint cover assemblies.

          - Install in true alignment and proper relationship to joints and adjoining finished surfaces measured from established lines and levels.

          - Adjust for differences between actual structural gap and nominal design gap due to ambient temperature at time of installation.

          - Cut and fit ends to accommodate thermal expansion and contraction of metal without buckling of frames.

          - Install frames in continuous contact with adjacent surfaces.

            - Shimming is not permitted.

          - Locate anchors at interval recommended by manufacturer, but not less than 3 inches (75 mm) from each end and not more than 24 inches (600 mm) o.c.

Retain "Elastomeric Seals" Paragraph below for systems with elastomeric seals.

        - Elastomeric Seals: Install elastomeric seals and membranes in frames to comply with manufacturer's written instructions. Install with minimum number of end joints.

          - Provide in continuous lengths for straight sections.

          - Seal transitions. Vulcanize or heat-weld field-spliced joints as recommended by manufacturer.

          - Mechanically lock seals into frames or adhere to frames with adhesive or pressure-sensitive tape as recommended by manufacturer.

Retain "Preformed Foam Joint Seals" Paragraph below for foam joint seals.

        - Preformed Foam Joint Seals: Install in compliance with manufacturer's written instructions. Install with minimum number of end joints.

          - Install each length of seal immediately after removing protective wrapping.

          - Firmly secure compressed joint seals to joint gap side to obtain full bond using exposed pressure-sensitive adhesive or field-applied adhesive as recommended by manufacturer.

          - Do not pull or stretch material. Produce seal continuity at splices, ends, turns, and intersections of joints.

          - For applications at low ambient temperatures, heat foam joint seal material in compliance with manufacturer's written instructions.

        - Install with hairline mitered corners where expansion joint cover assemblies change direction or abut other materials.

        - Terminate exposed ends of expansion joint cover assemblies with field- or factory-fabricated termination devices.

Retain "Fire-Resistance-Rated Assemblies" Paragraph below if required.

        - Fire-Resistance-Rated Assemblies: Coordinate installation of expansion joint cover assembly materials and associated work so complete assemblies comply with performance requirements.

          - Fire Barriers: Install fire barriers to provide continuous, uninterrupted fire resistance throughout length of joint, including transitions and field splices.

Retain "Moisture Barrier Drainage" Paragraph below if retaining moisture barriers, and indicate method of drainage and location of fitting on Drawings.

        - Moisture Barrier Drainage: If indicated, provide drainage fitting and connect to drains.

      - CONNECTIONS

        - Transition to Roof Expansion Joint Covers: Coordinate installation of exterior wall and soffit expansion joint covers with roof expansion joint covers specified in Section 077129 "Manufactured Roof Expansion Joints."[ Install factory-fabricated units at transition between exterior walls and soffits and roof expansion joint cover assemblies.]

      - PROTECTION

        - Do not remove protective covering until finish work in adjacent areas is complete. When protective covering is removed, clean exposed metal surfaces to comply with manufacturer's written instructions.

        - Protect the installation from damage by work of other Sections.

END OF SECTION 079513.16