Copyright 2022 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 081416 - FLUSH WOOD DOORS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Access Manufacturer-Provided, AIA MasterSpec-Based Sections:

<Double click here for this Section based on specific manufacturer’s products set as Basis-of-Design at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED v4, LEED v4.1, IgCC/ASHRAE 189.1, and Green Globes. Sustainable design requirements may be inserted in the Section Text using the hypertext links.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Solid-core five-ply flush wood veneer-faced doors and transom panels for transparent finish.

          - Solid-core five-ply flush wood doors and transom panels for opaque finish.

          - Solid-core seven-ply flush wood veneer-faced doors and transom panels for transparent finish.

          - Solid-core seven-ply flush wood doors and transom panels for opaque finish.

          - Solid-core flush wood doors and transom panels with plastic-laminate-faces.

          - Hollow-core flush wood veneer-faced doors for transparent finish.

          - Hollow-core flush wood doors for opaque finish.

          - Hollow-core flush wood doors with plastic-laminate faces.

          - Fire-rated wood door frames.

          - Light frames and louvers.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 064023 "Interior Architectural Woodwork" for wood door frames[ including 20-minute fire-rated wood door frames].

Retain first subparagraph below if any doors are blueprint matched with wood paneling.

          - Section 064216 "Flush Wood Paneling" for requirements for veneers from the same flitches for both flush wood doors and flush wood paneling.

          - Section 083473.16 "Wood Sound Control Door Assemblies" for acoustic flush wood doors.

          - Section 088000 "Glazing" for glass view panels in flush wood doors.

          - [Section 099113 "Exterior Painting"] [Section 099123 "Interior Painting"] [and] [Section 099300 "Staining and Transparent Finishing"] for field finishing doors.

          - Section 134900 "Radiation Protection" for lead-lined flush wood doors.

      - PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a conference.

        - Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

If needed, insert list of conference participants not mentioned in Section 013100 "Project Management and Coordination."

      - ACTION SUBMITTALS

        - Product Data:

          - Solid-core five-ply flush wood veneer-faced doors and transom panels for transparent finish.

          - Solid-core five-ply flush wood doors and transom panels for opaque finish.

          - Solid-core seven-ply flush wood veneer-faced doors and transom panels for transparent finish.

          - Solid-core seven-ply flush wood doors and transom panels for opaque finish.

          - Solid-core flush wood doors and transom panels with plastic-laminate-faces.

          - Hollow-core flush wood veneer-faced doors for transparent finish.

          - Hollow-core flush wood doors for opaque finish.

          - Hollow-core flush wood doors with plastic-laminate faces.

          - Fire-rated wood door frames.

          - Light frames and louvers.

        - Product Data Submittals: For each product, including the following:

          - Door core materials and construction.

          - Door edge construction

          - Door face type and characteristics.

          - Door louvers.

          - Door trim for openings.

          - Door frame construction.

          - Factory-machining criteria.

          - Factory-[priming] [finishing] specifications.

        - Sustainable Design Submittals:

          - <Double click to insert sustainable design text for EPDs and HPDs.>

          - <Double click to insert sustainable design text for regional materials.>

          - <Double click to insert sustainable design text for certified wood.>

          - <Double click to insert sustainable design text for certified wood.>

          - <Double click to insert sustainable design text for adhesives.>

          - <Double click to insert sustainable design text for composite wood.>

        - Shop Drawings: Indicate location, size, and hand of each door; elevation of each type of door; construction details not covered in Product Data; and the following:

          - Door schedule indicating door[ and frame] location, type, size, fire protection rating, and swing.

          - Door elevations, dimension and locations of hardware, lite and louver cutouts, and glazing thicknesses.

          - Details of frame for each frame type, including dimensions and profile.

          - Details of electrical raceway and preparation for electrified hardware, access control systems, and security systems.

          - Dimensions and locations of blocking for hardware attachment.

          - Dimensions and locations of mortises and holes for hardware.

          - Clearances and undercuts.

          - Requirements for veneer matching.

          - Doors to be factory [primed] [finished] and application requirements.

Retain subparagraph below and applicable option if retaining other requirements for AWI's or WI's quality certification programs.

          - Apply [AWI Quality Certification] [WI Certified Compliance] Program label to Shop Drawings.

        - Samples for Initial Selection: For [plastic-laminate door faces] [polymer edging] [factory-finished doors] [and] [factory-finished door frames].

Delete "Samples for Initial Selection" Paragraph above if colors and other characteristics are preselected and specified or scheduled. Retain "Samples for Verification" Paragraph below with or without above.

        - Samples for Verification:

Consider deleting first three subparagraphs below if retaining corner-section Samples.

          - Factory finishes applied to actual door face materials, approximately 8 by 10 inches (200 by 250 mm), for each material and finish.[ For each wood species and transparent finish, provide set of three Samples showing typical range of color and grain to be expected in finished Work.]

          - Plastic laminate, 6 inches (150 mm) square, for each color, texture, and pattern selected.

          - Polymer edging, in manufacturer's standard colors.

          - Corner sections of doors, approximately 8 by 10 inches (200 by 250 mm), with door faces and edges representing actual materials to be used.

          - Louver blade and frame sections, 6 inches (150 mm) long, for each material and finish specified.

          - Frames for light openings, 6 inches (150 mm) long, for each material, type, and finish required.

      - INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Data: For door inspector.

Retain one of or both "Fire-Rated Door Inspector" and "Egress Door Inspector" subparagraphs below, or delete first two subparagraphs and retain third subparagraph. First paragraph applies to the IBC and NFPA 101. Second subparagraph applies to NFPA 101. Certification in third subparagraph below should be acceptable by all authorities having jurisdiction. See the Evaluations.

          - Fire-Rated Door Inspector: Submit documentation of compliance with NFPA 80, Section 5.2.3.1.

          - Egress Door Inspector: Submit documentation of compliance with NFPA 101, Section 7.2.1.15.4.

          - Submit copy of DHI's Fire and Egress Door Assembly Inspector (FDAI) certificate.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

        - Sample Warranty: For special warranty.

      - CLOSEOUT SUBMITTALS

        - Special warranties.

Retain "Quality Standard Compliance Certificates" Paragraph below if AWI Quality Certification Program or WI Certified Compliance Program is required.

        - Quality Standard Compliance Certificates: [AWI Quality Certification] [WI Certified Compliance] Program certificates.

        - Record Documents: For fire-rated doors, list of door numbers and applicable room name and number to which door accesses.

      - QUALITY ASSURANCE

        - <Double click to insert sustainable design text for manufacturer qualifications.>

        - <Double click to insert sustainable design text for vendor qualifications.>

Retain one of two options in "Manufacturer's Certification" Paragraph below if AWI Quality Certification Program or WI Certified Compliance Program is required. Both AWI and WI will inspect work and provide certification for work that passes inspection if manufacturer is not licensed under their respective programs.

        - Manufacturer's Certification: Licensed participant in [AWI's Quality Certification Program] [WI's Certified Compliance Program].

        - Fire-Rated Door Inspector Qualifications: Inspector for field quality-control inspections of fire-rated door assemblies complies with qualifications set forth in NFPA 80, Section 5.2.3.1 and the following:

Retain subparagraph below if requiring fire door inspectors to be certified under DHI's certification program. Verify, with authorities having jurisdiction, if other DHI certifications are acceptable, such as Architectural Hardware Consultant (AHC), Certified Door Consultant (CDC), and Architectural Openings Consultant (AOC).

          - DHI's Fire and Egress Door Assembly Inspector (FDAI) certification.

        - Egress Door Inspector Qualifications: Inspector for field quality-control inspections of egress door assemblies complies with qualifications set forth in NFPA 101, Section 7.2.1.15.4 and the following:

Retain subparagraph below if requiring egress door inspectors to be certified under DHI's certification program. Verify, with authorities having jurisdiction, if other DHI certifications are acceptable, such as AHC, CDC and AOC.

          - DHI's Fire and Egress Door Assembly Inspector (FDAI) certification.

      - DELIVERY, STORAGE, AND HANDLING

        - Comply with requirements of referenced standard and manufacturer's written instructions.

Retain first paragraph below for factory-finished doors and high-quality unfinished doors. Second option is standard with some manufacturers and costs extra with others.

        - Package doors individually in [plastic bags or cardboard cartons] [cardboard cartons, and wrap bundles of doors in plastic sheeting].

        - Mark each door on[ top and] bottom rail with opening number used on Shop Drawings.

      - FIELD CONDITIONS

        - Environmental Limitations:

Retain subparagraph below if relative humidity is not controlled during occupancy.

          - Do not deliver or install doors until spaces are enclosed and weathertight, wet-work in spaces is complete and dry, and HVAC system is operating and maintaining temperature and relative humidity at levels designed for building occupants for the remainder of construction period.

Retain subparagraph below if relative humidity will be controlled after building is occupied, and retain one of three options or insert another range based on local climatological data. First option applies to Ontario, Quebec, and most of the United States. Second option applies to damp coastal areas of southern United States and the Maritime Provinces. Third option applies to dry southwestern United States and to Alberta, Manitoba, and Saskatchewan. For unfinished wood doors, narrower ranges will be required to maintain optimum moisture content. See relative humidity and moisture-content map in AWI/AWMCA/WI's "Architectural Woodwork Standards."

          - Do not deliver or install doors until building is enclosed and weathertight, wet work is complete, and HVAC system is operating and maintaining temperature between 60 and 90 deg F (16 and 32 deg C) and relative humidity between [25 and 55] [43 and 70] [17 and 50] <Insert numbers> percent during remainder of construction period.

      - WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

        - Special Warranty: Manufacturer agrees to repair or replace doors[ and frames] that fail in materials or workmanship within specified warranty period.

          - Failures include, but are not limited to, the following:

            - Delamination of veneer.

            - Warping (bow, cup, or twist) more than 1/4 inch (6.4 mm) in a 42-by-84-inch (1067-by-2134-mm) section.

            - Telegraphing of core construction in face veneers exceeding 0.01 inch in a 3-inch (0.25 mm in a 76.2-mm) span.

Retain or delete first subparagraph below to suit Project. This provision is not standard with all manufacturers.

          - Warranty also includes installation and finishing that may be required due to repair or replacement of defective doors[ and frames].

Warranties for exterior doors vary from no warranty to a warranty for a period of up to five years. Before retaining "Warranty Period for Solid-Core Exterior Doors" Subparagraph below, verify availability of warranty period with manufacturers; delete if retaining manufacturers that offer no warranty. Standard manufacturer's warranty generally goes into effect on date of shipment, not date of Substantial Completion.

          - Warranty Period for Solid-Core Exterior Doors: [Two] [Five] <Insert number> years from date of Substantial Completion.

"Warranty Period for Solid-Core Interior Doors" Subparagraph below is typical; revise if required. Coordinate with manufactures included in Part 2.

          - Warranty Period for Solid-Core Interior Doors: Life of installation.

Warranties for hollow-core doors vary with manufacturer and type of hollow core. Before retaining "Warranty Period for Hollow-Core Interior Doors" Subparagraph below, verify availability of warranty period with manufacturers. Standard manufacturer's warranties generally go into effect on date of shipment, not date of Substantial Completion.

          - Warranty Period for Hollow-Core Interior Doors: [One] [Two] <Insert number> year(s) from date of Substantial Completion.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - SOURCE LIMITATIONS

Retain one or both options in paragraph below for wood doors that are matched with wood paneling.

        - Obtain flush wood doors [indicated to be blueprint matched with paneling] [and wood paneling] from single manufacturer.

      - PERFORMANCE REQUIREMENTS

Retain "Fire-Rated Wood Doors and Frame Assemblies" Paragraph below if applicable.

        - Fire-Rated Wood Door and Frame Assemblies: Assemblies complying with NFPA 80 that are listed and labeled by a qualified testing agency acceptable to authorities having jurisdiction, for fire-protection ratings [and temperature-rise limits ]indicated on Drawings, based on testing at positive pressure in accordance with [UL 10C] [or] [NFPA 252].

Retain "Oversize Fire-Rated Door Assemblies" Subparagraph below if required by authorities having jurisdiction.

          - Oversize Fire-Rated Door Assemblies: For units exceeding sizes of tested assemblies, provide certification by a qualified testing agency that doors comply with standard construction requirements for tested and labeled fire-rated door assemblies except for size.

Retain "Temperature-Rise Limit" Subparagraph below if required. The IBC allows an exception for buildings equipped throughout with fire-suppression sprinklers.

          - Temperature-Rise Limit: [Where indicated on Drawings] [At vertical exit enclosures and exit passageways], provide doors that have a maximum transmitted temperature end point of not more than 450 deg F (250 deg C) above ambient after 30 minutes of standard fire-test exposure.

Retain "Smoke- and Draft-Control Door Assemblies" Paragraph below if required. The IBC requires fire door assemblies to comply with smoke- and draft-control requirements in corridors, smoke barriers, and smoke partitions.

        - Smoke- and Draft-Control Door Assemblies: Listed and labeled for smoke and draft control by a qualified testing agency acceptable to authorities having jurisdiction, based on testing in accordance with UL 1784 and installed in compliance with NFPA 105.

      - FLUSH WOOD DOORS AND FRAMES, GENERAL

Retain one standard in "Quality Standard" Paragraph below. Review retained standard and coordinate its requirements with retained options. See the Evaluations.

        - Quality Standard: In addition to requirements specified, comply with [AWI/AWMAC/WI's "Architectural Woodwork Standards."] [ANSI/WDMA I.S. 1A.]

Certification programs in first subparagraph below are available to member and nonmember firms of AWI and WI. Both organizations will inspect doors and provide certification for doors that pass inspection if door manufacturer is not licensed.

          - Provide [labels] [and] [certificates] from [AWI] [WI] certification program indicating that doors[ and frames] comply with requirements of grades specified.

Retain one of first two subparagraphs below if Project is to be certified under AWI Quality Certification Program.

            - This project has been registered with AWI as AWI Quality Certification Program Number <Insert number>.

            - Contractor registers the Work under this Section with the AWI Quality Certification Program at www.awiqcp.org or by calling 855-345-0991.

Retain subparagraph below only if Drawings and Specifications are more restrictive than quality standard requirements.

          - The Contract Documents contain requirements that are more stringent than the referenced quality standard. Comply with the Contract Documents in addition to those of the referenced quality standard.

        - <Double click to insert sustainable design text for regional materials.>

        - <Double click to insert sustainable design text for certified wood.>

        - <Double click to insert sustainable design text for adhesives.>

        - <Double click to insert sustainable design text for composite wood products.>

      - SOLID-CORE FIVE-PLY FLUSH WOOD VENEER-FACED DOORS AND TRANSOM PANELS FOR TRANSPARENT FINISH

Retain this article for traditional five-ply flush wood doors. Doors with two-ply faces (skins), currently marketed by some manufacturers as five-ply doors, are specified in "Seven-Ply Flush Wood Veneer-Faced Doors and Transom Panels for Transparent Finish" Article, as they are seven-ply doors in actuality.

Insert drawing designation, if applicable, for each product required. Use these designations on Drawings to identify each product.

        - Exterior Doors, Solid-Core Five-Ply Veneer-Faced <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

WDMA indicates that its standard is not intended for exterior doors. If exterior flush wood doors are required and ANSI/WDMA I.S. 1A is referenced, usually retain first option in "Performance Grade" Subparagraph below.

          - Performance Grade: ANSI/WDMA I.S. 1A [Extra Heavy Duty] [Heavy Duty] [as indicated on Drawings].

Retain "ANSI/WDMA I.S. 1A Quality Grade" or "Architectural Woodwork Standards Quality Grade" Subparagraph below.

          - ANSI/WDMA I.S. 1A Quality Grade: [Premium] [Custom].

          - Architectural Woodwork Standards Quality Grade: [Premium] [Custom].

          - Faces: Single-ply wood veneer not less than 1/50 inch (0.508 mm) thick.

Options in "Species" Subparagraph below are examples only; revise or insert another species.

            - Species: [Anigre] [Select white ash] [Figured select white ash] [Select white birch] [Select red birch] [Cherry] [Select red gum] [Figured select red gum] [Select white maple] [Red oak] [White oak] [Persimmon] [Sapele] [Sycamore] [Walnut] <Insert species>.

First option in "Cut" Subparagraph below applies only to oak.

            - Cut: [Rotary cut] [Plain sliced (flat sliced)] [Quarter sliced] [Rift cut].

            - Match between Veneer Leaves: [Book] [Slip] [Random] match.

In "Assembly of Veneer Leaves on Door Faces" Subparagraph below, first option is standard for Premium-grade doors. Third option is standard for Custom-grade doors.

            - Assembly of Veneer Leaves on Door Faces: [Center-balance] [Balance] [Running] match.

            - Pair and Set Match: Provide for doors hung in same opening[ or separated only by mullions].

Retain "Exposed Vertical and Top Edges" Subparagraph below if top edges of doors are visible, such as doors in multistory spaces. Retain one of four options; last two require factory prefitting.

          - Exposed Vertical and Top Edges: [Same species as faces or a compatible species - Architectural Woodwork Standards edge Type A] [Same species as faces - Architectural Woodwork Standards edge Type A] [Applied wood-veneer edges of same species as faces and covering edges of faces - Architectural Woodwork Standards edge Type B] [Applied wood edges of same species as faces and covering edges of crossbands - Architectural Woodwork Standards edge Type D].

          - Core:

Retain one of first four subparagraphs below. Particleboard cores are not generally recommended for exterior doors.

            - ANSI A208.1, [Grade LD-1] [Grade LD-2] particleboard.

            - Glued wood stave.

            - WDMA I.S. 10 structural composite lumber.

In each of first two subparagraphs below, first option is for Extra Heavy Duty performance grade, second option is for Heavy Duty performance grade.

              - Screw Withdrawal, Door Face: [550 lbf (2440 N)] [475 lb (2110 N)].

              - Screw Withdrawal, Vertical Door Edge: [550 lbf (2440 N)] [475 lb (2110 N)].

            - Either glued wood stave or WDMA I.S. 10 structural composite lumber.

          - Construction: Five plies, hot-pressed bonded (vertical and horizontal edging is bonded to core), with entire unit abrasive planed before veneering.

          - Adhesives: Type I in accordance with WDMA T.M. 6.

Insert drawing designation, if applicable, for each product required. Use these designations on Drawings to identify each product.

        - Interior Doors, Solid-Core Five-Ply Veneer-Faced <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Performance Grade" or "Performance Grade by Location" Subparagraph below to specify performance grade if referencing ANSI/WDMA I.S. 1A.

          - Performance Grade: ANSI/WDMA I.S. 1A [Extra Heavy Duty] [Heavy Duty] [Standard Duty] [as indicated on Drawings].

          - Performance Grade by Location:

            - ANSI/WDMA I.S. 1A Extra Heavy Duty: [Classrooms] [public toilets] [janitor's closets] [assembly spaces] [exits] [and] [patient rooms] <Insert locations> [and where indicated on Drawings].

            - ANSI/WDMA I.S. 1A Standard Duty: [Closets (not including janitor's closets)] [and] [private toilets] <Insert locations> [and where indicated on Drawings].

Retain "ANSI/WDMA I.S. 1A Quality Grade" or "Architectural Woodwork Standards Quality Grade" Subparagraph below.

          - ANSI/WDMA I.S. 1A Quality Grade: [Premium] [Custom].

          - Architectural Woodwork Standards Quality Grade: [Premium] [Custom].

          - Faces: Single-ply wood veneer not less than 1/50 inch (0.508 mm) thick.

Options in "Species" Subparagraph below are examples only; revise or insert another species.

            - Species: [Anigre] [Select white ash] [Figured select white ash] [Select white birch] [Select red birch] [Cherry] [Select red gum] [Figured select red gum] [Select white maple] [Red oak] [White oak] [Persimmon] [Sapele] [Sycamore] [Walnut] <Insert species>.

First option in "Cut" Subparagraph below applies only to oak.

            - Cut: [Rotary cut] [Plain sliced (flat sliced)] [Quarter sliced] [Rift cut].

            - Match between Veneer Leaves: [Book] [Slip] [Random] match.

In "Assembly of Veneer Leaves on Door Faces" Subparagraph below, first option is standard for Premium-grade doors. Third option is standard for Custom-grade doors.

            - Assembly of Veneer Leaves on Door Faces: [Center-balance] [Balance] [Running] match.

            - Pair and Set Match: Provide for doors hung in same opening[ or separated only by mullions].

            - Room Match:

Retain one of first two subparagraphs below only for highest-quality work with Premium-grade doors.

              - Match door faces within each separate room or area of building. Corridor-door faces do not need to match where they are separated by [10 feet (3 m)] [20 feet (6 m)] <Insert dimension> or more.

First subparagraph below is based on requirement for WI Premium-grade doors.

              - Provide door faces of compatible color and grain within each separate room or area of building.

Before retaining "Transom Match" Subparagraph below, verify availability of veneers for selected matching; usually retain first option. See "Referenced Standards" Article in the Evaluations.

            - Transom Match: [Continuous match] [End match] [As indicated].

            - Blueprint Match: Where indicated, provide doors with faces produced from same flitches as adjacent wood paneling and arranged to provide blueprint match with wood paneling. Comply with requirements in Section 064216 "Flush Wood Paneling."

Retain "Exposed Vertical and Top Edges" Subparagraph below if top edges of doors are visible, such as doors in multistory spaces. Retain one of four options; last two require factory prefitting.

          - Exposed Vertical and Top Edges: [Same species as faces or a compatible species - Architectural Woodwork Standards edge Type A] [Same species as faces - Architectural Woodwork Standards edge Type A] [Applied wood-veneer edges of same species as faces and covering edges of faces - Architectural Woodwork Standards edge Type B] [Applied wood edges of same species as faces and covering edges of crossbands - Architectural Woodwork Standards edge Type D].

            - Fire-Rated Single Doors: Provide edge construction with intumescent seals concealed by outer stile. Comply with specified requirements for exposed vertical edges.

            - Fire-Rated Pairs of Doors:

Retain one of first two subparagraphs below. Retain first subparagraph if steel edges and astragals are unacceptable. Coordinate availability and ratings with manufacturers. Retain second subparagraph if steel edges and astragals are acceptable.

              - Provide fire-retardant stiles that are listed and labeled for applications indicated without formed-steel edges and astragals. Provide stiles with concealed intumescent seals. Comply with specified requirements for exposed edges.

              - Provide formed-steel edges and astragals with intumescent seals.

                - Finish steel edges and astragals with baked enamel[ same color as doors].

Retain last subparagraph above or first subparagraph below; delete option above if edges and astragals are field painted.

                - Finish steel edges and astragals to match door hardware (locksets or exit devices).

            - Mineral-Core Doors: At hinge stiles, provide laminated-edge construction with improved screw-holding capability and split resistance. Comply with specified requirements for exposed edges.

Requirements in "Screw-Holding Capability" Subparagraph below are from ANSI/WDMA I.S. 1A. Options are performance duty levels for Extra Heavy Duty, Heavy Duty, and Standard Duty, respectively. Before retaining, verify that products comply with requirement selected.

              - Screw-Holding Capability: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)] in accordance with WDMA T.M. 10.

          - Core for Non-Fire-Rated Doors:

Retain one or more of first four subparagraphs below.

            - ANSI A208.1, [Grade LD-1] [Grade LD-2] particleboard.

Consider deleting "Blocking" Subparagraph below. Some door manufacturers contend that blocking weakens particleboard-core doors and is not required. If retaining subparagraph, retain one of two options.

              - Blocking: Provide wood blocking in particleboard-core doors as [needed to eliminate through-bolting hardware.] [follows:]

If retaining "Blocking" Subparagraph and second option above, retain first three subparagraphs below for blocking required.

                - 5-inch (125-mm) top-rail blocking, in doors indicated to have closers.

                - 5-inch (125-mm) bottom-rail blocking, in exterior doors and doors indicated to have kick, mop, or armor plates.

                - 5-inch (125-mm) midrail blocking, in doors indicated to have exit devices.

Usually delete requirement for midrail blocking in last subparagraph above and retain first subparagraph below.

              - Provide doors with [glued-wood-stave] [or] [WDMA I.S. 10 structural-composite-lumber] cores instead of particleboard cores for doors scheduled to receive exit devices in [Section 087100 "Door Hardware."] [Section 087111 "Door Hardware (Descriptive Specification."]

            - Glued wood stave.

            - WDMA I.S. 10 structural composite lumber.

In each of first two subparagraphs below, first option is for Extra Heavy Duty performance grade, second option is for Heavy Duty performance grade.

              - Screw Withdrawal, Door Face: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)].

              - Screw Withdrawal, Vertical Door Edge: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)].

            - Either glued wood stave or WDMA I.S. 10 structural composite lumber.

          - Core for Fire-Rated Doors: As required to achieve fire-protection rating indicated on Drawings.

            - Blocking for Mineral-Core Doors: Provide composite blocking with improved screw-holding capability approved for use in doors of fire-protection ratings indicated on Drawings as [needed to eliminate through-bolting hardware.] [follows:]

Retain "Blocking for Mineral-Core Doors" Subparagraph above and first four subparagraphs below only after verifying availability for fire-protection rating required. Delete first four subparagraphs below if retaining first option above.

              - 5-inch (125-mm) top-rail blocking.

              - 5-inch (125-mm) bottom-rail blocking, in doors indicated to have protection plates.

              - 5-inch (125-mm) midrail blocking, in doors indicated to have armor plates.

              - [4-1/2-by-10-inch (114-by-250-mm) lock blocks] [5-inch (125-mm) midrail blocking], in doors indicated to have exit devices.

          - Construction: Five plies, hot-pressed bonded (vertical and horizontal edging is bonded to core), with entire unit abrasive planed before veneering.

      - SOLID-CORE FIVE-PLY FLUSH WOOD DOORS AND TRANSOM PANELS FOR OPAQUE FINISH

Retain this article for traditional five-ply flush wood doors. Doors with two-ply faces (skins), currently marketed by some manufacturers as five-ply doors, are specified under "Seven-Ply Flush Wood Veneer -Faced Doors and Transom Panels for Opaque Finish" Article, as they are seven-ply doors in actuality.

Insert drawing designation, if applicable, for each product required. Use these designations on Drawings to identify each product.

        - Exterior Doors, Solid-Core Five-Ply for Opaque Finish <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Performance Grade" Subparagraph below to specify performance grade if referencing ANSI/WDMA I.S. 1A.

          - Performance Grade: ANSI/WDMA I.S. 1A [Extra Heavy Duty] [Heavy Duty] [as indicated on Drawings].

Retain "ANSI/WDMA I.S. 1A Quality Grade" or "Architectural Woodwork Standards Quality Grade" Subparagraph below.

          - ANSI/WDMA I.S. 1A Quality Grade: [Premium] [Custom].

          - Architectural Woodwork Standards Quality Grade: [Premium] [Custom].

First option in "Faces" Subparagraph below is highest quality. Coordinate with requirements of door grade selected.

          - Faces: [MDO] [Any closed-grain hardwood of mill option].

            - Apply MDO to [standard-thickness, closed-grain, hardwood face veneers] [or] [directly to high-density hardboard crossbands].

Retain option in "Exposed Vertical and Top Edges" Subparagraph below if top edges of doors are visible, such as doors in multistory spaces.

          - Exposed Vertical and Top Edges: Any closed-grain hardwood.

          - Core:

Retain one of first four subparagraphs below. Particleboard cores are not generally recommended for exterior doors.

            - ANSI A208.1, [Grade LD-1] [Grade LD-2] particleboard.

            - Glued wood stave.

            - WDMA I.S. 10 structural composite lumber.

In each of first two subparagraphs below, first option is for Extra Heavy Duty performance grade, second option is for Heavy Duty performance grade.

              - Screw Withdrawal, Door Face: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)].

              - Screw Withdrawal, Vertical Door Edge: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)].

            - Either glued wood stave or WDMA I.S. 10 structural composite lumber.

          - Construction: Five plies, hot-pressed, bonded (vertical and horizontal edging is bonded to core), with entire unit abrasive planed before veneering.

          - Adhesives: Type I in accordance with WDMA T.M. 6.

Insert drawing designation, if applicable, for each product required. Use these designations on Drawings to identify each product.

        - Interior Doors, Solid-Core Five-Ply for Opaque Finish <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Performance Grade" or "Performance Grade by Location" Subparagraph below to specify performance grade if referencing ANSI/WDMA I.S. 1A.

          - Performance Grade: ANSI/WDMA I.S. 1A [Extra Heavy Duty] [Heavy Duty] [Standard Duty] [as indicated on Drawings].

          - Performance Grade by Location:

            - ANSI/WDMA I.S. 1A Extra Heavy Duty: [Classrooms] [public toilets] [janitor's closets] [assembly spaces] [exits] [and] [patient rooms] <Insert locations> [and where indicated on Drawings].

            - ANSI/WDMA I.S. 1A Standard Duty: [Closets (not including janitor's closets)] [and] [private toilets] <Insert locations> [and where indicated on Drawings].

Retain "ANSI/WDMA I.S. 1A Quality Grade" or "Architectural Woodwork Standards Quality Grade" Subparagraph below.

          - ANSI/WDMA I.S. 1A Quality Grade: [Premium] [Custom].

          - Architectural Woodwork Standards Quality Grade: [Premium] [Custom].

First option in "Faces" Subparagraph below is highest quality; last is most economical. Coordinate with requirements of door grade selected.

          - Faces: [MDO] [Any closed-grain hardwood of mill option] [Hardboard or MDF].

            - Apply MDO to [standard-thickness, closed-grain, hardwood face veneers] [or] [directly to high-density hardboard crossbands].

            - Hardboard Faces: ANSI A135.4, Class 1 (tempered) or Class 2 (standard).

            - MDF Faces: ANSI A208.2, Grade 150 or Grade 160.

Retain option in "Exposed Vertical and Top Edges" Subparagraph below if top edges of doors are visible, such as doors in multistory spaces.

          - Exposed Vertical and Top Edges: Any closed-grain hardwood.

            - Fire-Rated Single Doors: Provide edge construction with intumescent seals concealed by outer stile. Comply with specified requirements for exposed vertical edges.

            - Fire-Rated Pairs of Doors:

Retain one of first two subparagraphs below. Retain first subparagraph if steel edges and astragals are unacceptable. Coordinate availability and ratings with manufacturers. Retain second subparagraph if steel edges and astragals are acceptable.

              - Provide fire-retardant stiles that are listed and labeled for applications indicated without formed-steel edges and astragals. Provide stiles with concealed intumescent seals. Comply with specified requirements for exposed edges.

              - Provide formed-steel edges and astragals with intumescent seals.

                - Finish steel edges and astragals with baked enamel[ same color as doors].

Retain last subparagraph above or first subparagraph below; delete option above if edges and astragals are field painted.

                - Finish steel edges and astragals to match door hardware (locksets or exit devices).

            - Mineral-Core Doors: At hinge stiles, provide laminated-edge construction with improved screw-holding capability and split resistance. Comply with specified requirements for exposed edges.

Requirements in "Screw-Holding Capability" Subparagraph below are from ANSI/WDMA I.S. 1A. Options are performance duty levels for Extra Heavy Duty, Heavy Duty, and Standard Duty, respectively. Before retaining, verify that products comply with requirement selected.

              - Screw-Holding Capability: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)] in accordance with WDMA T.M. 10.

          - Core for Non-Fire-Rated Doors:

Retain one or more of first four subparagraphs below.

            - ANSI A208.1, [Grade LD-1] [Grade LD-2] particleboard.

Consider deleting "Blocking" Subparagraph below. Some door manufacturers contend that blocking weakens particleboard-core doors and is not required. If retaining subparagraph, retain one of two options.

              - Blocking: Provide wood blocking in particleboard-core doors as [needed to eliminate through-bolting hardware.] [follows:]

If retaining "Blocking" Subparagraph and second option above, retain first three subparagraphs below for blocking required.

                - 5-inch (125-mm) top-rail blocking, in doors indicated to have closers.

                - 5-inch (125-mm) bottom-rail blocking, in exterior doors and doors indicated to have kick, mop, or armor plates.

                - 5-inch (125-mm) midrail blocking, in doors indicated to have exit devices.

Usually delete requirement for midrail blocking in last subparagraph above and retain first subparagraph below.

              - Provide doors with [glued-wood-stave] [or] [WDMA I.S. 10 structural-composite-lumber] cores instead of particleboard cores for doors scheduled to receive exit devices in [Section 087100 "Door Hardware."] [Section 087111 "Door Hardware (Descriptive Specification."]

            - Glued wood stave.

            - WDMA I.S. 10 structural composite lumber.

In each of first two subparagraphs below, first option is for Extra Heavy Duty performance grade, second option is for Heavy Duty performance grade.

              - Screw Withdrawal, Door Face: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)].

              - Screw Withdrawal, Vertical Door Edge: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)].

            - Either glued wood stave or WDMA I.S. 10 structural composite lumber.

          - Core for Fire-Rated Doors: As required to achieve fire-protection rating indicated on Drawings.

            - Blocking for Mineral-Core Doors: Provide composite blocking with improved screw-holding capability approved for use in doors of fire-protection ratings indicated on Drawings as [needed to eliminate through-bolting hardware.] [follows:]

Retain "Blocking for Mineral-Core Doors" Subparagraph above and first four subparagraphs below only after verifying availability for fire-protection rating required. Delete first four subparagraphs below if retaining first option above.

              - 5-inch (125-mm) top-rail blocking.

              - 5-inch (125-mm) bottom-rail blocking, in doors indicated to have protection plates.

              - 5-inch (125-mm) midrail blocking, in doors indicated to have armor plates.

              - [4-1/2-by-10-inch (114-by-250-mm) lock blocks] [5-inch (125-mm) midrail blocking], in doors indicated to have exit devices.

          - Construction: Five plies, hot-pressed bonded (vertical and horizontal edging is bonded to core), with entire unit abrasive planed before veneering.

      - SOLID-CORE SEVEN-PLY FLUSH WOOD VENEER-FACED DOORS AND TRANSOM PANELS FOR TRANSPARENT FINISH

Retain this article for traditional seven-ply flush wood doors and doors with two-ply faces (skins), currently marketed by some manufacturers as five-ply doors, even though they are seven-ply doors in actuality.

Insert drawing designation, if applicable, for each product required. Use these designations on Drawings to identify each product.

        - Exterior Doors, Seven-Ply Veneer-Faced <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

WDMA indicates that its standard is not intended for exterior doors. If exterior flush wood doors are required and ANSI/WDMA I.S. 1A is referenced, usually retain first option in "Performance Grade" Subparagraph below.

          - Performance Grade: ANSI/WDMA I.S. 1A [Extra Heavy Duty] [Heavy Duty] [as indicated on Drawings].

Retain "ANSI/WDMA I.S. 1A Quality Grade" or "Architectural Woodwork Standards Quality Grade" Subparagraph below.

          - ANSI/WDMA I.S. 1A Quality Grade: [Premium] [Custom].

          - Architectural Woodwork Standards Quality Grade: [Premium] [Custom].

Retain first option in "Faces" Subparagraph below for traditional seven-ply wood doors. Retain second option for seven-ply doors being marketed as five-ply doors.

          - Faces: [Single-ply wood veneer not less than 1/50 inch (0.508 mm) thick] [or] [two-ply wood panel with wood veneer not less than 1/50 inch (0.508 mm) thick].

Options in "Species" Subparagraph below are examples only; revise or insert another species.

            - Species: [Anigre] [Select white ash] [Figured select white ash] [Select white birch] [Select red birch] [Cherry] [Select red gum] [Figured select red gum] [Select white maple] [Red oak] [White oak] [Persimmon] [Sapele] [Sycamore] [Walnut] <Insert species>.

First option in "Cut" Subparagraph below applies only to oak.

            - Cut: [Rotary cut] [Plain sliced (flat sliced)] [Quarter sliced] [Rift cut].

            - Match between Veneer Leaves: [Book] [Slip] [Random] match.

In "Assembly of Veneer Leaves on Door Faces" Subparagraph below, first option is standard for Premium-grade doors. Third option is standard for Custom-grade doors.

            - Assembly of Veneer Leaves on Door Faces: [Center-balance] [Balance] [Running] match.

            - Pair and Set Match: Provide for doors hung in same opening[ or separated only by mullions].

Retain first option in "Exposed Vertical and Top Edges" Subparagraph below if top edges of doors are visible, such as doors in multistory spaces. Retain one of four remaining options; last two require factory prefitting.

          - Exposed Vertical and Top Edges: [Same species as faces or a compatible species - Architectural Woodwork Standards edge Type A] [Same species as faces - Architectural Woodwork Standards edge Type A] [Applied wood-veneer edges of same species as faces and covering edges of faces - Architectural Woodwork Standards edge Type B] [Applied wood edges of same species as faces and covering edges of crossbands - Architectural Woodwork Standards edge Type D].

          - Core:

Retain one of first four subparagraphs below. Particleboard cores are not generally recommended for exterior doors.

            - ANSI A208.1, [Grade LD-1] [Grade LD-2] particleboard.

            - Glued wood stave.

            - WDMA I.S. 10 structural composite lumber.

In each of first two subparagraphs below, first option is for Extra Heavy Duty performance grade, second option is for Heavy Duty performance grade.

              - Screw Withdrawal, Door Face: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)].

              - Screw Withdrawal, Vertical Door Edge: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)].

            - Either glued wood stave or WDMA I.S. 10 structural composite lumber.

Retain one of first two options in "Construction" Subparagraph below. First option below applies to traditional five-ply doors. Third option applies to traditional seven-ply doors and seven-ply doors with two-ply faces, being marketed as five-ply doors.

          - Construction: Seven plies, [hot-pressed] [or] [cold-pressed] bonded (vertical and horizontal edging is bonded to core), with entire unit abrasive planed before veneering.

          - Adhesives: Type I in accordance with WDMA T.M. 6.

Insert drawing designation, if applicable, for each product required. Use these designations on Drawings to identify each product.

        - Interior Doors, Seven-Ply Veneer-Faced <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Performance Grade" or "Performance Grade by Location" Subparagraph below to specify performance grade if referencing ANSI/WDMA I.S. 1A.

          - Performance Grade: ANSI/WDMA I.S. 1A [Extra Heavy Duty] [Heavy Duty] [Standard Duty] [as indicated on Drawings].

          - Performance Grade by Location:

            - ANSI/WDMA I.S. 1A Extra Heavy Duty: [Classrooms] [public toilets] [janitor's closets] [assembly spaces] [exits] [and] [patient rooms] <Insert locations> [and where indicated on Drawings].

            - ANSI/WDMA I.S. 1A Standard Duty: [Closets (not including janitor's closets)] [and] [private toilets] <Insert locations> [and where indicated on Drawings].

Retain "ANSI/WDMA I.S. 1A Quality Grade" or "Architectural Woodwork Standards Quality Grade" Subparagraph below.

          - ANSI/WDMA I.S. 1A Quality Grade: [Premium] [Custom].

          - Architectural Woodwork Standards Quality Grade: [Premium] [Custom].

Retain first option in "Faces" Subparagraph below for traditional five-ply wood doors. Retain second option for seven-ply door being marketed as a five-ply door.

          - Faces: [Single-ply wood veneer not less than 1/50 inch (0.508 mm) thick] [or] [two-ply wood panel with wood veneer not less than 1/50 inch (0.508 mm) thick].

Options in "Species" Subparagraph below are examples only; revise or insert another species.

            - Species: [Anigre] [Select white ash] [Figured select white ash] [Select white birch] [Select red birch] [Cherry] [Select red gum] [Figured select red gum] [Select white maple] [Red oak] [White oak] [Persimmon] [Sapele] [Sycamore] [Walnut] <Insert species>.

First option in "Cut" Subparagraph below applies only to oak.

            - Cut: [Rotary cut] [Plain sliced (flat sliced)] [Quarter sliced] [Rift cut].

            - Match between Veneer Leaves: [Book] [Slip] [Random] match.

In "Assembly of Veneer Leaves on Door Faces" Subparagraph below, first option is standard for Premium-grade doors. Third option is standard for Custom-grade doors.

            - Assembly of Veneer Leaves on Door Faces: [Center-balance] [Balance] [Running] match.

            - Pair and Set Match: Provide for doors hung in same opening[ or separated only by mullions].

            - Room Match:

Retain one of first two subparagraphs below only for highest-quality work with Premium-grade doors.

              - Match door faces within each separate room or area of building. Corridor-door faces do not need to match where they are separated by [10 feet (3 m)] [20 feet (6 m)] <Insert dimension> or more.

First subparagraph below is based on requirement for WI Premium-grade doors.

              - Provide door faces of compatible color and grain within each separate room or area of building.

Before retaining "Transom Match" Subparagraph below, verify availability of veneers for selected matching; usually retain first option. See "Referenced Standards" Article in the Evaluations.

            - Transom Match: [Continuous match] [End match] [As indicated on Drawings].

            - Blueprint Match: Where indicated, provide doors with faces produced from same flitches as adjacent wood paneling and arranged to provide blueprint match with wood paneling. Comply with requirements in Section 064216 "Flush Wood Paneling."

Retain first option in "Exposed Vertical and Top Edges" Subparagraph below if top edges of doors are visible, such as doors in multistory spaces. Retain one of four remaining options; last two require factory prefitting.

          - Exposed Vertical and Top Edges: [Same species as faces or a compatible species - Architectural Woodwork Standards edge Type A] [Same species as faces - Architectural Woodwork Standards edge Type A] [Applied wood-veneer edges of same species as faces and covering edges of faces - Architectural Woodwork Standards edge Type B] [Applied wood edges of same species as faces and covering edges of crossbands - Architectural Woodwork Standards edge Type D].

            - Fire-Rated Single Doors: Provide edge construction with intumescent seals concealed by outer stile. Comply with specified requirements for exposed vertical edges.

            - Fire-Rated Pairs of Doors:

Retain one of first two subparagraphs below. Retain first subparagraph if steel edges and astragals are unacceptable. Coordinate availability and ratings with manufacturers. Retain second subparagraph if steel edges and astragals are acceptable.

              - Provide fire-retardant stiles that are listed and labeled for applications indicated without formed-steel edges and astragals. Provide stiles with concealed intumescent seals. Comply with specified requirements for exposed edges.

              - Provide formed-steel edges and astragals with intumescent seals.

                - Finish steel edges and astragals with baked enamel[ same color as doors].

Retain last subparagraph above or first subparagraph below; delete option above if edges and astragals are field painted.

                - Finish steel edges and astragals to match door hardware (locksets or exit devices).

            - Mineral-Core Doors: At hinge stiles, provide laminated-edge construction with improved screw-holding capability and split resistance. Comply with specified requirements for exposed edges.

Requirements in "Screw-Holding Capability" Subparagraph below are from ANSI/WDMA I.S. 1A. Options are performance duty levels for Extra Heavy Duty, Heavy Duty, and Standard Duty, respectively. Before retaining, verify that products comply with requirement selected.

              - Screw-Holding Capability: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)] in accordance with WDMA T.M. 10.

Retain one of first four subparagraphs below.

          - Core for non-fire-rated doors, ANSI A208.1, [Grade LD-1] [Grade LD-2] particleboard.

Consider deleting "Blocking" Subparagraph below. Some door manufacturers contend that blocking weakens particleboard-core doors and is not required. If retaining subparagraph, retain one of two options.

            - Blocking: Provide wood blocking in particleboard-core doors as [needed to eliminate through-bolting hardware.] [follows:]

If retaining "Blocking" Subparagraph and second option above, retain first three subparagraphs below for blocking required.

              - 5-inch (125-mm) top-rail blocking, in doors indicated to have closers.

              - 5-inch (125-mm) bottom-rail blocking, in exterior doors and doors indicated to have kick, mop, or armor plates.

              - 5-inch (125-mm) midrail blocking, in doors indicated to have exit devices.

Usually delete requirement for midrail blocking in last subparagraph above and retain first subparagraph below.

            - Provide doors with [glued-wood-stave] [or] [WDMA I.S. 10 structural-composite-lumber] cores instead of particleboard cores for doors scheduled to receive exit devices in [Section 087100 "Door Hardware."] [Section 087111 "Door Hardware (Descriptive Specification."]

          - Core for non-fire-rated doors, glued wood stave.

          - Core for non-fire-rated doors, WDMA I.S. 10 structural composite lumber.

In each of first two subparagraphs below, first option is for Extra Heavy Duty performance grade, second option is for Heavy Duty performance grade.

            - Screw Withdrawal, Door Face: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)].

            - Screw Withdrawal, Vertical Door Edge: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)].

          - Core for non-fire-rated doors, either glued wood stave or WDMA I.S. 10 structural composite lumber.

          - Core for fire-rated doors, as required to achieve fire-protection rating indicated on Drawings.

            - Blocking for Mineral-Core Doors: Provide composite blocking with improved screw-holding capability approved for use in doors of fire-protection ratings indicated on Drawings as [needed to eliminate through-bolting hardware.] [follows:]

Retain "Blocking for Mineral-Core Doors" Subparagraph above and first four subparagraphs below only after verifying availability for fire-protection rating required. Delete first four subparagraphs below if retaining first option above.

              - 5-inch (125-mm) top-rail blocking.

              - 5-inch (125-mm) bottom-rail blocking, in doors indicated to have protection plates.

              - 5-inch (125-mm) midrail blocking, in doors indicated to have armor plates.

              - [4-1/2-by-10-inch (114-by-250-mm) lock blocks] [5-inch (125-mm) midrail blocking], in doors indicated to have exit devices.

          - Construction: Seven plies, [hot-pressed] [or] [cold-pressed], bonded or unbonded.

      - SOLID-CORE SEVEN-PLY FLUSH WOOD DOORS AND TRANSOM PANELS FOR OPAQUE FINISH

Insert drawing designation, if applicable, for each product required. Use these designations on Drawings to identify each product.

        - Exterior Doors, Seven-Ply for Opaque Finish <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Performance Grade" Subparagraph below to specify performance grade if referencing ANSI/WDMA I.S. 1A.

          - Performance Grade: ANSI/WDMA I.S. 1A [Extra Heavy Duty] [Heavy Duty] [as indicated on Drawings].

Retain "ANSI/WDMA I.S. 1A Quality Grade" or "Architectural Woodwork Standards Quality Grade" Subparagraph below.

          - ANSI/WDMA I.S. 1A Quality Grade: [Premium] [Custom].

          - Architectural Woodwork Standards Quality Grade: [Premium] [Custom].

First option in "Faces" Subparagraph below is highest quality. Coordinate with requirements of door grade selected.

          - Faces: [MDO] [Any closed-grain hardwood of mill option].

            - Apply MDO to [standard-thickness, closed-grain, hardwood face veneers] [or] [directly to high-density hardboard crossbands].

Retain option in "Exposed Vertical and Top Edges" Subparagraph below if top edges of doors are visible, such as doors in multistory spaces.

          - Exposed Vertical and Top Edges: Any closed-grain hardwood.

          - Core:

Retain one of first four subparagraphs below. Particleboard cores are not generally recommended for exterior doors.

            - ANSI A208.1, [Grade LD-1] [Grade LD-2] particleboard.

            - Glued wood stave.

            - WDMA I.S. 10 structural composite lumber.

In each of first two subparagraphs below, first option is for Extra Heavy Duty performance grade, second option is for Heavy Duty performance grade.

              - Screw Withdrawal, Door Face: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)].

              - Screw Withdrawal, Vertical Door Edge: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)].

            - Either glued wood stave or WDMA I.S. 10 structural composite lumber.

Retain first two options in "Construction" Subparagraph below. First option below applies to traditional five-ply doors. Third option applies to traditional seven-ply doors and seven-ply doors with two-ply faces, being marketed as five-ply doors.

          - Construction: Seven plies, [hot-pressed] [or] [cold-pressed], bonded (vertical and horizontal edging is bonded to core), with entire unit abrasive planed before veneering.

          - Adhesives: Type I in accordance with WDMA T.M. 6.

Insert drawing designation, if applicable, for each product required. Use these designations on Drawings to identify each product.

        - Interior Doors, Seven-Ply for Opaque Finish <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Performance Grade" or "Performance Grade by Location" Subparagraph below to specify performance grade if referencing ANSI/WDMA I.S. 1A.

          - Performance Grade: ANSI/WDMA I.S. 1A [Extra Heavy Duty] [Heavy Duty] [Standard Duty] [as indicated on Drawings].

          - Performance Grade by Location:

            - ANSI/WDMA I.S. 1A Extra Heavy Duty: [Classrooms] [public toilets] [janitor's closets] [assembly spaces] [exits] [and] [patient rooms] <Insert locations> [and where indicated on Drawings].

            - ANSI/WDMA I.S. 1A Standard Duty: [Closets (not including janitor's closets)] [and] [private toilets] <Insert locations> [and where indicated on Drawings].

Retain "ANSI/WDMA I.S. 1A Quality Grade" or "Architectural Woodwork Standards Quality Grade" Subparagraph below.

          - ANSI/WDMA I.S. 1A Quality Grade: [Premium] [Custom].

          - Architectural Woodwork Standards Quality Grade: [Premium] [Custom].

First option in "Faces" Subparagraph below is highest quality; last is most economical. Coordinate with requirements of door grade selected.

          - Faces: [MDO] [Any closed-grain hardwood of mill option] [Hardboard or MDF].

            - Apply MDO to [standard-thickness, closed-grain, hardwood face veneers] [or] [directly to high-density hardboard crossbands].

            - Hardboard Faces: ANSI A135.4, Class 1 (tempered) or Class 2 (standard).

            - MDF Faces: ANSI A208.2, Grade 150 or Grade 160.

Retain option in "Exposed Vertical and Top Edges" Subparagraph below if top edges of doors are visible, such as doors in multistory spaces.

          - Exposed Vertical and Top Edges: Any closed-grain hardwood.

            - Fire-Rated Single Doors: Provide edge construction with intumescent seals concealed by outer stile. Comply with specified requirements for exposed vertical edges.

            - Fire-Rated Pairs of Doors:

Retain one of first two subparagraphs below. Retain first subparagraph if steel edges and astragals are unacceptable. Coordinate availability and ratings with manufacturers. Retain second subparagraph if steel edges and astragals are acceptable.

              - Provide fire-retardant stiles that are listed and labeled for applications indicated without formed-steel edges and astragals. Provide stiles with concealed intumescent seals. Comply with specified requirements for exposed edges.

              - Provide formed-steel edges and astragals with intumescent seals.

                - Finish steel edges and astragals with baked enamel[ same color as doors].

Retain last subparagraph above or first subparagraph below; delete option above if edges and astragals are field painted.

                - Finish steel edges and astragals to match door hardware (locksets or exit devices).

            - Mineral Core Doors: At hinge stiles, provide laminated-edge construction with improved screw-holding capability and split resistance. Comply with specified requirements for exposed edges.

Requirements in "Screw-Holding Capability" Subparagraph below are from ANSI/WDMA I.S. 1A. Options are performance duty levels for Extra Heavy Duty, Heavy Duty, and Standard Duty, respectively. Before retaining, verify that products comply with requirement selected.

              - Screw-Holding Capability: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)] in accordance with WDMA T.M. 10.

Retain one of first four subparagraphs below.

          - Core for non-fire-rated doors, ANSI A208.1, [Grade LD-1] [Grade LD-2] particleboard.

Consider deleting "Blocking" Subparagraph below. Some door manufacturers contend that blocking weakens particleboard-core doors and is not required. If retaining subparagraph, retain one of two options.

            - Blocking: Provide wood blocking in particleboard-core doors as [needed to eliminate through-bolting hardware.] [follows:]

If retaining "Blocking" Subparagraph and second option above, retain first three subparagraphs below for blocking required.

              - 5-inch (125-mm) top-rail blocking, in doors indicated to have closers.

              - 5-inch (125-mm) bottom-rail blocking, in exterior doors and doors indicated to have kick, mop, or armor plates.

              - 5-inch (125-mm) midrail blocking, in doors indicated to have exit devices.

Usually delete requirement for midrail blocking in last subparagraph above and retain first subparagraph below.

            - Provide doors with [glued-wood-stave] [or] [WDMA I.S. 10 structural-composite-lumber] cores instead of particleboard cores for doors scheduled to receive exit devices in [Section 087100 "Door Hardware."] [Section 087111 "Door Hardware (Descriptive Specification."]

          - Core for non-fire-rated doors, glued wood stave.

          - Core for non-fire-rated doors, WDMA I.S. 10 structural composite lumber.

In each of first two subparagraphs below, first option is for Extra Heavy Duty performance grade, second option is for Heavy Duty performance grade.

            - Screw Withdrawal, Door Face: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)].

            - Screw Withdrawal, Vertical Door Edge: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)].

          - Core for non-fire-rated doors, either glued wood stave or WDMA I.S. 10 structural composite lumber.

          - Core for fire-rated doors, as required to achieve fire-protection rating indicated on Drawings.

            - Blocking for Mineral-Core Doors: Provide composite blocking with improved screw-holding capability approved for use in doors of fire-protection ratings indicated on Drawings as [needed to eliminate through-bolting hardware.] [follows:]

Retain "Blocking for Mineral-Core Doors" Subparagraph above and first four subparagraphs below only after verifying availability for fire-protection rating required. Delete first four subparagraphs below if retaining first option above.

              - 5-inch (125-mm) top-rail blocking.

              - 5-inch (125-mm) bottom-rail blocking, in doors indicated to have protection plates.

              - 5-inch (125-mm) midrail blocking, in doors indicated to have armor plates.

              - [4-1/2-by-10-inch (114-by-250-mm) lock blocks] [5-inch (125-mm) midrail blocking], in doors indicated to have exit devices.

In "Construction" Subparagraph below, coordinate construction type with core material. Glued-wood-stave core is available only with bonded construction, and nonglued-wood-stave core is available only with nonbonded construction.

          - Construction: Seven plies, [hot-pressed] [or] [cold-pressed], bonded or unbonded.

      - SOLID-CORE FLUSH WOOD DOORS AND TRANSOM PANELS WITH PLASTIC-LAMINATE FACES

Insert drawing designation, if applicable, for each product required. Use these designations on Drawings to identify each product.

        - Interior Doors, Solid Core with Plastic-Laminate Faces <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Performance Grade" or "Performance Grade by Location" Subparagraph below to specify performance grade if referencing ANSI/WDMA I.S. 1A.

          - Performance Grade: ANSI/WDMA I.S. 1A [Extra Heavy Duty] [Heavy Duty] [Standard Duty] [as indicated on Drawings].

          - Performance Grade by Location:

            - ANSI/WDMA I.S. 1A Extra Heavy Duty: [Classrooms] [public toilets] [janitor's closets] [assembly spaces] [exits] [and] [patient rooms] <Insert locations> [and where indicated on Drawings].

            - ANSI/WDMA I.S. 1A Standard Duty: [Closets (not including janitor's closets)] [and] [private toilets] <Insert locations> [and where indicated on Drawings].

Retain "ANSI/WDMA I.S. 1A Quality Grade" or "Architectural Woodwork Standards Quality Grade" Subparagraph below.

          - ANSI/WDMA I.S. 1A Quality Grade: [Premium] [Custom].

          - Architectural Woodwork Standards Quality Grade: [Premium] [Custom].

Retain one of two options in "Plastic-Laminate Faces" Subparagraph below, usually the first one. First is typical 0.048-inch- (1.2-mm-) thick material; second is 0.118-inch- (3.0-mm-) thick material made specifically for doors and is expensive. Before specifying second option, verify availability with manufacturers.

          - Plastic-Laminate Faces: High-pressure decorative laminates complying with ISO 4586-3, [Grade HGS] [Grade HSH].

Revise "Colors, Patterns, and Finishes" Subparagraph below to indicate color, pattern, and finish if preselected.

          - Colors, Patterns, and Finishes: [As indicated] [As selected by Architect from laminate manufacturer's full range of products].

Retain first option in "Exposed Vertical and Top Edges" Subparagraph below if top edges of doors are visible, such as doors in multistory spaces. Retain one of four remaining options; last two require factory prefitting. Impact-resistant polymer edging is standard for some manufacturers.

          - Exposed Vertical and Top Edges: [Hardwood edges for staining to match faces] [Hardwood edges for painting] [Plastic laminate that matches faces, applied before faces] [or] [impact-resistant polymer edging, applied after faces].

            - Fire-Rated Single Doors: Provide edge construction with intumescent seals concealed by outer stile. Comply with specified requirements for exposed vertical edges.

            - Fire-Rated Pairs of Doors:

Retain one of first two subparagraphs below. Retain first subparagraph if steel edges and astragals are unacceptable. Coordinate availability and ratings with manufacturers. Retain second subparagraph if steel edges and astragals are acceptable.

              - Provide fire-retardant stiles that are listed and labeled for applications indicated without formed-steel edges and astragals. Provide stiles with concealed intumescent seals. Comply with specified requirements for exposed edges.

              - Provide formed-steel edges and astragals with intumescent seals.

                - Finish steel edges and astragals with baked enamel[ same color as doors].

Retain last subparagraph above or first subparagraph below; delete option above if edges and astragals are field painted.

                - Finish steel edges and astragals to match door hardware (locksets or exit devices).

            - Mineral-Core Doors: At hinge stiles, provide laminated-edge construction with improved screw-holding capability and split resistance. Comply with specified requirements for exposed edges.

Requirements in "Screw-Holding Capability" Subparagraph below are from ANSI/WDMA I.S. 1A. Options are performance duty levels for Extra Heavy Duty, Heavy Duty, and Standard Duty, respectively. Before retaining, verify that products comply with requirement selected.

              - Screw-Holding Capability: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)] in accordance with WDMA T.M. 10.

          - Core for Non-Fire-Rated Doors:

Retain one of first four subparagraphs below.

            - ANSI A208.1, [Grade LD-1] [Grade LD-2] particleboard.

Consider deleting "Blocking" Subparagraph below. Some door manufacturers contend that blocking weakens particleboard-core doors and is not required. If retaining subparagraph, retain one of two options.

              - Blocking: Provide wood blocking in particleboard-core doors as [needed to eliminate through-bolting hardware.] [follows:]

If retaining "Blocking" Subparagraph and second option above, retain first three subparagraphs below for blocking required.

                - 5-inch (125-mm) top-rail blocking, in doors indicated to have closers.

                - 5-inch (125-mm) bottom-rail blocking, in exterior doors and doors indicated to have kick, mop, or armor plates.

                - 5-inch (125-mm) midrail blocking, in doors indicated to have exit devices.

Usually delete requirement for midrail blocking in last subparagraph above and retain first subparagraph below.

              - Provide doors with [glued-wood-stave] [or] [WDMA I.S. 10 structural-composite-lumber] cores instead of particleboard cores for doors scheduled to receive exit devices in [Section 087100 "Door Hardware."] [Section 087111 "Door Hardware (Descriptive Specification."]

            - Glued wood stave.

            - WDMA I.S. 10 structural composite lumber.

In each of first two subparagraphs below, first option is for Extra Heavy Duty performance grade, second option is for Heavy Duty performance grade.

              - Screw Withdrawal, Door Face: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)].

              - Screw Withdrawal, Vertical Door Edge: [550 lbf (2440 N)] [475 lbf (2110 N)] [400 lbf (1780 N)].

            - Either glued wood stave or WDMA I.S. 10 structural composite lumber.

          - Core for Fire-Rated Doors: As required to achieve fire-protection rating indicated on Drawings.

            - Blocking for Mineral-Core Doors: Provide composite blocking with improved screw-holding capability approved for use in doors of fire-protection ratings indicated on Drawings as [needed to eliminate through-bolting hardware.] [follows:]

Retain "Blocking for Mineral-Core Doors" Subparagraph above and first four subparagraphs below only after verifying availability for fire-protection rating required. Delete first four subparagraphs below if retaining first option above.

              - 5-inch (125-mm) top-rail blocking.

              - 5-inch (125-mm) bottom-rail blocking, in doors indicated to have protection plates.

              - 5-inch (125-mm) midrail blocking, in doors indicated to have armor plates.

              - [4-1/2-by-10-inch (114-by-250-mm) lock blocks] [5-inch (125-mm) midrail blocking], in doors indicated to have exit devices.

          - Construction:

Retain one of two subparagraphs below. Glued-wood-stave core is only allowed with five-ply construction. See the Evaluations.

            - Three plies, [hot-pressed] [or] [cold-pressed] bonded (vertical and horizontal edging is bonded to core), with entire unit abrasive planed before faces are applied.

            - Five plies, [hot-pressed] [or] [cold-pressed] bonded (vertical and horizontal edging is bonded to core), with entire unit abrasive planed before faces and crossbands are applied.

      - HOLLOW-CORE FLUSH WOOD VENEER-FACED DOORS FOR TRANSPARENT FINISH

Insert drawing designation, if applicable, for each product required. Use these designations on Drawings to identify each product.

        - Interior Doors, Hollow-Core Veneer Faced <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Performance Grade: ANSI/WDMA I.S. 1A Standard Duty.

Retain "ANSI/WDMA I.S. 1A Quality Grade" or "Architectural Woodwork Standards Quality Grade" Subparagraph below.

          - ANSI/WDMA I.S. 1A Quality Grade: [Premium] [Custom].

          - Architectural Woodwork Standards Quality Grade: [Premium] [Custom].

Options in "Species" Subparagraph below are examples only; revise or insert another species.

          - Species: [Anigre] [Select white ash] [Figured select white ash] [Select white birch] [Select red birch] [Cherry] [Select red gum] [Figured select red gum] [Select white maple] [Red oak] [White oak] [Persimmon] [Sapele] [Sycamore] [Walnut] <Insert species>.

First option in "Cut" Subparagraph below applies only to oak.

          - Cut: [Rotary cut] [Plain sliced (flat sliced)] [Quarter sliced] [Rift cut].

          - Match between Veneer Leaves: [Book] [Slip] [Random] match.

In "Assembly of Veneer Leaves on Door Faces" Subparagraph below, first option is standard for Premium-grade doors. Third option is standard for Custom-grade doors.

          - Assembly of Veneer Leaves on Door Faces: [Center-balance] [Balance] [Running] match.

          - Pair and Set Match: Provide for doors hung in same opening[ or separated only by mullions].

Retain first option in "Exposed Vertical and Top Edges" Subparagraph below if top edges of doors are visible, such as doors in multistory spaces. Retain one of four remaining options; last two require factory prefitting.

          - Exposed Vertical and Top Edges: [Same species as faces or a compatible species - Architectural Woodwork Standards edge Type A] [Same species as faces - Architectural Woodwork Standards edge Type A] [Applied wood-veneer edges of same species as faces and covering edges of faces - Architectural Woodwork Standards edge Type B] [Applied wood edges of same species as faces and covering edges of crossbands - Architectural Woodwork Standards edge Type D].

Retain "Construction" Subparagraph below for ANSI/WDMA I.S. 1A. An institutional core requires 6- to 12-inch (152- to 300-mm) top and bottom rail blocking; a standard core requires only 1-1/8-inch (29-mm) rails.

          - Construction: [Institutional] [Standard] hollow core.

          - Blocking: Provide wood blocking with minimum dimensions as follows:

            - 5-by-18-inch (125-by-460-mm) lock blocks[ at both stiles].

Blocking in first subparagraph above is usually standard; three subparagraphs below are optional features. Delete blocking not required.

            - 5-inch (125-mm) top-[ and bottom-]rail blocking.

            - 10-inch (250-mm)[ top- and] bottom-rail blocking.

            - 2-1/2-inch (64-mm) midrail blocking.

      - HOLLOW-CORE FLUSH WOOD DOORS FOR OPAQUE FINISH

Insert drawing designation, if applicable, for each product required. Use these designations on Drawings to identify each product.

        - Interior Doors, Hollow Core for Opaque Finish <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Performance Grade: WDMA ANSI/I.S. 1A Standard Duty.

Retain "ANSI/WDMA I.S. 1A Quality Grade" or "Architectural Woodwork Standards Quality Grade" Subparagraph below.

          - ANSI/WDMA I.S. 1A Quality Grade: [Premium] [Custom].

          - Architectural Woodwork Standards Quality Grade: [Premium] [Custom].

First option in "Faces" Subparagraph below is higher quality than second option. Coordinate with requirements of door grade selected.

          - Faces: [Any closed-grain hardwood of mill option] [Hardboard or MDF].

            - Hardboard Faces: ANSI A135.4, Class 1 (tempered) or Class 2 (standard).

            - MDF Faces: ANSI A208.2, Grade 150 or Grade 160.

Retain option in "Exposed Vertical and Top Edges" Subparagraph below if top edges of doors are visible, such as doors in multistory spaces.

          - Exposed Vertical and Top Edges: Any closed-grain hardwood.

Retain "Construction" Subparagraph below for ANSI/WDMA I.S. 1A. An institutional core requires 6- to 12-inch (152- to 302-mm) top and bottom rail blocking; a standard core requires only 1-1/8-inch (29-mm) rails.

          - Construction: [Institutional] [Standard] hollow core.

          - Blocking: Provide wood blocking with minimum dimensions as follows:

            - 5-by-18-inch (125-by-460-mm) lock blocks[ at both stiles].

Blocking in first subparagraph above is usually standard; three subparagraphs below are optional features. Delete blocking not required.

            - 5-inch (125-mm) top-[ and bottom-]rail blocking.

            - 10-inch (250-mm)[ top- and] bottom-rail blocking.

            - 2-1/2-inch (64-mm) midrail blocking.

      - HOLLOW-CORE FLUSH WOOD DOORS WITH PLASTIC-LAMINATE-FACES

Insert drawing designation, if applicable, for each product required. Use these designations on Drawings to identify each product.

        - Interior Doors, Hollow Core with Plastic-Laminate-Faces <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Performance Grade: ANSI/WDMA I.S. 1A Standard Duty.

Retain "ANSI/WDMA I.S. 1A Quality Grade" or "Architectural Woodwork Standards Quality Grade" Subparagraph below.

          - ANSI/WDMA I.S. 1A Quality Grade: [Premium] [Custom].

          - Architectural Woodwork Standards Quality Grade: [Premium] [Custom].

Retain one of two options in "Plastic-Laminate Faces" Subparagraph below, usually the first one. First is typical 0.048-inch- (1.2-mm-) thick material; second is 0.118-inch- (3.0-mm-) thick material made specifically for doors and is expensive. Before specifying second option, verify availability with manufacturers.

          - Plastic-Laminate Faces: High-pressure decorative laminates complying with ISO 4586-3, [Grade HGS] [Grade HSH].

Revise "Colors, Patterns, and Finishes" Subparagraph below to indicate color, pattern, and finish if preselected.

          - Colors, Patterns, and Finishes: [As indicated] [As selected by Architect from laminate manufacturer's full range of products].

Retain first option in "Exposed Vertical and Top Edges" Subparagraph below if top edges of doors are visible, such as doors in multistory spaces. Retain one of four remaining options; last two require factory prefitting.

          - Exposed Vertical and Top Edges: [Hardwood edges for staining to match faces] [Hardwood edges for painting] [Plastic laminate that matches faces, applied before faces] [Impact-resistant polymer edging, applied after faces].

Third option in "Polymer Edging Color" Subparagraph below can be expensive.

            - Polymer Edging Color: [Beige] [Brown] [Same color as faces].

Retain "Construction" Subparagraph below for ANSI/WDMA I.S. 1A. An institutional core requires 6- to 12-inch (152- to 302-mm) top and bottom rail blocking; a standard core requires only 1-1/8-inch (29-mm) rails.

          - Construction: [Institutional] [Standard] hollow core.

          - Blocking: Provide wood blocking with minimum dimensions as follows:

            - 5-by-18-inch (125-by-460-mm) lock blocks[ at both stiles].

Blocking in first subparagraph above is usually standard; three subparagraphs below are optional features. Delete blocking not required.

            - 5-inch (125-mm) top-[ and bottom-]rail blocking.

            - 10-inch (250-mm)[ top- and] bottom-rail blocking.

            - 2-1/2-inch (64-mm) midrail blocking.

      - FIRE-RATED WOOD DOOR FRAMES

        - Interior Fire-Rated Door Frames:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "ANSI/WDMA I.S. 1A Quality Grade" or "Architectural Woodwork Standards Quality Grade" Subparagraph below.

          - ANSI/WDMA I.S. 1A Quality Grade: [Premium] [Custom].

          - Architectural Woodwork Standards Quality Grade: [Premium] [Custom].

Retain "Wood Species and Cut" Subparagraph below if frames and jambs match doors. Otherwise, retain both "Species" and "Cut" subparagraphs below.

          - Wood Species and Cut: Match species and cut indicated for wood doors unless otherwise indicated.

Options in "Species" Subparagraph below are examples only; revise or insert another species.

          - Species: [Anigre] [Select white ash] [Figured select white ash] [Select white birch] [Select red birch] [Cherry] [Select red gum] [Figured select red gum] [Select white maple] [Red oak] [White oak] [Persimmon] [Sapele] [Sycamore] [Walnut] <Insert species>.

First option in "Cut" Subparagraph below applies only to oak.

          - Cut: [Plain sliced/plain sawn] [Quarter cut/quarter sawn] [Rift cut/rift sawn].

Retain one of three options in "Wood Moisture Content" Paragraph below. First range applies to Ontario, Quebec, and most of the United States. Second applies to damp coastal areas of southern United States and Maritime Provinces. Third applies to dry southwestern United States, Alberta, Manitoba, and Saskatchewan. See relative-humidity and moisture-content map in AWI/AWMCA/WI's "Architectural Woodwork Standards." Some locations have microclimates that differ from the surrounding region.

          - Wood Moisture Content: [5 to 10] [8 to 13] [4 to 9] percent.

          - Profile: [T-stop] [Flat] [Single rabbet] [Double rabbet] [As indicated on Drawings].

          - Construction: Solid lumber, fire-retardant particleboard, or fire-retardant medium density fiberboard (MDF) with veneered exposed surfaces and listed and labeled by a testing and inspecting agency acceptable to authorities having jurisdiction, for fire ratings indicated on Drawings.

      - LIGHT FRAMES AND LOUVERS

Retain one or more of "Wood Beads for Light Openings in Wood Doors," "Wood-Veneered Beads for Light Openings in Fire-Rated Doors," and "Metal Frames for Light Openings in Fire-Rated Doors" paragraphs below if light openings are required.

        - Wood Beads for Light Openings in Wood Doors: Provide manufacturer's standard wood beads unless otherwise indicated.

Retain one of three options in "Wood Species" Subparagraph below.

          - Wood Species: [Same species as door faces] [Species compatible with door faces] [Any closed-grain hardwood].

Retain one of five options in "Profile" Subparagraph below, or revise to suit Project.

          - Profile: [Flush rectangular beads] [Recessed tapered beads] [Recessed tapered beads with exposed banding] [Lipped tapered beads] [Manufacturer's standard shape].

Retain subparagraph below if required.

          - At wood-core doors with 20-minute fire-protection ratings, provide wood beads and metal glazing clips approved for such use.

Retain "Wood-Veneered Beads for Light Openings in Fire-Rated Doors" or "Metal Frames for Light Openings in Fire-Rated Doors" Paragraph below if required for doors with fire-protection rating exceeding 20 minutes. See NFPA 80 for requirements.

        - Wood-Veneered Beads for Light Openings in Fire-Rated Doors: Manufacturer's standard wood-veneered noncombustible beads matching veneer species of door faces and approved for use in doors of fire-protection rating indicated on Drawings. Include concealed metal glazing clips where required for opening size and fire-protection rating indicated.

        - Metal Frames for Light Openings in Fire-Rated Doors: Manufacturer's standard frame formed of 0.048-inch- (1.2-mm-) thick, cold-rolled steel sheet; [factory primed for paint] [with baked-enamel- or powder-coated] finish; and approved for use in doors of fire-protection rating indicated on Drawings.

        - Wood Louvers: Door manufacturer's standard solid-wood louvers unless otherwise indicated.

Retain one of three options in "Wood Species" Subparagraph below.

          - Wood Species: [Same species as door faces] [Species compatible with door faces] [Any closed-grain hardwood].

          - Profile: [Flat] [Chevron].

        - Metal Louvers:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Blade Type: [Vision-proof, inverted V] [Vision-proof, inverted Y] [Darkroom-type, double inverted V].

          - Metal and Finish:

Retain one of three subparagraphs below.

            - Hot-dip galvanized steel, 0.040 inch (1.0 mm) thick, [factory primed for paint] [with baked-enamel- or powder-coated] finish.

            - Extruded aluminum with Class II, clear anodic finish, AA-M12C22A31.

            - Extruded aluminum with [light bronze] [medium bronze] [dark bronze] [black], Class II, color anodic finish, AA-M12C22A32/A34.

        - Louvers for Fire-Rated Doors: Metal louvers with fusible link and closing device, listed and labeled for use in doors with fire-protection rating of 1-1/2 hours and less.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Metal and Finish: Hot-dip galvanized steel, 0.040 inch (1.0 mm) thick, [factory primed for paint] [with baked-enamel- or powder-coated] finish.

      - FABRICATION

Typically, retain first paragraph below. Retain paragraph and revise to indicate exceptions if only some doors are required to be factory fitted. Plastic-laminate-edged and factory-finished doors must be factory fitted and machined. Fire-rated and plastic-laminate-faced doors with wood edges should also be factory fitted and machined.

Standard fitting may be inadequate for doors 2-1/2 inches (64 mm) thick or more or for doors exposed to wide changes in humidity and temperature.

        - Factory fit doors to suit frame-opening sizes indicated.

          - Comply with clearance requirements of referenced quality standard for fitting unless otherwise indicated.

          - Comply with NFPA 80 requirements for fire-rated doors.

Typically, retain first paragraph below. Retain paragraph and revise to indicate exceptions if only some doors are required to be factory machined.

        - Factory machine doors for hardware that is not surface applied.

          - Locate hardware to comply with DHI-WDHS-3.

          - Comply with final hardware schedules, door frame Shop Drawings, ANSI/BHMA-156.115-W, and hardware templates.

Retain first subparagraph below for metal frames for wood doors.

          - Coordinate with hardware mortises in metal frames, to verify dimensions and alignment before factory machining.

          - For doors scheduled to receive electrified locksets, provide factory-installed raceway and wiring to accommodate specified hardware.

Retain "Metal Astragals" Subparagraph below with pairs of factory-fitted, fire-rated doors where astragals, etc., are required.

          - Metal Astragals: Factory machine astragals and formed-steel edges for hardware for pairs of fire-rated doors.

Retain "Transom and Side Panels" Paragraph below if applicable. Indicate here or on Drawings if doors and transoms are rabbeted. Verify that transom sizes and attachment methods comply with fire-protection ratings if using fire-rated doors with transoms.

        - Transom and Side Panels:

          - Fabricate matching panels with same construction, exposed surfaces, and finish as specified for associated doors.

          - Finish bottom edges of transoms and top edges of rabbeted doors same as door stiles.

Retain first subparagraph below if applicable, or revise if another method of attachment is required.

          - Fabricate door and transom panels with full-width, solid-lumber[, rabbeted,] meeting rails.

          - Provide factory-installed spring bolts for concealed attachment into jambs of metal door frames.

        - Openings: Factory cut and trim openings through doors.

          - Light Openings: Trim openings with moldings of material and profile indicated.

"Glazing" Subparagraph below is unnecessary if using only metal light frames.

          - Glazing: Factory install glazing in doors indicated to be factory finished. Comply with applicable requirements in Section 088000 "Glazing."

          - Louvers: Factory install louvers in prepared openings.

Retain "Exterior Doors" Paragraph below to provide additional weather resistance at exterior doors.

        - Exterior Doors: Factory treat exterior doors with water repellent after fabrication has been completed but before factory [priming] [finishing].

Retain subparagraph below for outswinging exterior doors. Before retaining, verify availability with manufacturers or delete and include with weather stripping in Section 087100 "Door Hardware" or Section 087111 "Door Hardware (Descriptive Specification)."

          - Flash top of outswinging doors with manufacturer's standard metal flashing.

      - FACTORY PRIMING

Retain this article if field-finished doors are required to be factory primed. Factory fitting is recommended to minimize damage to factory-primed doors.

        - Doors for Opaque Finish: Factory prime faces, all four edges, edges of cutouts, and mortises with one coat of wood primer specified in [Section 099113 "Exterior Painting."] [Section 099123" Interior Painting."]

      - FACTORY FINISHING

Retain this article if factory finishing is required. Factory finishing can be used to help comply with sustainable design requirements, which limit VOC content of paints and coatings used within buildings. Factory finishing also has other advantages. See the Evaluations.

        - Comply with referenced quality standard for factory finishing.

          - Complete fabrication, including fitting doors for openings and machining for hardware that is not surface applied, before finishing.

          - Finish faces, all four edges, edges of cutouts, and mortises.

          - Stains and fillers may be omitted on[ top and] bottom edges, edges of cutouts, and mortises.

Retain one of first three paragraphs below.

        - Factory finish doors.

        - Factory finish doors that are indicated on Drawings to receive transparent finish.

        - Factory finish doors where indicated in schedules or on Drawings as factory finished.

        - Transparent Finish:

Retain "Architectural Woodwork Standards Grade" or "ANSI/WDMA I.S. 1A Grade" Subparagraph below, usually retain same grade for finish as specified for doors.

          - Architectural Woodwork Standards Grade: [Premium] [Custom].

Retain one of first four subparagraphs below, or insert another finish system. Before specifying, verify availability of finishes with manufacturers. Finish systems vary among manufacturers. Most manufacturers offer System-9 as standard. Require Samples for verification.

            - System-5, Varnish, Conversion.

            - System-9, UV Curable, Acrylated Epoxy, Polyester or Urethane.

            - System-10, UV Curable, Water Based.

            - System-11, Polyurethane, Catalyzed.

          - ANSI/WDMA I.S. 1A Grade: [Premium] [Custom].

Retain one of first three subparagraphs below, or insert another finish system. Before specifying, verify availability of finishes with manufacturers. Finish systems vary among manufacturers. Most manufacturers offer TR-8 as standard. Require Samples for verification.

            - TR-4 Conversion Varnish.

            - TR-6 Catalyzed Polyurethane.

            - TR-8 UV Cured Acrylated Polyester/Urethane.

Retain one of three options in "Staining" Subparagraph below.

          - Staining: [Match Architect's sample] [As selected by Architect from manufacturer's full range] [None required].

Retain one of two options in "Sheen" Subparagraph below, or revise to suit Project.

          - Sheen: [Satin] [Semigloss].

        - Opaque Finish:

Retain "Architectural Woodwork Standards Grade" or "ANSI/WDMA I.S. 1A Grade" Subparagraph below, usually retain same grade for finish as specified for doors.

          - Architectural Woodwork Standards Grade: [Premium] [Custom].

Retain one of first four subparagraphs below, or insert another finish system. Before specifying, verify availability of finishes with manufacturers. Finish systems vary among manufacturers.

            - System-5, Varnish, Conversion.

            - System-9, UV Curable, Acrylated Epoxy, Polyester, or Urethane.

            - System-10, UV Curable, Water Based.

            - System-11, Polyurethane, Catalyzed.

          - ANSI/WDMA I.S. 1A Grade: [Premium] [Custom].

Retain one of first two subparagraphs below, or insert another finish system. Before specifying, verify availability of finishes with manufacturers. Finish systems vary among manufacturers.

            - OP-4 Conversion Varnish.

            - OP-6 Catalyzed Polyurethane.

          - Color: [Match Architect's sample] [As selected by Architect from manufacturer's full range].

Retain one of three options in "Sheen" Subparagraph below, or revise to suit Project.

          - Sheen: [Satin] [Semigloss] [Gloss].

- EXECUTION

      - EXAMINATION

        - Examine doors and installed door frames, with Installer present, before hanging doors.

          - Verify that installed frames comply with indicated requirements for type, size, location, and swing characteristics and have been installed with level heads and plumb jambs.

          - Reject doors with defects.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - Hardware: For installation, see [Section 087100 "Door Hardware."] [Section 087111 "Door Hardware (Descriptive Specification)."]

        - Install doors[ and frames] to comply with manufacturer's written instructions and referenced quality standard, and as indicated.

        - Install frames level, plumb, true, and straight.

          - Shim as required with concealed shims. Install level and plumb to a tolerance of 1/8 inch in 96 inches (3.2 mm in 2400 mm).

          - Anchor frames to anchors or blocking built in or directly attached to substrates.

            - Secure with countersunk, concealed fasteners and blind nailing.

            - Use fine finishing nails[ or finishing screws] for exposed fastening, countersunk and filled flush with woodwork.

              - For factory-finished items, use filler matching finish of items being installed.

Retain first subparagraph below for fire-rated doors and frames.

          - Install fire-rated doors and frames in accordance with NFPA 80.

Retain subparagraph below for smoke- and draft-control doors. The IBC requires fire door assemblies to comply with smoke- and draft-control requirements in corridors, smoke barriers, and smoke partitions.

          - Install smoke- and draft-control doors in accordance with NFPA 105.

Retain "Job-Fitted Doors" Paragraph below if all doors are not factory fitted. Factory fitting of fire-rated doors is preferred to job fitting, because of limitations on trimming narrower stiles and rails.

        - Job-Fitted Doors:

          - Align and fit doors in frames with uniform clearances and bevels as indicated below.

            - Do not trim stiles and rails in excess of limits set by manufacturer or permitted for fire-rated doors.

          - Machine doors for hardware.

          - Seal edges of doors, edges of cutouts, and mortises after fitting and machining.

          - Clearances:

Clearances in first three subparagraphs below describe typical prefit clearances; revise to suit office practice and for doors thicker than 1-3/4 inches (44 mm).

            - Provide 1/8 inch (3.2 mm) at heads, jambs, and between pairs of doors.

            - Provide 1/8 inch (3.2 mm) from bottom of door to top of decorative floor finish or covering unless otherwise indicated on Drawings.

            - Where threshold is shown or scheduled, provide 1/4 inch (6.4 mm) from bottom of door to top of threshold unless otherwise indicated.

Retain first subparagraph below for fire-rated doors or if doors are not factory fitted.

            - Comply with NFPA 80 for fire-rated doors.

          - Bevel non-fire-rated doors 1/8 inch in 2 inches (3-1/2 degrees) at lock and hinge edges.

Last subparagraph above is standard bevel; revise to suit Project if required. See the Evaluations. Retain subparagraph below for fire-rated doors or if not factory fitted. Fire-rated doors can be trimmed only to a limited extent, because of narrow stiles and rails.

          - Bevel fire-rated doors 1/8 inch in 2 inches (3-1/2 degrees) at lock edge; trim stiles and rails only to extent permitted by labeling agency.

        - Factory-Fitted Doors: Align in frames for uniform clearance at each edge.

        - Factory-Finished Doors: Restore finish before installation if fitting or machining is required at Project site.

      - FIELD QUALITY CONTROL

Retaining second option in "Inspection Agency" Paragraph is typical. If retaining second option in "Inspection Agency" Paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals."

        - Inspection Agency: [Owner will engage] [Engage] a qualified inspector to perform inspections and to furnish reports to Architect.

        - Inspections:

          - Provide inspection of installed Work through [AWI's Quality Certification Program] [WI's Certified Compliance Program], certifying that wood doors and frames, including installation, comply with requirements of AWI/AWMCA/WI's "Architectural Woodwork Standards" for the specified grade.

          - Fire-Rated Door Inspections: Inspect each fire-rated door in accordance with NFPA 80, Section 5.2.

Retain "Egress Door Inspections" Subparagraph below for projects under NFPA 101, for Assembly, Educational, Day-Care, and Residential Board and Care occupancies.

          - Egress Door Inspections: Inspect each door equipped with panic hardware, each door equipped with fire exit hardware, each door located in an exit enclosure, each electrically controlled egress door, and each door equipped with special locking arrangements in accordance with NFPA 101, Section 7.2.1.15.

        - Repair or remove and replace installations where inspections indicate that they do not comply with specified requirements.

        - Reinspect repaired or replaced installations to determine if replaced or repaired door assembly installations comply with specified requirements.

        - Prepare and submit separate inspection report for each fire-rated door assembly indicating compliance with each item listed in [NFPA 80] [and] [NFPA 101].

      - ADJUSTING

        - Operation: Rehang or replace doors that do not swing or operate freely.

        - Finished Doors: Replace doors that are damaged or that do not comply with requirements. Doors may be repaired or refinished if Work complies with requirements and shows no evidence of repair or refinishing.

END OF SECTION 081416