Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 104513 - PHOTOLUMINESCENT EGRESS PATH MARKINGS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Access Manufacturer-Provided, AIA MasterSpec-Based Sections:

<Double click here for this Section based on specific manufacturer’s products set as Basis-of-Design at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED 2009, LEED v4, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using the hypertext links.

MasterSpec includes provisions for LEED 2009, LEED v4, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using the hypertext links.

- GENERAL

      - SUMMARY

        - Section includes photoluminescent egress path markings.

        - Related Requirements:

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 101423 "Panel Signage" for photoluminescent floor number and evacuation route signs.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

        - Sustainable Design Submittals:

          - <Double click to insert sustainable design text for adhesives.>

        - Shop Drawings: For photoluminescent egress path markings.

          - Include plans, elevations, and details.

        - Samples: For each exposed product and for each color and texture specified, 6 inches (150 mm) long or full size.

      - INFORMATIONAL SUBMITTALS

        - Product Test Reports: Based on evaluation of comprehensive tests performed by a qualified testing agency, for luminance level of photoluminescent egress path markings.

        - Sample Warranties: For special warranties.

      - WARRANTY

When warranties are required, verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

        - Manufacturer's Warranty: Manufacturer agrees to replace photoluminescent egress path markings that fail in materials or workmanship within specified warranty period.

          - Failure includes, but is not limited to, decline in luminance below specified brightness level.

Several manufacturers offer limited lifetime warranties. Confirm availability and suitability.

          - Warranty Period: [25] <Insert number> years from date of Substantial Completion.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - PERFORMANCE REQUIREMENTS

Requirements in "Luminance" Paragraph below are based on the IBC; confirm with authorities having jurisdiction.

        - Luminance: Comply with one of the following; testing by a qualified testing agency:

          - UL 1994.

          - ASTM E2072; except that the charging source is to be 1 foot-candle (11 lux) of fluorescent illumination for 60 min., and the minimum luminance is to be 30 millicandelas/sq. m after 10 min. and 5 millicandelas/sq. m after 90 min.

      - PHOTOLUMINESCENT EGRESS PATH MARKINGS

        - Photoluminescent Egress Path Markings: Photoluminescent products containing no radioactive materials and requiring no electrical power.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Stair-and-Landing Nosing Markings:

Retain one of two subparagraphs below. NFPA 101 and local codes may not permit adhesive tape stripes.

          - Slip-resistive self-adhesive tape stripes; [1 inch (25 mm)] [2 inches (51 mm)] wide.

          - Slip-resistive [1-inch- (25-mm-)] [2-inch- (51-mm-)] wide stripes mounted to extruded-aluminum nosings[; with self-adhesive foam backing].

        - Handrail Markings: Self-adhesive [tape] [semi-rigid] stripes; [1 inch (25 mm)] [2 inches (51 mm)] wide.

        - Floor-Mounted Perimeter Markings: Self-adhesive tape stripes; [1 inch (25 mm)] [2 inches (51 mm)] wide[; with directional arrows].

        - Wall-Mounted Perimeter Markings:

Retain one of two subparagraphs below.

          - Self-adhesive tape stripes; [1 inch (25 mm)] [2 inches (51 mm)] wide[; with directional arrows].

          - [1-inch- (25-mm-)] [2-inch- (51-mm-)] wide stripes mounted to aluminum retainer[; with directional arrows].

        - Obstacle Marking: Self-adhesive stripe with alternating diagonal bands of black and photoluminescent material.

        - Door Frame Markings:

Retain one of two subparagraphs below.

          - Self-adhesive tape stripes [1 inch (25 mm)] [2 inches (51 mm)] wide[; with directional arrows].

          - [1-inch- (25-mm-)] [2-inch (51-mm-)] wide stripes mounted to aluminum retainer[; with directional arrows].

        - Door Hardware Markings: Square [self-adhesive sticker] [rigid plastic], 4 inches by 4 inches (102 mm by 102 mm).

Signs required by "Exit Signs" Paragraph below are for photoluminescent egress path requirements only; they do not meet the requirements for emergency exit signs and lighting in other parts of the IBC.

        - Exit Signs: Rigid plastic or aluminum sign for low-level mounting, with emergency exit symbol complying with NFPA 170[; with self-adhesive backing]; with a minimum height of 4 inches (102 mm); and with running man symbol facing right or left to suit installation condition.

        - Extruded Aluminum: ASTM B221 (ASTM B221M), Alloy 6063.

        - Adhesive: As recommended by manufacturer.

          - <Double click to insert sustainable design text for VOC content of adhesive.>

          - <Double click to insert sustainable design text for low emitting adhesives.>

- EXECUTION

      - PREPARATION

        - Comply with manufacturer's written instructions for surface preparation.

        - Clean and prepare surfaces to achieve a smooth, dry, clean surface free of flaking, unsound coatings, cracks, defects, projections, depressions, and substances that could impair bond between photoluminescent egress path markings and wall or floor surfaces.

      - INSTALLATION

        - General: Install photoluminescent egress path markings according to manufacturer's written instructions.

        - Install aluminum nosings with adhesive and mechanical fasteners.

END OF SECTION 104513