Copyright 2016 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 210518 - ESCUTCHEONS FOR FIRE-SUPPRESSION PIPING

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section title referenced in this Section is correct for this Project's Specifications; Section title may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Escutcheons.

          - Floor plates.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

        - Existing Piping to Remain: Existing piping that is not to be removed and that is not otherwise indicated to be removed, removed and salvaged, or removed and reinstalled.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

- PRODUCTS

Manufacturers and products listed in SpecAgent and MasterWorks Paragraph Builder are neither recommended nor endorsed by the AIA or Deltek. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - MANUFACTURERS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

      - ESCUTCHEONS

Retain types and finish options in this article that match those retained in Part 3.

Escutcheons described in "One-Piece, Steel Type"; "One-Piece, Stainless-Steel Type"; and "One-Piece, Cast-Brass Type" paragraphs below are generally available in 5/8-inch (15-mm) OD, 7/8-inch (22-mm) OD, 1-1/4-inch (32-mm) OD, 1-1/2-inch (38-mm) OD, 3/8-inch (10-mm) IPS, 1/2-inch (13-mm) IPS, 3/4-inch (19-mm) IPS, 1-1/4-inch (32-mm) IPS, 1-1/2-inch (38-mm) IPS, and 2-inch (50-mm) IPS. Stainless-steel escutcheons and brass escutcheons have limited size availability and are not offered by all manufacturers. Each finish is not offered with each base metal by all manufacturers. Consult manufacturers.

        - One-Piece, Steel Type: With [polished, chrome-plated] [polished brass] finish and setscrew fastener.

        - One-Piece, Stainless-Steel Type: With polished stainless-steel finish.

        - One-Piece, Cast-Brass Type: With [polished, chrome-plated] [polished brass] finish and setscrew fastener.

Escutcheons described in "One-Piece, Deep-Pattern Type" Paragraph below are generally available in 1-1/4-inch (32-mm) OD, 1-1/2-inch (38-mm) OD, 1-1/4-inch (32-mm) IPS, and 1-1/2-inch (38-mm) IPS. The "brass" option below has limited size availability and is not offered by every manufacturer. Consult manufacturers.

        - One-Piece, Deep-Pattern Type: Deep-drawn, box-shaped [steel] [brass] with polished, chrome-plated finish and spring-clip fasteners.

Escutcheons described in "One-Piece, Stamped-Steel Type" Paragraph below are generally available in 5/8-inch (15-mm) OD, 7/8-inch (22-mm) OD, 1-1/4-inch (32-mm) OD, 1-1/2-inch (38-mm) OD, 3/8-inch (10-mm) IPS, 1/2-inch (13-mm) IPS, 3/4-inch (19-mm) IPS, 1-inch (25-mm) IPS, 1-1/4-inch (32-mm) IPS, 1-1/2-inch (38-mm) IPS, and 2-inch (50-mm) IPS.

        - One-Piece, Stamped-Steel Type: With polished, chrome-plated finish and spring-clip fasteners.

Retain one or both finish options in "Split-Plate, Stamped-Steel Type" Paragraph below that match escutcheon types retained in Part 3. Escutcheons described in paragraph are generally available in 5/8-inch (15-mm) OD, 7/8-inch (22-mm) OD, 1-1/4-inch (32-mm) OD, 1-1/2-inch (38-mm) OD, 3/8-inch (10-mm) IPS, 1/2-inch (13-mm) IPS, 3/4-inch (19-mm) IPS, 1-inch (25-mm) IPS, 1-1/4-inch (32-mm) IPS, 1-1/2-inch (38-mm) IPS, and 2-inch (50-mm) IPS.

        - Split-Plate, Stamped-Steel Type: With polished, chrome-plated finish; [concealed] [and] [exposed-rivet] hinge; and spring-clip fasteners.

      - FLOOR PLATES

Escutcheons described in "Split Floor Plates" Paragraph below are generally available in 5/8-inch (15-mm) OD, 7/8-inch (22-mm) OD, 1-1/4-inch (32-mm) OD, 1-1/2-inch (38-mm) OD, 3/8-inch (10-mm) IPS, 1/2-inch (13-mm) IPS, 3/4-inch (19-mm) IPS, 1-1/4-inch (32-mm) IPS, 1-1/2-inch (38-mm) IPS, and 2-inch (50-mm) IPS. Consult manufacturers.

        - Split Floor Plates: Steel with concealed hinge.

- EXECUTION

      - INSTALLATION

        - Install escutcheons for piping penetrations of walls, ceilings, and finished floors.

        - Install escutcheons with ID to closely fit around pipe, tube, and insulation of piping and with OD that completely covers opening.

Coordinate retained selections with Section 220518 "Escutcheons for Plumbing Piping" and Section 230518 "Escutcheons for HVAC Piping" for consistency.

See Part 2 for information on availability of finishes and sizes.

          - Escutcheons for New Piping[ and Relocated Existing Piping]:

            - Piping with Fitting or Sleeve Protruding from Wall: One-piece, deep pattern.

            - Chrome-Plated Piping: One-piece [steel] [cast brass][ or split-plate steel] with polished, chrome-plated finish.

Retain one of four "Insulated Piping" subparagraphs below.

            - Insulated Piping: One-piece steel with [polished, chrome-plated] [polished brass] finish.

            - Insulated Piping: One-piece stainless steel with polished stainless-steel finish.

            - Insulated Piping: One-piece cast brass with [polished, chrome-plated] [polished brass] finish.

            - Insulated Piping: One-piece stamped steel [or split-plate, stamped steel with concealed hinge] [or split-plate, stamped steel with exposed-rivet hinge] with polished, chrome-plated finish.

Retain one of four "Bare Piping at Wall and Floor Penetrations in Finished Spaces" subparagraphs below.

            - Bare Piping at Wall and Floor Penetrations in Finished Spaces: One-piece steel with [polished, chrome-plated] [polished brass] finish.

            - Bare Piping at Wall and Floor Penetrations in Finished Spaces: One-piece stainless steel with polished stainless-steel finish.

            - Bare Piping at Wall and Floor Penetrations in Finished Spaces: One-piece cast brass with [polished, chrome-plated] [polished brass] finish.

            - Bare Piping at Wall and Floor Penetrations in Finished Spaces: One-piece stamped steel [or split-plate, stamped steel with concealed hinge] [or split-plate, stamped steel with exposed-rivet hinge] with polished, chrome-plated finish.

Retain one of four "Bare Piping at Ceiling Penetrations in Finished Spaces" subparagraphs below.

            - Bare Piping at Ceiling Penetrations in Finished Spaces: One-piece steel with [polished, chrome-plated] [polished brass] finish.

            - Bare Piping at Ceiling Penetrations in Finished Spaces: One-piece stainless steel with polished stainless-steel finish.

            - Bare Piping at Ceiling Penetrations in Finished Spaces: One-piece cast brass with [polished, chrome-plated] [polished brass] finish.

            - Bare Piping at Ceiling Penetrations in Finished Spaces: One-piece stamped steel [or split-plate, stamped steel with concealed hinge] [or split-plate, stamped steel with exposed-rivet hinge] with polished, chrome-plated finish.

Retain one of three "Bare Piping in Unfinished Service Spaces" subparagraphs below.

            - Bare Piping in Unfinished Service Spaces: One-piece steel with polished, chrome-plated finish.

            - Bare Piping in Unfinished Service Spaces: One-piece cast brass with [polished, chrome-plated] [rough-brass] finish.

            - Bare Piping in Unfinished Service Spaces: One-piece stamped steel [or split-plate, stamped steel with concealed hinge] [or split-plate, stamped steel with exposed-rivet hinge] with polished, chrome-plated finish.

Retain one of three "Bare Piping in Equipment Rooms" subparagraphs below.

            - Bare Piping in Equipment Rooms: One-piece steel with polished, chrome-plated finish.

            - Bare Piping in Equipment Rooms: One-piece cast brass with [polished, chrome-plated] [rough-brass] finish.

            - Bare Piping in Equipment Rooms: One-piece stamped steel [or split-plate, stamped steel with concealed hinge] [or split-plate, stamped steel with exposed-rivet hinge] with polished, chrome-plated finish.

          - Escutcheons for Existing Piping to Remain:

            - Chrome-Plated Piping: Split-plate, stamped steel with [concealed] [or] [exposed-rivet] hinge with polished, chrome-plated finish.

            - Insulated Piping: Split-plate, stamped steel with [concealed] [or] [exposed-rivet] hinge with polished, chrome-plated finish.

            - Bare Piping at Wall and Floor Penetrations in Finished Spaces: Split-plate, stamped steel with [concealed] [or] [exposed-rivet] hinge with polished, chrome-plated finish.

            - Bare Piping at Ceiling Penetrations in Finished Spaces: Split-plate, stamped steel with [concealed] [or] [exposed-rivet] hinge with polished, chrome-plated finish.

            - Bare Piping in Unfinished Service Spaces: Split-plate, stamped steel with [concealed] [or] [exposed-rivet] hinge with polished, chrome-plated finish.

            - Bare Piping in Equipment Rooms: Split-plate, stamped steel with [concealed] [or] [exposed-rivet] hinge with polished, chrome-plated finish.

        - Install floor plates for piping penetrations of equipment-room floors.

        - Install floor plates with ID to closely fit around pipe, tube, and insulation of piping and with OD that completely covers opening.

Subparagraphs below apply to both bare and insulated piping.

          - New Piping [and] [Relocated Existing Piping]: One-piece, floor plate.

          - Existing Piping: Split floor plate.

      - FIELD QUALITY CONTROL

        - Using new materials, replace broken and damaged escutcheons and floor plates.

END OF SECTION 210518