Copyright 2019 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 210548.13 - VIBRATION CONTROLS FOR FIRE-SUPPRESSION PIPING AND EQUIPMENT

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Use this Section if Project is not in a seismic area. Use Section 210548 "Vibration and Seismic Controls for Fire-Suppression Piping and Equipment" for projects in a seismic area.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Elastomeric isolation pads.

          - Elastomeric isolation mounts.

          - Restrained elastomeric isolation mounts.

          - Elastomeric hangers.

          - Snubbers.

          - Restraints - rigid type.

          - Restraints - cable type.

          - Restraint accessories.

          - Post-installed concrete anchors.

          - Concrete inserts.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 220548.13 "Vibration Controls for Plumbing Piping and Equipment" for devices for plumbing equipment and systems.

          - Section 230548.13 "Vibration Controls for HVAC" for devices for HVAC equipment and systems.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

        - IBC: International Building Code.

        - OSHPD: Office of Statewide Health Planning and Development (for the State of California).

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

          - Include rated load, rated deflection, and overload capacity for each vibration isolation device.

Retain first subparagraph below if load design services have been delegated to Contractor.

          - Include load rating for each wind-load-restraint fitting and assembly.

          - Illustrate and indicate style, material, strength, fastening provision, and finish for each type and size of vibration isolation device [and wind-load-restraint ]component.

          - Annotate to indicate application of each product submitted and compliance with requirements.

          - Interlocking Snubbers: Include ratings for horizontal, vertical, and combined loads.

        - Shop Drawings:

          - Detail fabrication and assembly of equipment bases. Detail fabrication including anchorages and attachments to structure and to supported equipment. Include adjustable motor bases, rails, and frames for equipment mounting.

Retain "Delegated-Design Submittal" Paragraph below if wind-load-restraint design services have been delegated to Contractor.

        - Delegated-Design Submittal:

          - For each wind-load protection device that is required by this Section or is indicated on Drawings, submit the following:

            - Wind-Load-Restraint Selection: Select wind-load restraints complying with performance requirements, design criteria, and analysis data.

            - Riser Supports: Include riser diagrams and calculations showing anticipated expansion and contraction at each support point, initial and final loads on building structure. Include certification by professional engineer that riser system was examined for excessive stress and that none exists.

            - Post-Installed Concrete Anchors and Inserts: Include calculations showing anticipated wind loads.

            - Wind-Load Design Calculations: Submit all static and dynamic loading calculations prepared under "Wind-Load Design Calculations" Paragraph in "Performance Requirements" Article.

Retain "Qualified Professional Engineer" Subparagraph below if certification by a qualified professional engineer is required by codes, authorities having jurisdiction, or Owner.

            - Qualified Professional Engineer: All designated-design submittals for wind-load-restraint calculations are to be signed and sealed by qualified professional engineer responsible for their preparation.

Retain "Wind-Load-Restraint Detail Drawings" Subparagraph below only if design requirements apply but calculations have not been made and details or charts on Drawings do not describe wind restraints in detail. Retaining subparagraph requires Contractor to submit delegated-design Drawings prepared by a professional engineer. Revise to suit Project requirements.

          - Wind-Load-Restraint Detail Drawing:

            - Design Analysis: To support selection and arrangement of wind load restraints. Include calculations of combined tensile and shear loads.

            - Details: Indicate fabrication and arrangement. Detail attachments of restraints to the restrained items and to the structure. Show attachment locations, methods, and spacings. Identify components, list their strengths, and indicate directions and values of forces transmitted to the structure during wind events. Indicate association with vibration isolation devices.

            - All delegated-design submittals for wind-restraint detail Drawings are to be signed and sealed by qualified professional engineer responsible for their preparation.

          - Product Listing, Preapproval, and Evaluation Documentation: By [an evaluation service member of ICC-ES] [UL] [FM Approvals] [OSHPD] [an agency acceptable to authorities having jurisdiction], showing maximum ratings of restraint items and the basis for approval (tests or calculations).

          - Riser Supports: Include riser diagrams and calculations showing anticipated expansion and contraction at each support point, initial and final loads on building structure. Include certification that riser system was examined for excessive stress and that none exists.

      - INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below if piping, equipment, and other fire-suppression system components are installed in congested areas.

        - Coordination Drawings: Show coordination of vibration isolation [and wind-load reinforcement ]device installation for fire-suppression piping and equipment with other systems and equipment in the vicinity, including other supports and restraints, if any.

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Data: For [professional engineer] [and] [testing agency].

Retain "Welding certificates" Paragraph below if retaining "Welding Qualifications" Paragraph in "Quality Assurance" Article.

        - Welding certificates.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

Retain "Wind-Load Performance Certification" Paragraph below in "Informational Submittals" Article of all Specification Sections that specify fire-suppression system equipment requiring wind-load certification.

See "Wind-Load Certification" Article in the Evaluations for a discussion on certification. Certification requirement covers fire-suppression system equipment subject to wind load. These must be identified by fire-suppression system engineer in the Equipment Schedule or a separate Vibration Isolation and Wind-Load Control Schedule; or, if the number of devices and systems is small, they can be listed in the Specifications.

        - Wind-Load Performance Certification: Provide special certification for fire-suppression system components subject to high wind exposure and impact damage and designated on Drawings or in the Specifications to require wind-load performance certification.

          - Provide equipment manufacturer's written certification for each designated fire suppression system device, stating that it will remain in place and operable following the design wind event and comply with all requirements of authorities having jurisdiction.

          - Certification must be based on ICC-ES or similar nationally recognized testing standard procedures acceptable to authorities having jurisdiction.

Retain subparagraph below only if systems requiring wind-load performance certification are not scheduled. If a schedule is not being used, all wind-load performance certified systems must be listed below. See "Wind-Load Certification" Article in the Evaluations for more information.

          - The following fire-suppression system systems and components require special certification for high wind performance. Written special certification of resistance to the effects of high wind load and impact damage must be provided by manufacturer.

            - <Insert list>.

      - QUALITY ASSURANCE

If an independent testing agency is required, see Section 014000 "Quality Requirements" for general testing and inspecting agency qualification requirements. If additional control is needed, retain "Testing Agency Qualifications" Paragraph below to specify 29 CFR 1910.7 which defines "NRTL" (nationally recognized testing laboratory) as it applies to testing and inspecting for safety, and lists, labels, or accepts equipment and materials that comply with certain OSHA criteria.

Retain below if Contractor is to select testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article.

        - Testing Agency Qualifications: An independent agency, with the experience and capability to conduct testing indicated, that is an NRTL as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

Retain "Welding Qualifications" Paragraph below if shop or field welding is required. If retaining, also retain "Welding certificates" Paragraph in "Informational Submittals" Article.

        - Welding Qualifications: Qualify procedures and personnel according to AWS D1.1/D1.1M, "Structural Welding Code - Steel."

Retain "Wind-Load-Restraint Device Load Ratings" Paragraph below if wind-load-restraint device testing is applicable.

        - Wind-Load-Restraint Device Load Ratings: Devices to be tested and rated in accordance with applicable code requirements and authorities having jurisdiction. Devices to be listed by a nationally recognized third party that requires periodic follow-up inspections and has a listing directory available to the public. Provide third-party listing by one or more of the following: [ICC-ES product listing] [UL product listing] [FM Approvals] [an evaluation service member of ICC-ES] [an agency acceptable to authorities having jurisdiction].

- PRODUCTS

Manufacturers and products listed in SpecAgent and MasterWorks Paragraph Builder are neither recommended nor endorsed by the AIA or Deltek. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

See the Evaluations for more detailed information about controlling vibration, additional information on products described in this Section, illustrations, selection guides, and supplements to Equipment Schedules.

      - PERFORMANCE REQUIREMENTS

Retain "Delegated Design" Paragraph below if Contractor is required to assume responsibility for design.

        - Delegated Design: Engage a qualified professional engineer, as defined in Section 014000 "Quality Requirements," to design wind-load-restraint system.

Retain "Wind-Load Performance" Subparagraph below if wind-load protection is required. Delete subparagraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to high wind events. Coordinate requirements with Project structural engineer.

          - Wind-Load Performance: Equipment must be designed and secured to withstand effects of high wind events determined in accordance with [ASCE/SEI 7-05] [ASCE/SEI 7-10] [ASCE/SEI 7-16] <Insert requirement>.

Retain "Wind-Load Design Calculations" Paragraph and applicable calculation factors subparagraph below if wind-load reinforcement design services have been delegated to Contractor.

        - Wind-Load Design Calculations:

ASCE/SEI 7 and NFPA 13 are generally applicable in most locations, but it is fire-suppression system engineer's responsibility to determine the applicable building codes and editions thereof, and applicable wind-load design standards that apply to this Project. Data and information required for wind-load calculations in ASCE/SEI 7 are listed below. ASCE/SEI 7-05, ASCE/SEI 7-10, and ASCE/SEI 7-16 differ somewhat; material from all three editions has been included below and has been noted. Fire-suppression system engineer must delete all non-applicable editions throughout the Section.

If a calculation method other than that prescribed in ASCE/SEI 7 is to be used, fire-suppression system engineer must revise the Section Text to provide alternative appropriate calculation parameters and instruction for delegated designer in lieu of those given below.

          - Comply with wind-load-restraint requirements of all applicable codes and authorities having jurisdiction.

          - Perform calculations to obtain force information necessary to properly select wind-load-restraint devices, fasteners, and anchorage. Perform calculations using methods acceptable to applicable code authorities and as presented in [ASCE/SEI 7-05] [ASCE/SEI 7-10] [ASCE/SEI 7-16] <Insert ASCE/SEI 7 edition or other wind-load calculation method required by authorities having jurisdiction>. Where "ASCE/SEI 7" is used throughout this Section, it is to be understood that the edition referred to in this subparagraph is intended as referenced throughout the Section Text unless otherwise noted.

            - Factors indicated below that are specific to individual pieces of equipment must be obtained by Contractor and must be included in individual component submittal packages.

            - Coordinate design wind-load calculations with vibration isolation calculations for equipment requiring both wind-load reinforcement and vibration isolation. Comply with requirements in other Sections in addition to those in this Section for equipment mounted outdoors.

Data values identified below as applying to all components on Project are to be inserted by fire-suppression system engineer into these Specifications where indicated in the following list. Data values that are specific to an individual generic component and are indicated to be scheduled should be included by fire-suppression system engineer in Fire-Suppression System Vibration Isolation and Wind-Load-Restraint Schedule or the individual component schedules on Drawings. Data values that are specific to an individual piece of equipment as provided by Contractor and are indicated to be obtained by Contractor must be included in individual component submittal packages.

Retain one of first two design wind pressure subparagraphs below if ASCE/SEI 7-16 applies to this Project.

          - Design wind pressure "p" for external sidewall-mounted equipment is to be calculated by Delegated-Design Contractor using methods in ASCE/SEI 7-16, Ch. 30. Perform calculations in accordance with one of the following, as appropriate:

            - PART 1: Low-Rise Buildings.

            - PART 2: Low-Rise Buildings (Simplified).

            - PART 3: Buildings with "h" less than 60 feet (18.3 m).

            - PART 4: Buildings with "h" greater than 60 feet (18.3 m) and less than 160 feet (48.8 m).

            - PART 5: Open Buildings.

          - Design wind pressure "p" for rooftop equipment is to be calculated by Delegated-Design Contractor using methods in ASCE/SEI 7-16, Ch. 30, PART 6: Building Appurtenances and Rooftop Structures and Equipment.

"Risk category" value is determined by fire-suppression system engineer from Project structural engineer or ASCE/SEI 7-16, Table 1.5-1.

            - Risk Category: [I] [II] [III] [IV] [V].

"Mean Roof Height" is determined by fire-suppression system engineer from Project Drawings.

            - h = Mean Roof Height: <Insert value>.

"Basic Wind Speed" value is obtained by fire-suppression system engineer from Wind Hazard map in ASCE/SEI 7-16 Section 26.5 or other source approved by authorities having jurisdiction.

            - V = Basic Wind Speed: <Insert value>.

"Wind directionality factor" value is obtained by fire-suppression system engineer from ASCE/SEI 7-16 Section 26.6 and Table 26.6-1 or other source approved by authorities having jurisdiction.

            - Kd = Wind Directionality Factor: <Insert factor>.

"Exposure category" value is obtained by fire-suppression system engineer from ASCE/SEI 7-16 Section 26.7 or other source approved by authorities having jurisdiction.

            - Exposure Category: [B] [C] [D].

"Topographic factor" value is obtained by fire-suppression system engineer from ASCE/SEI 7-16 Section 26.8 and Table 26.8-1 or other source approved by authorities having jurisdiction.

            - Kzt = Topographic Factor: <Insert factor>.

"Ground elevation factor" value is obtained by fire-suppression system engineer from ASCE/SEI 7-16 Section 26.8 and Table 26.8-1 or other source approved by authorities having jurisdiction.

            - Ke = Ground Elevation Factor: <Insert factor>.

"Velocity pressure exposure coefficient" value at height z and height h is obtained by fire-suppression system engineer from ASCE/SEI 7-16 Section 26.10.1 or other source approved by authorities having jurisdiction.

            - Kz = Velocity Pressure Exposure Coefficient (Evaluated at Height z): <Insert coefficient>.

            - Kh = Velocity Pressure Exposure Coefficient (Evaluated at Height h): <Insert coefficient>.

            - qz = Velocity Pressure: Value calculated by delegated wind-load design Contractor using methods detailed in ASCE/SEI 7-16 Section 26.10.1 or other source approved by authorities having jurisdiction.

            - qh = Velocity Pressure: Value calculated by delegated wind-load design Contractor using methods detailed in ASCE/SEI 7-16 Section 26.10.1 or other source approved by authorities having jurisdiction.

"Gust-effect factor" is obtained by fire-suppression system engineer form ASCE/SEI 7-16 Section 26.11 or other source approved authorities having jurisdiction.

            - G = Gust-Effect Factor: [0.85] <Insert factor>.

"Enclosure classification" is obtained by fire-suppression system engineer from ASCE/SEI 7-16 Section 26.12 or other source approved by authorities having jurisdiction.

            - Enclosure Classification: <Insert classification>.

"Internal pressure coefficient" is obtained by fire-suppression system engineer from ASCE/SEI 7-16, Table 26.13-1 or other source approved by authorities having jurisdiction.

            - GCpi = Internal Pressure Coefficient: <Insert coefficient>.

Retain one of two design wind pressure subparagraphs below if ASCE/SEI 7-10 applies to this Project.

          - Design wind pressure "p" for external sidewall-mounted equipment is to be calculated by Delegated-Design Contractor using the methods in ASCE/SEI 7-10, Ch. 30. Perform calculations according to PART 1: -Rise Buildings, PART 2: Low-Rise Buildings (Simplified), PART 3: Buildings with "h" greater than 60 feet (18.3 m), PART 4: Buildings with "h" less than 160 feet (48.8 m), or PART 5: Open Buildings, as appropriate.

          - Design wind pressure "p" for rooftop equipment is to be calculated by Delegated-Design Contractor using methods in ASCE/SEI 7-10, Ch. 30, PART 6: Building Appurtenances and Rooftop Structures and Equipment.

"Risk category" value is determined by fire-suppression system engineer from Project structural engineer or ASCE/SEI 7-10, Table 1.5-1.

            - Risk Category: [I] [II] [III] [IV] [V].

"Mean Roof Height" is determined by fire-suppression system engineer from Project Drawings.

            - h = Mean Roof Height: <Insert value>.

"Basic Wind Speed" value is obtained by fire-suppression system engineer from Wind Hazard map in ASCE/SEI 7-10, Figures 26.5-1A through 26.1C or other source approved by authorities having jurisdiction.

            - V = Basic Wind Speed: <Insert value>.

"Wind directionality factor" value is obtained by fire-suppression system engineer from ASCE/SEI 7-10 Section 26.6 and Table 26.6-1 or other source approved by authorities having jurisdiction.

            - Kd = Wind Directionality Factor: <Insert factor>.

"Exposure category" value is obtained by fire-suppression system engineer from ASCE/SEI 7-10 Section 26.7 or other source approved by authorities having jurisdiction.

            - Exposure Category: [B] [C] [D].

"Topographic factor" value is obtained by fire-suppression system engineer from ASCE/SEI 7-10 Section 26.8 and Table 26.8-1 or other source approved by authorities having jurisdiction.

            - Kzt = Topographic Factor: <Insert factor>.

"Velocity pressure exposure coefficient" is obtained by fire-suppression system engineer from ASCE/SEI 7-10 Section 26.10.1 or other source approved by authorities having jurisdiction.

            - Kz = Velocity Pressure Exposure Coefficient (Evaluated at Height z): <Insert coefficient>.

            - Kh = Velocity Pressure Exposure Coefficient (Evaluated at Height h): <Insert coefficient>.

            - qz = Velocity Pressure at Height z: Value calculated by delegated wind-load design Contractor using methods detailed in ASCE/SEI 7-10 Section 26.10.1 or other source approved by authorities having jurisdiction.

            - qh = Velocity Pressure at Height h: Value calculated by delegated wind-load design Contractor using methods detailed in ASCE/SEI 7-10 Section 26.10.1 or other source approved by authorities having jurisdiction.

"Gust-effect factor" is obtained by fire-suppression system engineer form ASCE/SEI 7-10 Section 26.9 or other source approved by authorities having jurisdiction.

            - G = Gust-Effect Factor: [0.85] <Insert factor>.

"Enclosure classification" is obtained by fire-suppression system engineer from ASCE/SEI 7-10 Section 26.10 or other source approved by authorities having jurisdiction.

            - Enclosure Classification: <Insert classification>.

"Internal pressure coefficient" is obtained by fire-suppression system engineer from ASCE/SEI 7-10 Section 26.11 and Table 26.11-1 or other source approved by authorities having jurisdiction.

            - GCpi = Internal Pressure Coefficient: <Insert coefficient>.

Retain design wind force Subparagraph below if ASCE/SEI 7-05 applies to this Project.

          - Design wind force "F" for rooftop equipment and external sidewall-mounted equipment such as louvers is to be calculated by Delegated-Design Contractor using methods in ASCE/SEI 7-05, Ch. 6.

"Importance Factor" value is determined by fire-suppression system engineer from ASCE/SEI 7-05, Table 6-1 and ASCE/SEI 7-05, Table 1-1.

            - I = Importance Factor: <Insert factor>.

"Mean Roof Height" is determined by fire-suppression system engineer from Project Drawings.

            - h = Mean Roof Height: <Insert value>.

"Basic Wind Speed" value is obtained by fire-suppression system engineer from Wind Hazard map in ASCE/SEI 7-05, Figure 6.1 or other source approved by authorities having jurisdiction.

            - V = Basic Wind Speed: <Insert value>.

"Wind directionality factor" value is obtained by fire-suppression system engineer from ASCE/SEI 7-05, Table 6-4 or other source approved by authorities having jurisdiction.

            - Kd = Wind Directionality Factor: <Insert factor>.

"Exposure category" value is obtained by fire-suppression system engineer from ASCE/SEI 7-05 Section 6.5.6.3 or other source approved by authorities having jurisdiction.

            - Exposure Category: [B] [C] [D].

"Topographic factor" value is obtained by fire-suppression system engineer from ASCE/SEI 7-05 Section 6.5.7.2, Table 6-4 or other source approved by authorities having jurisdiction.

            - Kzt = Topographic Factor: <Insert factor>.

"Velocity pressure exposure coefficient" is obtained by fire-suppression system engineer from ASCE/SEI 7-05 Section 6.5.6.6, Table 6-3 or other source approved by authorities having jurisdiction.

            - Kz = Velocity Pressure Exposure Coefficient (Evaluated at Height z): <Insert coefficient>.

            - Kh = Velocity Pressure Exposure Coefficient (Evaluated at Height h): <Insert coefficient>.

            - qz = Velocity Pressure at Height z: Value calculated by delegated wind-load design Contractor using methods detailed in ASCE/SEI 7-05 Section 6.5.10 or other source approved by authorities having jurisdiction.

            - qh = Velocity Pressure at Roof Height h: Value calculated by delegated wind-load design Contractor using methods detailed in ASCE/SEI 7-05 Section 6.5.10 or other source approved by authorities having jurisdiction.

"Gust-effect factor" is obtained by fire-suppression system engineer from ASCE/SEI 7-05 Section 6.5.8 or other source approved by authorities having jurisdiction.

            - G = Gust-Effect Factor: [0.85] <Insert factor>.

"Internal pressure coefficient" is obtained by fire-suppression system engineer from ASCE/SEI 7-05, Figure 6-5 or other source approved by authorities having jurisdiction.

            - GCpi = Internal Pressure Coefficient: <Insert coefficient>.

"External pressure coefficient" is obtained by fire-suppression system engineer from ASCE/SEI 7-05, Figures 6-11 through 6-16 or other source approved by authorities having jurisdiction.

            - GCp = External Pressure Coefficient: <Insert coefficient>.

            - Cf = Force Coefficient: Value determined by delegated wind-load design Contractor from ASCE/SEI 7-05, Figures 6-21 through 6-23 or other source approved by authorities having jurisdiction.

            - Af = Projected Area Normal to the Wind: Except where Cf is specified for the actual surface area, value determined by delegated wind-load design Contractor from equipment submittal or manufacturer.

        - Consequential Damage: Provide additional restraints for suspended fire-suppression system components or anchorage of floor-, roof-, or wall-mounted fire-suppression system components as indicated in [ASCE/SEI 7-05] [ASCE/SEI 7-10] [ASCE/SEI 7-16] so that failure of a non-essential or essential fire-suppression system component will not cause the failure of any other essential architectural, mechanical, or electrical building component.

        - Fire/Smoke Resistance: All devices and components that are not constructed of ferrous metals must have a maximum flame-spread index of 25 and maximum smoke-developed index of 50 when tested by an NRTL in accordance with ASTM E84 or UL 723, and be so labeled.

        - Component Supports:

          - Load ratings, features, and applications of all reinforcement components must be based on testing standards of a nationally recognized testing agency.

          - All component support attachments must comply with force and displacement resistance requirements of [ASCE/SEI 7-05 Section 13.6] [ASCE/SEI 7-10 Section 13.6] [ASCE/SEI 7-16 Section 13.6].

      - ELASTOMERIC ISOLATION PADS

Copy "Elastomeric Isolation Pads" Paragraph below and re-edit for each product.

Configuration and materials of elastomeric isolation pads depend on the equipment being supported. It is possible to have more than one type of elastomeric isolation pad on same Project. Insert Drawing designation. Use these designations on Drawings to identify each product.

        - Elastomeric Isolation Pads: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Fabrication: Single or multiple layers of sufficient durometer stiffness for uniform loading over pad area.

          - Size: Factory or field cut to match requirements of supported equipment.

          - Pad Material: Oil and water resistant with elastomeric properties. Neoprene rubber, silicone rubber, or other elastomeric material.

          - Surface Pattern: Smooth, ribbed, or waffle pattern.

Retain first subparagraph below if pad is infused with synthetic fibers.

          - Infused nonwoven cotton or synthetic fibers.

Retain first subparagraph below if galvanized-steel baseplates are adhered to isolation pad to facilitate load distribution.

          - Load-bearing metal plates adhered to pads.

Retain "Sandwich-Core Material" Subparagraph below if pad has a sandwich-core material.

Copy below and re-edit for each sandwich-core material. Core materials may not be elastomeric. See "Elastomeric Isolation Pads" Article in the Evaluations for more information.

          - Sandwich-Core Material: [Resilient] [and] [elastomeric] <Insert compound>.

Retain "Surface Pattern" Subparagraph below if the sandwich-core material has a surface pattern.

            - Surface Pattern: Smooth, ribbed, or waffle pattern.

Retain subparagraph below if pad is infused with synthetic fibers.

            - Infused nonwoven cotton or synthetic fibers.

      - ELASTOMERIC ISOLATION MOUNTS

Copy "Double-Deflection, Elastomeric Isolation Mounts" Paragraph below and re-edit for each product.

Configuration and materials of elastomeric isolation mounts depend on the equipment being supported. It is possible to have more than one type of elastomeric isolation mount on same Project. Insert drawing designation. Use these designations on Drawings to identify each product.

        - Double-Deflection, Elastomeric Isolation Mounts: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Mounting Plates:

            - Top Plate: Encapsulated steel load transfer top plates, factory drilled and threaded[ with threaded studs or bolts].

Retain "Baseplate" Subparagraph below if the elastomeric mount being specified has a baseplate.

            - Baseplate: Encapsulated steel bottom plates with holes provided for anchoring to support structure.

          - Elastomeric Material: Molded, oil and water resistant neoprene rubber, silicone rubber, or other elastomeric material.

      - RESTRAINED ELASTOMERIC ISOLATION MOUNTS

Copy "Restrained Elastomeric Isolation Mounts" Paragraph below and re-edit for each product.

Configuration and materials of restrained elastomeric isolation mounts depend on the equipment being supported. It is possible to have more than one type of restrained elastomeric isolation mount on same Project. Insert drawing designation. Use these designations on Drawings to identify each product.

        - Restrained Elastomeric Isolation Mounts: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: All-directional isolator with seismic restraints containing two separate and opposing elastomeric elements that prevent central threaded element and attachment hardware from contacting the housing during normal operation.

            - Housing: Cast-ductile iron or welded steel.

            - Elastomeric Material: Molded, oil-resistant rubber, neoprene, or other elastomeric material.

      - ELASTOMERIC HANGERS

Copy "Elastomeric Mount in a Steel Frame with Upper and Lower Steel Hanger Rods" Paragraph below and re-edit for each product.

Configuration and materials of elastomeric hangers depend on the equipment being supported. It is possible to have more than one type of elastomeric hanger on same Project. Insert drawing designation. Use these designations on Drawings to identify each product.

        - Elastomeric Mount in a Steel Frame with Upper and Lower Steel Hanger Rods: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Frame: Steel, fabricated with a connection for an upper threaded hanger rod and an opening on the underside to allow for a maximum of 30 degrees of angular lower hanger-rod misalignment without binding or reducing isolation efficiency.

          - Damping Element: Molded, oil-resistant rubber, neoprene, or other elastomeric material with a projecting bushing for the underside opening preventing steel-to-steel contact.

      - SNUBBERS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Factory fabricated using welded structural-steel shapes and plates, anchor bolts, and replaceable resilient isolation washers and bushings.

          - Post-Installed Concrete Anchor Bolts: Secure to concrete surface with post-installed concrete anchors. Anchors to be seismically prequalified in accordance with ACI 355.2 testing and designated in accordance with [ACI 318-08 Appendix D for 2009 IBC] [ACI 318-11 Appendix D for 2012 IBC] [ACI 318-14 Ch. 17 for 2015 or 2018 IBC].

          - Preset Concrete Inserts: Seismically prequalified in accordance with ICC-ES AC446 testing.

          - Anchors in Masonry: Design in accordance with TMS 402.

          - Resilient Isolation Washers and Bushings: Oil- and water-resistant neoprene.

          - Resilient Cushion: Maximum 1/4-inch (6-mm) air gap, and minimum 1/4 inch (6 mm) thick.

      - RESTRAINTS - RIGID TYPE

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Shop- or field-fabricated bracing assembly made of AISI S110-07-S1 slotted steel channels, ANSI/ASTM A53/A53M steel pipe as per NFPA 13, or other rigid steel brace member. Includes accessories for attachment to braced component at one end and to building structure at the other end and other matching components and with corrosion-resistant coating; rated in tension, compression, and torsion forces.

      - RESTRAINTS - CABLE TYPE

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Seismic-Restraint Cables: [ASTM A1023/A1023M galvanized or ASTM A603 galvanized-steel] [ASTM A492 stainless steel] cables. End connections made of steel assemblies with thimbles, brackets, swivel, and bolts designed for seismic-restraining cable service; with fittings attached by means of poured socket, swaged socket or mechanical (Flemish eye) loop.

        - Restraint cable assembly with cable fittings must comply with ASCE/SEI 19. All cable fittings and complete cable assembly must maintain the minimum cable breaking force. U-shaped cable clips and wedge-type end fittings do not comply and are unacceptable.

      - RESTRAINT ACCESSORIES

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Hanger-Rod Stiffener" Paragraph below for strengthening resistance of hanger rods against seismic and wind forces that may cause buckling of rods; delete if detailed on Drawings. Use with either rigid- or cable-type bracing assemblies when required to counter seismic and wind forces. Detail fabrication and indicate locations on Drawings.

        - Hanger-Rod Stiffener: [Steel tube or steel slotted-support-system sleeve with internally bolted connections] [Reinforcing steel angle clamped] to hanger rod. Non-metallic stiffeners are unacceptable.

        - Hinged and Swivel Brace Attachments: Multifunctional steel connectors for attaching hangers to [rigid channel bracings] [and] [restraint cables].

        - Bushings for Floor-Mounted Equipment Anchor Bolts: Neoprene bushings designed for rigid equipment mountings, and matched to type and size of anchor bolts and studs.

        - Bushing Assemblies for Wall-Mounted Equipment Anchorage: Assemblies of neoprene elements and steel sleeves designed for rigid equipment mountings, and matched to type and size of attachment devices used.

        - Resilient Isolation Washers and Bushings: One-piece, molded, oil- and water-resistant neoprene, with a flat washer face.

      - POST-INSTALLED CONCRETE ANCHORS

        - Mechanical Anchor Bolts:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Drilled-in and stud-wedge or female-wedge type in zinc-coated steel for interior applications and stainless steel for exterior applications. Select anchor bolts with strength required for anchor and as tested according to ASTM E488/E488M.

        - Adhesive Anchor Bolts:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Drilled-in and capsule anchor system containing PVC or urethane methacrylate-based resin and accelerator, or injected polymer or hybrid mortar adhesive. Provide anchor bolts and hardware with zinc-coated steel for interior applications and stainless steel for exterior applications. Select anchor bolts with strength required for anchor and as tested according to ASTM E488/E488M.

        - Provide post-installed concrete anchors that have been prequalified for use in wind-load applications. Post-installed concrete anchors must comply with all requirements of [ASCE/SEI 7-05, Ch. 13] [ASCE/SEI 7-10, Ch. 13] [ASCE/SEI 7-16, Ch. 13].

          - Prequalify post-installed anchors in concrete in accordance with ACI 355.2 or other approved qualification testing procedures.

          - Prequalify post-installed anchors in masonry in accordance with approved qualification procedures.

Retain paragraph below if ASCE/SEI 7-05 applies.

        - Expansion-type anchor bolts are not permitted for equipment in excess of 10 hp (7.46 kW) that is not vibration isolated.

          - Undercut expansion anchors are permitted.

      - CONCRETE INSERTS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Provide preset concrete inserts that are seismically prequalified in accordance with ICC-ES AC466 testing.

        - Comply with ANSI/MSS SP-58.

- EXECUTION

      - EXAMINATION

        - Examine areas and equipment to receive vibration isolation[ and wind-force-restraint] devices for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

        - Examine roughing-in of reinforcement and cast-in-place anchors to verify actual locations before installation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - APPLICATIONS

        - Multiple Pipe Supports: Secure pipes to trapeze member with clamps approved for application by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction].

Retain "Hanger-Rod Stiffeners" Paragraph below if wind-force restraint is required. Indicate on Drawings, in schedules, or a combination of both, the locations where hanger rods for individual pipes and hanger rods for trapeze hangers require hanger-rod stiffeners.

        - Hanger-Rod Stiffeners: Install where indicated or scheduled on Drawings to receive them and where required to prevent buckling of hanger rods due to high wind forces.

Retain "Strength of Support and Restraint Assemblies" Paragraph below where wind restraints are used.

        - Strength of Support and Restraint Assemblies: Where not indicated, select sizes of components so strength is adequate to carry static and wind load within specified loading limits.

      - INSTALLATION OF VIBRATION-CONTROL [AND WIND-LOAD-RESTRAINT ]DEVICES

        - Provide vibration-control devices for systems and equipment where indicated in Equipment Schedules or Fire-Suppression Vibration Isolation [and Wind-Load-Restraints ]Schedule, where indicated on Drawings, or where the Specifications indicate they are to be installed on specific equipment and systems.

Retain first paragraph below where wind restraints are used.

        - Provide wind-load-restraint devices for systems and equipment where indicated in Equipment Schedules or Vibration Isolation [and Wind-Load-Restraints ]Schedules, where indicated on Drawings, where the Specifications indicate they are to be installed on specific equipment and systems, and where required by applicable codes.

        - Coordinate location of embedded connection hardware with supported equipment attachment and mounting points and with requirements for concrete reinforcement and formwork specified in Section 033000 "Cast-in-Place Concrete."

        - Installation of vibration isolators[ and wind-load restraints] must not cause any stresses, misalignment, or change of position of equipment or piping.

        - Comply with requirements in Section 077200 "Roof Accessories" for installation of equipment supports and roof penetrations.

        - Equipment Restraints:

Indicate type and quantity of snubbers and wind-load-restraint devices described in three subparagraphs below, on Drawings, or in Fire-Suppression Vibration Isolation and Wind Load Restraints Schedule on Drawings.

          - Install snubbers on fire-suppression equipment mounted on vibration isolators. Locate snubbers as close as possible to vibration isolators and bolt to equipment base and supporting structure.

          - Install resilient bolt isolation washers on equipment anchor bolts where clearance between anchor and adjacent surface exceeds 0.125 inch (3.2 mm).

        - Piping Restraints:

          - Comply with all requirements in NFPA 13.

          - Design piping sway bracing according to NFPA 13.

            - Maximum spacing of all sway bracing to be no greater than indicated in NFPA 13.

            - Design loading of all sway bracing not to exceed values indicated in NFPA 13.

Retain first paragraph below if wind-load restraints are required.

        - Install wind-load-restraint devices using methods approved by [an evaluation service member of ICC-ES] [OSHPD] [an agency acceptable to authorities having jurisdiction] that provides required submittals for component.

        - Install bushing assemblies for anchor bolts for floor-mounted equipment, arranged to provide resilient media between anchor bolt and mounting hole in concrete base.

        - Install bushing assemblies for mounting bolts for wall-mounted equipment, arranged to provide resilient media where equipment or equipment-mounting channels are attached to wall.

        - Attachment to Structure: If specific attachment is not indicated, anchor bracing to structure at flanges of beams, at upper truss chords of bar joists, or at concrete members.

        - Post-Installed Concrete Anchors:

          - Identify position of reinforcing steel and other embedded items prior to drilling holes for anchors. Do not damage existing reinforcing or embedded items during coring or drilling. Notify the structural engineer if reinforcing steel or other embedded items are encountered during drilling. Locate and avoid prestressed tendons, electrical and telecommunications conduit, and gas lines.

          - Do not drill holes in concrete or masonry until concrete, mortar, or grout has achieved full design strength.

          - Mechanical-Type Anchor Bolts: Protect threads from damage during anchor installation. Heavy-duty sleeve anchors shall be installed with sleeve fully engaged in the structural element to which anchor is to be fastened.

          - Adhesive-Type Anchor Bolts: Clean holes to remove loose material and drilling dust prior to installation of adhesive. Place adhesive in holes proceeding from the bottom of the hole and progressing toward the surface in such a manner as to avoid introduction of air pockets in the adhesive.

          - Set anchors to manufacturer's recommended torque, using a torque wrench.

          - Install zinc-coated steel anchors for interior and stainless steel anchors for exterior applications.

      - ACCOMMODATION OF DIFFERENTIAL STRUCTURAL MOTION

Coordinate this article with Drawings.

        - Install flexible connections in piping where they cross structural construction joints and other points where differential movement may occur, where adjacent sections or branches are supported by different structural elements, and where the connections terminate with connection to equipment that is anchored to a different structural element from the one supporting the connections as they approach equipment. Comply with requirements in Section 211200 "Fire-Suppression Standpipes," Section 211313 "Wet-Pipe Sprinkler Systems," and Section 211316 "Dry-Pipe Sprinkler Systems" for piping flexible connections.

      - ADJUSTING

        - Adjust isolators after system is at operating weight.

        - Adjust limit stops on restrained-spring isolators to mount equipment at normal operating height. After equipment installation is complete, adjust limit stops so they are out of contact during normal operation.

      - FIELD QUALITY CONTROL

Retain first option in "Testing Agency" Paragraph below if Owner will hire an independent testing agency.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain "Manufacturer's Field Service" Paragraph below to require a factory-authorized service representative to perform tests and inspections.

        - Manufacturer's Field Service: Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

        - Tests and Inspections:

          - Provide evidence of recent calibration of test equipment by a testing agency acceptable to authorities having jurisdiction.

          - Schedule test with Owner, through Architect, before connecting anchorage device to restrained component (unless postconnection testing has been approved), and with at least seven days' advance notice.

          - Obtain Architect's approval before transmitting test loads to structure. Provide temporary load-spreading members.

          - Test at no fewer than [four] <Insert number> of each type and size of installed anchors and fasteners selected by Architect.

          - Test to 90 percent of rated proof load of device.

          - Measure isolator restraint clearance.

          - Measure isolator deflection.

          - Verify snubber minimum clearances.

        - Remove and replace malfunctioning units and retest as specified above.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Units will be considered defective if they do not pass tests and inspections.

        - Prepare test and inspection reports.

END OF SECTION 210548.13