Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 211119 – FIRE DEPARTMENT CONNECTIONS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Exposed-type fire-department connections.

          - Flush-type fire-department connections.

          - Yard-type fire-department connections.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

          - Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for each fire-department connection.

- PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

      - EXPOSED-TYPE FIRE-DEPARTMENT CONNECTION

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Standard: UL 405.

        - Type: Exposed, projecting, for wall mounting.

        - Pressure Rating: 175 psig (1200 kPa) minimum.

        - Body Material: Corrosion-resistant metal.

        - Inlets: Brass with threads according to NFPA 1963 and matching local fire-department sizes and threads. Include extension pipe nipples, brass lugged swivel connections, and check devices or clappers.

        - Caps: Brass, lugged type, with gasket and chain.

        - Escutcheon Plate: Round, brass, wall type.

        - Outlet: Back, with pipe threads.

        - Number of Inlets: [Two] [Three].

Retain first option in "Escutcheon Plate Marking" Paragraph below if standpipes supply a sprinkler system.

        - Escutcheon Plate Marking: Similar to "[AUTO SPKR & STANDPIPE] [STANDPIPE]."

        - Finish: [Polished chrome plated] [Rough brass or bronze] [Rough chrome plated].

        - Outlet Size: [NPS 4 (DN 100)] [NPS 5 (DN 125)] [NPS 6 (DN 150)].

      - FLUSH-TYPE FIRE-DEPARTMENT CONNECTION

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Standard: UL 405.

        - Type: Flush, for wall mounting.

        - Pressure Rating: 175 psig (1200 kPa) minimum.

        - Body Material: Corrosion-resistant metal.

        - Inlets: Brass with threads according to NFPA 1963 and matching local fire-department sizes and threads. Include extension pipe nipples, brass lugged swivel connections, and check devices or clappers.

        - Caps: Brass, lugged type, with gasket and chain.

        - Escutcheon Plate: Rectangular, brass, wall type.

        - Outlet: With pipe threads.

        - Body Style: [Horizontal] [Square] [Vertical].

        - Number of Inlets: [Two] [Three] [Four] [Six].

        - Outlet Location: [Back] [Bottom] [Left side] [Right side] [Top].

Retain first option in "Escutcheon Plate Marking" Paragraph below if standpipes supply a sprinkler system.

        - Escutcheon Plate Marking: Similar to "[AUTO SPKR & STANDPIPE] [STANDPIPE]."

        - Finish: [Polished chrome plated] [Rough brass or bronze] [Rough chrome plated].

        - Outlet Size: [NPS 4 (DN 100)] [NPS 5 (DN 125)] [NPS 6 (DN 150)] [NPS 8 (DN 200)].

      - YARD-TYPE FIRE-DEPARTMENT CONNECTION

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Standard: UL 405.

        - Type: Exposed, freestanding.

        - Pressure Rating: [175 psig (1200 kPa) minimum] [300 psig (2070 kPa)].

        - Body Material: Corrosion-resistant metal.

        - Inlets: Brass with threads according to NFPA 1963 and matching local fire-department sizes and threads. Include extension pipe nipples, brass lugged swivel connections, and check devices or clappers.

        - Caps: Brass, lugged type, with gasket and chain.

        - Escutcheon Plate: Round, brass, floor type.

        - Outlet: Bottom, with pipe threads.

        - Number of Inlets: [Two] [Three] [Four].

        - Sleeve: [Brass] [Not required].

        - Sleeve Height: 18 inches (460 mm).

Retain first option in "Escutcheon Plate Marking" Paragraph below if standpipes supply a sprinkler system.

        - Escutcheon Plate Marking: Similar to "[AUTO SPKR & STANDPIPE] [STANDPIPE]."

        - Finish[, Including Sleeve]: [Polished chrome plated] [Rough brass or bronze] [Rough chrome plated].

        - Outlet Size: [NPS 4 (DN 100)] [NPS 5 (DN 125)] [NPS 6 (DN 150)].

- EXECUTION

      - EXAMINATION

        - Examine conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of fire-department connections.

        - Examine roughing-in for fire-suppression standpipe system to verify actual locations of piping connections before fire-department connection installation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - Install wall-type fire-department connections.

        - Install yard-type fire-department connections in concrete slab support. Comply with requirements for concrete in Section 033000 "Cast-in-Place Concrete."

        - Install [two] [three] <Insert number> protective pipe bollards [around] [on sides of] each fire-department connection. Comply with requirements for bollards in Section 055000 "Metal Fabrications."

        - Install automatic (ball-drip) drain valve at each check valve for fire-department connection.

END OF SECTION 211119