Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 211213 - FIRE-SUPPRESSION HOSES AND NOZZLES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - NPS 1-1/2 (DN 40) rack-type hose stations.

          - NPS 1-1/2 by NPS 2-1/2 (DN 40 by DN 65) rack-type hose stations.

          - NPS 1-1/2 (DN 40) reel-type hose stations.

          - Monitors.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 104413 "Fire Protection Cabinets" for hose cabinets.

          - Section 211200 "Fire-Suppression Standpipes" for fire hose valves.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

          - Include construction details, material descriptions, dimensions of individual components and profiles, and finishes.

        - Shop Drawings:

          - Include plans, elevations, sections, and mounting and attachment details.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For each product type to include in operation and maintenance manuals.

- PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

      - NPS 1-1/2 (DN 40) RACK-TYPE HOSE STATIONS

Coordinate cabinet-mounted units with requirements in Section 104413 "Fire Protection Cabinets."

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Hose Rack:

          - Standard: UL 47.

          - Material: [Brass or bronze with polished chrome-plated] [Steel with red-enamel] finish.

          - Type: Hose-rack assembly. Include hose valve, hose rack, water-retention device, hose pins, and hose.

          - Operation: Semiautomatic.

          - Sized to hold fire hose.

        - Hose Valve:

          - Standard: UL 668, NPS 1-1/2 (DN 40), for connecting fire hose.

If retaining first option in "Type" Subparagraph below, also retain pressure-control device and insert outlet pressure setting in appropriate subparagraphs below.

          - Type: [Adjustable] [Nonadjustable].

          - Pressure-Control Device: [Pressure reducing] [or] [pressure restricting].

          - Design Outlet Pressure Setting: [Not applicable] <Insert psig (kPa)>.

          - Hose Valve and Trim Finish: [Polished chrome-plated] [Rough brass or bronze] [Rough chrome-plated].

          - Pressure Rating: 300 psig (2070 kPa) minimum.

          - Pattern: Angle.

          - Material: Brass or bronze.

          - Pressure-Control Device: UL 1468 integral or for field installation if indicated.

          - Size: NPS 1-1/2 (DN 40).

          - Inlet: Female pipe threads.

          - Outlet: Male hose threads according to NFPA 1963 and matching local fire-department threads.

        - Hose:

          - Standards: NFPA 1961 and UL 219 lined fire hose with swivel inlet, coupling, gaskets, and nozzle.

          - Size: NPS 1-1/2 (DN 40).

          - Length: [50 feet (15 m)] [75 feet (23 m)] [100 feet (30 m)] <Insert dimension>.

          - Jacket: [Combination of natural and synthetic threads] [Natural thread] [Synthetic thread].

          - Lining: [Rubber, plastic, or combination of rubber and plastic compounds] [Combination of rubber and plastic compounds] [Rubber compound] [Plastic compound].

          - Cover: Rubber, plastic, or combination of rubber and plastic compounds.

          - Nozzle: UL 401.

            - Material: [Brass] [Polished brass] [Rough chrome-plated brass] [Polished chrome-plated brass] [Polycarbonate plastic].

            - Type: [Plain, for nonadjustable water stream] [Spray, adjustable from shutoff to fog spray or straight stream] [Spray, adjustable from shutoff to full fog; for use on electrical fires].

      - NPS 1-1/2 BY NPS 2-1/2 (DN 40 BY DN 65) RACK-TYPE HOSE STATIONS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Hose Rack:

          - Standard: UL 47.

          - Material: [Brass or bronze with polished chrome-plated] [Steel with red-enamel] finish.

          - Type: Hose-rack assembly. Include hose valve, reducer adapter, hose rack, water-retention device, hose pins, and hose.

          - Operation: Semiautomatic.

          - Sized to hold fire hose.

        - Hose Valve:

          - Standard: UL 668, NPS 2-1/2 (DN 65), for connecting fire hose.

If retaining first option in "Type" Subparagraph below, also retain pressure-control device and insert outlet pressure setting in appropriate subparagraphs below.

          - Type: [Adjustable] [Nonadjustable].

          - Pressure-Control Device: [Pressure reducing] [or] [pressure restricting].

          - Design Outlet Pressure Setting: [Not applicable] <Insert psig (kPa)>.

          - Hose Valve and Trim Finish: [Polished chrome-plated] [Rough brass or bronze] [Rough chrome-plated].

          - Pressure Rating: 300 psig (2070 kPa) minimum.

          - Pattern: Angle.

          - Material: Brass or bronze.

          - Pressure-Control Device: UL 1468, integral or for field installation if indicated.

          - Size: NPS 2-1/2 (DN 65).

          - Inlet: Female pipe threads.

          - Outlet: Male hose threads according to NFPA 1963 and matching local fire-department threads.

          - Reducer Adapter: NPS 2-1/2 by NPS 1-1/2 (DN 65 by DN 40).

        - Hose:

          - Standards: NFPA 1961 and UL 219, lined fire hose with swivel inlet, coupling, gaskets, and nozzle.

          - Size: NPS 1-1/2 (DN 40).

          - Length: [50 feet (15 m)] [75 feet (23 m)] [100 feet (30 m)] <Insert dimension>.

          - Jacket: [Combination of natural and synthetic threads] [Natural thread] [Synthetic thread].

          - Lining: [Rubber, plastic, or combination of rubber and plastic compounds] [Combination of rubber and plastic compounds] [Rubber compound] [Plastic compound].

          - Cover: Rubber, plastic, or combination of rubber and plastic compounds.

          - Nozzle: UL 401 spray nozzle unless plain nozzle is indicated.

            - Material: [Brass] [Polished brass] [Rough chrome-plated brass] [Polished chrome-plated brass] [Polycarbonate plastic].

            - Type: [Plain, for nonadjustable water stream] [Spray, adjustable from shutoff to fog spray or straight stream] [Spray, adjustable from shutoff to full fog; for use on electrical fires].

      - NPS 1-1/2 (DN 40) REEL-TYPE HOSE STATIONS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Hose Reel:

          - Standard: UL 47.

          - Hose Reel and Bracket Material: Steel.

          - Type: Hose-reel assembly. Include hose valve, wall bracket, hose reel, water-retention device, hose pins, and hose.

          - Operation: Semiautomatic.

          - Sized to hold fire hose.

          - Finish: Red enamel.

        - Hose Valve:

          - Standard: UL 668, NPS 1-1/2 (DN 40), for connecting fire hose.

If retaining first option in "Type" Subparagraph below, also retain pressure-control device and insert outlet pressure setting in appropriate subparagraphs below.

          - Type: [Adjustable] [Nonadjustable].

          - Pressure-Control Device: [Pressure reducing] [or] [pressure restricting].

          - Design Outlet Pressure Setting: [Not applicable] <Insert psig (kPa)>.

          - Hose Valve and Trim Finish: [Polished chrome-plated] [Rough brass or bronze] [Rough chrome-plated].

          - Pressure Rating: 300 psig (2070 kPa) minimum.

          - Pattern: Angle.

          - Material: Brass or bronze.

          - Pressure-Control Device: UL 1468, integral or for field installation if indicated.

          - Size: NPS 1-1/2 (DN 40).

          - Inlet: Female pipe threads.

          - Outlet: Male hose threads according to NFPA 1963 and matching local fire-department threads.

        - Hose:

          - Standards: NFPA 1961 and UL 219 lined fire hose with swivel inlet, coupling, gaskets, and nozzle.

          - Size: NPS 1-1/2 (DN 40).

          - Length: [50 feet (15 m)] [75 feet (23 m)] [100 feet (30 m)] <Insert dimension>.

          - Jacket: [Combination of natural and synthetic threads] [Natural thread] [Synthetic thread].

          - Lining: [Rubber, plastic, or combination of rubber and plastic compounds] [Combination of rubber and plastic compounds] [Rubber compound] [Plastic compound].

          - Cover: Rubber, plastic, or combination of rubber and plastic compounds.

          - Nozzle: UL 401.

            - Material: [Brass] [Polished brass] [Rough chrome-plated brass] [Polished chrome-plated brass] [Polycarbonate plastic].

            - Type: Spray, adjustable from shutoff to [fog spray or straight stream] [full fog; for use on electrical fires].

      - MONITORS

Currently, no UL standard exists for monitors.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Type: Stationary.

        - Nozzle: UL 401, NPS 2-1/2 (DN 65), brass, adjustable from fog spray to straight stream to shutoff.

        - Horizontal Rotation: 360 degrees with locking device.

        - Vertical Rotation: 80-degree elevation and 60-degree depression with locking device.

        - Waterway: [Double] [Single] brass or stainless-steel tube.

        - Waterway Size: [NPS 2-1/2 (DN 65)] <Insert value> minimum.

        - Water Stream Flow: [500 gpm (31.5 L/s)] [750 gpm (47.3 L/s)] [1000 gpm (63 L/s)] <Insert value>.

        - Operation: [Lever] [Wheel].

        - Base Inlet Size: [NPS 2-1/2 (DN 65)] [NPS 3 (DN 80)] [NPS 4 (DN 100)].

        - Finish: Red-painted body with brass trim.

- EXECUTION

      - EXAMINATION

        - Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of fire hoses, reels, racks, and monitors.

        - Examine roughing-in for standpipe systems to verify actual locations of piping connections before installation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - HOSE-STATION INSTALLATION

Indicate hose-station locations, sizes, and special devices on Drawings.

        - Install freestanding hose stations for access and minimum passage restriction.

        - Install NPS 1-1/2 (DN 40) hose-station valves with flow-restricting device unless otherwise indicated.

        - Install NPS 2-1/2 (DN 65) hose connections with quick-disconnect NPS 2-1/2 by NPS 1-1/2 (DN 65 by DN 40) reducer adapter and flow-restricting device unless otherwise indicated.

        - Install freestanding hose stations with support or bracket attached to standpipe.

        - Install wall-mounted, rack hose stations in cabinets. Include pipe escutcheons, with finish matching valves, inside cabinet where water-supply piping penetrates cabinet. Install valves at angle required for connection of fire hose. Comply with requirements for cabinets in Section 104413 "Fire Protection Cabinets."

        - Install hose-reel hose stations on wall with bracket.

      - MONITOR INSTALLATION

        - Install monitors on standpipe piping.

END OF SECTION 211213