Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 220533 - HEAT TRACING FOR PLUMBING PIPING

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Access Manufacturer-Provided, AIA MasterSpec-Based Sections:

<Double click here for this Section based on specific manufacturer’s products set as Basis-of-Design at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section includes heat tracing of plumbing piping for freeze prevention [and, domestic hot-water-temperature maintenance] with self-regulating, parallel-resistance electric heating cables:

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 210533 "Heat Tracing for Fire-Suppression Piping."

          - Section 230533 "Heat Tracing for HVAC Piping."

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data: For each type of product.

          - Include rated capacities, operating characteristics, and furnished specialties and accessories.

          - Schedule heating capacity, length of cable, spacing, and electrical power requirement for each electric heating cable required.

        - Shop Drawings: For electric heating cable.

          - Include plans, elevations, sections, and attachment details.

          - Include diagrams for power, signal, and control wiring.

      - INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

        - Sample warranties.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For electric heating cables and controls to include in operation and maintenance manuals.

      - WARRANTY

When warranties are required, verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

        - Special Warranty: Manufacturer agrees to repair or replace electric heating cable that fails in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for electric heating cable. Special warranties often exclude labor.

          - Warranty Period: [Three] [Five] [10] <Insert number> years from date of Substantial Completion.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - SELF-REGULATING, PARALLEL-RESISTANCE HEATING CABLES

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain all heat tracing from one manufacturer.

        - Standard: IEEE 515.1.

        - Heating Element: Pair of parallel [No. 16] [No. 18] AWG, [tinned] [nickel-coated], stranded copper bus wires embedded in crosslinked conductive polymer core, which varies heat output in response to temperature along its length.

        - Electrical Insulating Jacket: Flame-retardant polyolefin.

        - Grounding Cover: [Copper] [Tinned-copper] braid.

Outer jacket in "Cable Cover" Paragraph below is optional feature and is required for waterproof applications; verify availability with manufacturer.

        - Cable Cover: Polyolefin outer jacket with ultraviolet inhibitor.

        - Terminate cable with waterproof, factory-assembled, nonheating leads with connectors at one end, and seal the opposite end watertight. Cable is to be capable of crossing over itself once without overheating.

        - Maximum Operating Temperature (Power On): [150 deg F (65 deg C)] <Insert temperature>.

Verify temperature of circulated media in freeze-protected piping in "Maximum Exposure Temperature (Power Off)" Paragraph below.

        - Maximum Exposure Temperature (Power Off): [185 deg F (85 deg C)] <Insert temperature>.

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70 by a qualified testing agency, and marked for intended location and application.

If Project has more than one type or configuration of electric heating cable, delete "Capacities and Characteristics" Paragraph below and schedule on Drawings. See the Evaluations for a sample schedule.

        - Capacities and Characteristics:

          - Maximum Heat Output: [3 W/ft. (9.8 W/m)] [5 W/ft. (16.4 W/m)] [8 W/ft. (26 W/m)] [10 W/ft. (32.8 W/m)] [12 W/ft. (39.4 W/m)] <Insert value>.

          - Piping Diameter: <Insert NPS (DN)>.

          - Number of Parallel Cables: <Insert number>.

          - Spiral Wrap Pitch: <Insert inches (mm)>.

          - Electrical Characteristics for Single-Circuit Connection:

Verify available voltages and heat-output ratings with manufacturer.

            - Volts: [120] [208] [240] [277] [480] <Insert number> V.

            - Phase: <Insert value>.

            - Hertz: <Insert number> Hz.

            - Full-Load Amperes: <Insert number> A.

            - Minimum Circuit Ampacity: <Insert number> A.

            - Maximum Overcurrent Protection: <Insert number> A.

      - CONTROLS

Retain "Pipe-Mounted Thermostats for Freeze Protection" Paragraph below to control electric heating cable for pipe-mounted freeze protection.

        - Pipe-Mounted Thermostats for Freeze Protection:

          - Remote bulb temperature control unit with adjustable range from [30 to 50 deg F (minus 1 to plus 10 deg C)] <Insert temperature range>.

          - Snap action; open-on-rise, single-pole switch with minimum current rating adequate for connected cable.

          - Remote temperature-sensing bulb on capillary, resistance temperature device, or thermistor for directly sensing outside air or pipe-wall temperature.

          - Corrosion-resistant, waterproof control enclosure.

        - Control Panel:

          - [Microprocessor-based] [Automatic] control with manual on, automatic, and standby/reset switch.

          - Remote temperature sensor senses outside air temperature; programmable to energize the freeze-protection cable when temperature falls below [34 to 44 deg F (1 to 7 deg C)] <Insert temperature range>.

Retain first subparagraph below if pipe-heating cable for domestic hot-water-temperature maintenance is utilized.

          - Remote temperature sensor senses domestic hot water temperature: programmable to control the domestic hot water temperature at [110 to 120 deg F (47 to 53 deg C)] <Insert temperature range>.

          - Corrosion-proof and waterproof enclosure suitable for outdoor mounting, for controls and temperature sensors.

          - Minimum 30 A contactor to energize cable or close other contactors.

          - Ground-fault protection.

          - Single-point control of heat tracing for freeze protection[ and domestic hot-water-temperature maintenance].

Where Project includes a central HVAC-control system, coordinate subparagraph below with the HVAC-control system to interface operational status and on/off control.

          - Provide communication ports with contacts, RS485, or Ethernet interface for remote monitoring and alarm by central HVAC-control system. Coordinate type of connection ports with Section 230923 "Direct Digital Control (DDC) System for HVAC."

Programmable timer operates domestic hot-water-temperature maintenance cable during occupied periods. Where the Project includes a central HVAC-control system, coordinate this specification Section with the HVAC-control system to interface operational status and on/off control. It may be practical to assign cable on/off function to the central HVAC-control system and delete the local programmable timer.

        - Programmable Timer for Domestic Hot-Water-Temperature Maintenance:

          - Microprocessor based.

          - Minimum of four separate schedules.

          - Minimum 24-hour battery carryover.

          - On-off-auto switch.

          - 365-day calendar with 20 programmable holidays.

          - Relays with contacts to indicate operational status, on or off, and for interface with central HVAC-control system.

      - ACCESSORIES

        - Cable Installation Accessories: Fiberglass tape, heat-conductive putty, cable ties, silicone end seals and splice kits, and installation clips all furnished by manufacturer, or as recommended in writing by manufacturer.

Retain "Warning Labels" or "Warning Tape" Paragraph below.

        - Warning Labels: See Section 220553 "Identification for Plumbing Piping and Equipment."

        - Warning Tape: Continuously printed "Electrical Tracing"; vinyl, at least 3 mils (0.08 mm) thick, and with pressure-sensitive, permanent, waterproof, self-adhesive back.

          - Width for Markers on Pipes with OD, Including Insulation, Less Than 6 Inches (150 mm): 3/4 inch (19 mm) minimum.

          - Width for Markers on Pipes with OD, Including Insulation, 6 Inches (150 mm) or Larger: 1-1/2 inches (38 mm) minimum.

- EXECUTION

      - EXAMINATION

        - Examine surfaces and substrates to receive electric heating cables for compliance with requirements for installation tolerances and other conditions affecting performance.

          - Ensure surfaces and pipes in contact with electric heating cables are free of burrs and sharp protrusions.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

Indicate location of heating cables and controls on Drawings.

        - Install electric heating cable at locations indicated and in accordance with NFPA 70.

        - Install electric heating cable across expansion, construction, and control joints in accordance with manufacturer's written instructions; use cable-protection conduit and slack cable to allow movement without damage to cable.

        - Install electric heating cables after piping has been tested and before insulation is installed.

        - Install electric heating cables in accordance with IEEE 515.1.

        - Install insulation over piping with electric cables in accordance with Section 220719 "Plumbing Piping Insulation."

        - Install warning tape on piping insulation where piping is equipped with electric heating cables.

        - Set field-adjustable switches and circuit-breaker trip ranges.

        - Install temperature-control units in an accessible location and in accordance with manufacturer's written instructions. Locate sensing bulbs to sense outside air temperature in a location where it will not be affected by direct sunlight or other heat sources.

If control panels are used, retain first paragraph below. Indicate locations on Drawings and provide detail to indicate sensor quantities and locations.

        - Install control panels and distribution panels where indicated and in accordance with manufacturer's written instructions.

        - Install and connect outside air and pipe temperature sensors.

      - ELECTRICAL CONNECTIONS

        - Ground equipment in accordance with Section 260526 "Grounding and Bonding for Electrical Systems."

        - Connect wiring in accordance with Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

        - Connect temperature-control unit for freeze protection to interrupt power supply to electric heating cable when outside air is above set point.

        - Connect temperature-control unit for domestic hot-water-temperature maintenance to interrupt power supply to electric heating cable when hot water is above set point.

        - Connect remote electronic temperature sensors.

      - FIELD QUALITY CONTROL

Retain first option in "Testing Agency" Paragraph below if Owner hires an independent testing agency.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain "Manufacturer's Field Service" Paragraph below to require a factory-authorized service representative to perform tests and inspections.

        - Manufacturer's Field Service: Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

        - Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

          - Perform tests after cable installation but before application of coverings, such as insulation, wall or ceiling construction, or concrete.

          - Test cables for electrical continuity and insulation integrity before energizing.

          - Test cables to verify rating and power input. Energize and measure voltage and current simultaneously.

        - Repeat tests for continuity, insulation resistance, and input power after applying thermal insulation on pipe-mounted cables.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Cables will be considered defective if they do not pass tests and inspections.

        - Prepare test and inspection reports.

      - PROTECTION

        - Protect installed heating cables, including nonheating leads, from damage.

        - Remove and replace damaged heat-tracing cables.

END OF SECTION 220533