Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 221423 - STORM DRAINAGE PIPING SPECIALTIES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Access Manufacturer-Provided, AIA MasterSpec-Based Sections:

<Double click here for this Section based on specific manufacturer’s products set as Basis-of-Design at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - General-purpose roof drains.

          - Promenade roof drains.

          - Deck roof drains

          - Miscellaneous storm drainage piping specialties.

          - Cleanouts.

          - Backwater valves.

          - Trench drains.

          - Channel drainage systems.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 076200 "Sheet Metal Flashing and Trim" for penetrations of roofs.

          - Section 078413 "Penetration Firestopping" for firestopping roof penetrations.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

          - General-purpose roof drains.

          - Promenade roof drains.

          - Deck roof drains.

          - Miscellaneous storm drainage piping specialties.

          - Cleanouts.

          - Backwater valves.

          - Trench drains.

          - Channel drainage systems.

      - QUALITY ASSURANCE

        - Provide drainage piping specialties are to bear label, stamp, or other markings of specified testing agency.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - GENERAL-PURPOSE ROOF DRAINS

Copy this article and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product. Not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers.

        - Cast-Iron Roof Drains:

Roof drains in "Cast-Iron, Large-Sump, General-Purpose Roof Drains" Subparagraph below are available in NPS 2 to NPS 10 (DN 50 to DN 250).

          - Cast-Iron, Large-Sump, General-Purpose Roof Drains: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.6.4.

            - Body Material: Cast iron.

            - Dimension of Body: Nominal [14-to 16-inch (357- to 406-mm)] <Insert dimension> diameter.

            - Dome Material: [Aluminum] [Cast iron] [PE] [Bronze] <Insert material>.

            - Combination flashing ring and gravel stop.

Side outlets are only available in limited number of outlet types. Consult manufacturers.

            - Outlet: [Bottom] [Side] <Insert location>.

            - Outlet Type: [No-hub] [Inside caulk] [Threaded] <Insert type>.

In "Options" Subparagraph below, not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers. Retain options below to suit Project.

            - Options:

              - Flow-control weirs.

              - Extension collars.

              - Underdeck clamp.

              - Expansion joint.

              - Sump receiver plate.

              - Perforated Gravel Guard: Stainless steel.

              - Vandal-proof dome.

              - Water Dam: [2 inches (50 mm) high] <Insert height>.

              - <Insert option>.

Roof drains in "Cast-Iron, Medium-Sump, General-Purpose Roof Drains" Subparagraph below are available in at least NPS 2 to NPS 6 (DN 50 to DN 150).

          - Cast-Iron, Medium-Sump, General-Purpose Roof Drains: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.6.4.

            - Body Material: Cast iron.

            - Dimension of Body: [8- to 12-inch (203- to 305-mm)] <Insert dimension> diameter.

            - Dome Material: [Aluminum] [Cast iron] [PE] [Bronze] <Insert material>.

            - Combination flashing ring and gravel stop.

Side outlets are only available in limited number of outlet types. Consult manufacturers.

            - Outlet: [Bottom] [Side] <Insert location>.

            - Outlet Type: [No-hub] [Inside caulk] [Threaded] <Insert type>.

In "Options" Subparagraph below, not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers. Retain options below to suit Project.

            - Options:

              - Flow-control weirs.

              - Extension collars.

              - Underdeck clamp.

              - Expansion joint.

              - Sump Receiver plate.

              - Wire Mesh: Stainless steel or brass over dome.

              - Perforated Gravel Guard: Stainless steel.

              - Vandal-proof dome.

              - Water Dam: [2 inches (50 mm) high] <Insert height>.

              - <Insert option>.

Roof drains in "Cast-Iron, Small-Sump, General-Purpose Roof Drains" Subparagraph below are available in NPS 2 to NPS 4 (DN 50 to DN 100).

          - Cast-Iron, Small-Sump, General-Purpose Roof Drains: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.6.4.

            - Body Material: Cast iron.

            - Dimension of Body: Nominal [8-inch (203-mm)] <Insert dimension> diameter.

            - Dome Material: [Cast iron] <Insert material>.

            - Combination flashing ring and gravel stop.

Side outlets are only available in limited number of outlet types. Consult manufacturers.

            - Outlet: [Bottom] [Side] <Insert location>.

            - Outlet Type: [No-hub] [Inside caulk] [Threaded] <Insert type>.

In "Options" Subparagraph below, not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers. Retain options below to suit Project.

            - Options:

              - Extension collars.

              - Underdeck clamp.

              - Expansion joint.

              - Sump receiver plate.

              - Wire Mesh: Stainless steel or brass over dome.

              - Vandal-proof dome.

              - <Insert option>.

Roof drains in "Cast-Iron Cornice and Gutter Roof Drains" Subparagraph below are available in at least NPS 2 to NPS 3 (DN 50 to DN 75). If only one type is required, drawing designation may be omitted.

          - Cast-Iron Cornice and Gutter Roof Drains: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.6.4.

            - Body Material: Cast iron

            - Dimension of Body: Nominal 6-inch (152-mm) diameter.

            - Dome Material: [Bronze] <Insert material and finish>.

            - Outlet: [Bottom] [Side] [45-degree angle].

            - Outlet Type: [Threaded] <Insert type>.

In "Options" Subparagraph below, not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers. Retain options below to suit Project.

            - Options:

              - Wire Mesh: Stainless steel or brass over dome.

              - Vandal-Proof Dome.

              - <Insert option>.

Roof drains in "Cast-Iron Parapet Roof Drains" Subparagraph below are available in at least NPS 2 to NPS 4 (DN 50 to DN 100).

Parapet roof drains may also be referred to as scupper drains.

          - Cast-Iron Parapet Roof Drains: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.6.4.

            - Body Material: Cast iron.

            - Grate Material: [Bronze] [Cast iron] [Nickel-bronze alloy] <Insert material>.

            - Outlet: [Back] [Angle] <Insert location>.

            - Outlet Type: [Threaded] <Insert type>.

In "Options" Subparagraph below, not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers. Retain options below to suit Project.

            - Options:

              - Wire Mesh: Stainless steel or brass over grate.

              - Vandal-proof grate.

              - <Insert option>.

        - Copper Roof Drains:

Roof drains in "Copper, Medium-Sump, General-Purpose Roof Drains" Subparagraph below are available in at least NPS 2 to NPS 6 (DN 50 to DN 150).

          - Copper, Medium-Sump, General-Purpose Roof Drains: <Insert drawing designation if any>

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.6.4.

            - Drain Body and Flange Material: Copper.

            - Dimension of Body: [8- to 12-inch (203- to 305-mm)] <Insert dimension> diameter.

            - Dome Material: [Aluminum] <Insert material>.

            - Combination flashing ring and gravel stop.

Side outlets are only available in limited number of outlet types. Consult manufacturers.

            - Outlet: [Bottom] [Side] <Insert location>.

            - Outlet Type: [Threaded] <Insert type>.

In "Options" Subparagraph below, not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers. Retain options below to suit Project.

            - Options:

              - Extension collars.

              - Underdeck clamp.

              - Expansion joint.

              - Sump receiver plate.

              - Wire Mesh: Stainless steel or brass over dome.

              - Perforated Gravel Guard: Stainless steel.

              - Vandal-proof dome.

              - Water Dam: [2 inches (50 mm) high] <Insert height>.

              - <Insert option>.

Roof drains in "Copper, Small-Sump, General-Purpose Roof Drains" Subparagraph below are available in NPS 2 to NPS 4 (DN 50 to DN 100).

          - Copper, Small-Sump, General-Purpose Roof Drains: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.6.4.

            - Body Material: Copper.

            - Dimension of Body: Nominal [8-inch (203-mm)] <Insert dimension> diameter.

            - Dome Material: [Aluminum] <Insert material>.

            - Outlet: [Bottom] <Insert location>.

            - Outlet Type: [O-ring] <Insert type>.

In "Options" Subparagraph below, not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers. Retain options below to suit Project.

            - Options:

              - Vandal-proof dome.

              - <Insert option>.

        - Aluminum Roof Drains:

Roof drains in "Aluminum, Small-Sump, General-Purpose Roof Drains" Subparagraph below are available in NPS 3 and NSP 4 (DN 75 and DN 100). Some manufacturers also offer NPS 2, NPS 5, and NPS 6 (DN 50, DN 125, and DN 150).

          - Aluminum, Small-Sump, General-Purpose Roof Drains: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.6.4.

            - Body Material: Aluminum.

            - Dimension of Body: Nominal [6-inch (150-mm)] <Insert dimension> diameter.

            - Dome Material: Aluminum.

            - Outlet: [Bottom] <Insert location>.

            - Outlet Type: [O-ring or mechanical seal] <Insert type>.

In "Options" Subparagraph below, not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers. Retain options below to suit Project.

            - Options:

              - Vandal-proof dome.

              - <Insert option>.

        - Plastic Roof Drains:

Roof drains in "Plastic General-Purpose Roof Drains" Subparagraph below are available in at least NPS 2 to NPS 4 (DN 50 to DN 100).

          - Plastic General-Purpose Roof Drains: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.6.4.

            - Body Material: [ABS] [or] [PVC] <Insert material>.

            - Sump Diameter: <Insert nominal dimension>.

            - Dome Material: [Aluminum] [Cast iron] [Plastic] <Insert material>.

            - Outlet: [Bottom] <Insert location>.

            - Outlet Type: <Insert type>.

In "Options" Subparagraph below, not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers. Retain options below to suit Project.

            - Options:

              - Combination flashing ring and gravel stop.

              - Extension collars.

              - Underdeck clamp.

              - Expansion joint.

              - Sump receiver plate.

              - Vandal-proof dome.

              - <Insert option>.

      - PROMENADE ROOF DRAINS

Copy this article and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Cast-Iron Promenade Roof Drains:

Roof drains in "Cast-Iron, Large-Sump, Promenade Roof Drains" Subparagraph below are available in NPS 2 to NPS 6 (DN 50 to DN 150).

          - Cast-Iron, Large-Sump, Promenade Roof Drains: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.6.4.

            - Body Material: Cast iron.

            - Dimension of Body: Nominal [12- to 14-inch (305- to 357-mm)] <Insert dimension> diameter.

            - Dimension of Frame and Grate: Nominal [12 to 14 inches (305 to 357 mm)] <Insert dimension> square.

            - Grate Material: [Bronze] [Cast iron] [Nickel-bronze alloy] <Insert material>.

Side outlets are available in a limited number of outlet types. Consult manufacturers.

            - Outlet: [Bottom] [Side].

            - Outlet Type: [No-hub] [Inside caulk] [Threaded] <Insert type>.

In "Options" Subparagraph below, not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers. Retain options below to suit Project.

            - Options:

              - Extension collars.

              - Underdeck clamp.

              - Expansion joint.

              - Sump receiver plate.

              - Vandal-proof grate.

              - <Insert option>.

Roof drains in "Cast-Iron, Medium-Sump, Promenade Roof Drains" Subparagraph below are available in NPS 2 to NPS 6 (DN 50 to DN 150).

          - Cast-Iron, Medium-Sump, Promenade Roof Drains: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.6.4.

            - Body Material: Cast iron.

            - Dimension of Body: [11- to 12-inch (280- to 305-mm)] <Insert dimension> diameter.

            - Dimension of Frame and Grate: Nominal [12 inches (305 mm)] <Insert dimension> square.

            - Grate Material: [Bronze] [Cast iron] [Nickel-bronze alloy] <Insert material>.

Side outlets are available in a limited number of outlet types. Consult manufacturers.

            - Outlet: [Bottom] [Side].

            - Outlet Type: [No-hub] [Inside caulk] [Threaded] <Insert type>.

In "Options" Subparagraph below, not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers. Retain options below to suit Project.

            - Options:

              - Extension collars.

              - Underdeck clamp.

              - Expansion joint.

              - Sump receiver plate.

              - Vandal-proof grate.

              - <Insert option>.

Roof drains in "Cast-Iron, Small-Sump, Promenade Roof Drains" Subparagraph below are available in NPS 2 to NPS 4 (DN 50 to DN 100).

          - Cast-Iron, Small-Sump, Promenade Roof Drains: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.6.4.

            - Body Material: Cast iron.

            - Dimension of Body: Nominal [8-inch (203-mm)] <Insert dimension> diameter.

            - Dimension of Frame and Grate: Nominal [8 inches (203 mm)] <Insert dimension> square.

            - Grate Material: [Bronze] [Cast iron] [Nickel-bronze alloy] <Insert material>.

            - Outlet: Bottom.

            - Outlet Type: [No-hub] [Inside caulk] [Threaded] <Insert type>.

In "Options" Subparagraph below, not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers. Retain options below to suit Project.

            - Options:

              - Extension collars.

              - Underdeck clamp.

              - Expansion joint.

              - Sump receiver plate.

              - Vandal-proof grate.

              - <Insert option>.

      - DECK ROOF DRAINS

Copy this article and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Cast-Iron Deck Roof Drains:

Roof drains in "Cast-Iron, Medium-Sump, Deck Roof Drains" Subparagraph below are available in NPS 2 to NPS 6 (DN 50 to DN 150).

          - Cast-Iron, Medium-Sump, Deck Roof Drains: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.6.4.

            - Body Material: Cast iron.

            - Overall Dimension of Frame and Grate: Nominal [12 to 14 inches (305 to 357 mm)] <Insert dimension> [round] [square].

            - Top-Loading Classification: [Heavy Duty] <Insert duty>.

            - Grate Material: [Cast or ductile iron] <Insert material>.

            - Flange: [Anchor] [Anchor with weep holes] [Not required].

Side outlets are only available in limited number of outlet types. Consult manufacturers.

            - Outlet: [Bottom] [Side] <Insert location>.

            - Outlet Type: [No-hub] [Inside caulk] [Threaded] <Insert type>.

In "Options" Subparagraph below, not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers. Retain options below to suit Project.

            - Options:

              - Clamping device.

              - Backwater valve.

              - Grate Finish: <Insert finish>.

              - Vandal-proof frame and grate.

              - <Insert option>.

Roof drains in "Metal, Small-Sump, Deck Roof Drains" Subparagraph below are available in NPS 2 to NPS 4 (DN 50 to DN 100).

          - Metal, Small-Sump, Deck Roof Drains: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.6.4.

            - Body Material: [Cast iron] [or] [Copper]

            - Overall Dimension of Frame and Grate: Nominal [8 inches (203 mm)] <Insert dimension> [round] [square].

            - Top-Loading Classification: <Insert duty>.

            - Grate Material: [Cast or ductile iron] <Insert material>.

            - Flange: [Anchor] [Anchor with weep holes] [Not required].

Side outlets are only available in limited number of outlet types. Consult manufacturers.

            - Outlet: [Bottom] [Side] <Insert location>.

            - Outlet Type: [No-hub] [Inside caulk] [Threaded] <Insert type>.

In "Options" Subparagraph below, not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers. Retain options below to suit Project.

            - Options:

              - Clamping device.

              - Grate Finish: <Insert finish>.

              - Vandal-proof frame and grate.

              - <Insert option>.

      - MISCELLANEOUS STORM DRAINAGE PIPING SPECIALTIES

Copy this article and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

In "Downspout Adapters" Paragraph below, adapters are available with NPS 2 to NPS 6 (DN 50 to DN 150) inlets and several downspout connection sizes.

        - Downspout Adapters: <Insert drawing designation if any>.

          - Description: Manufactured, gray-iron casting, for attaching to horizontal-outlet, parapet roof drain and to exterior sheet metal downspout.

          - Size: Inlet size to match parapet drain outlet.

In "Downspout Boots" Paragraph below, boots are generally available with inlet dimensions of 4 by 3 and 5 by 4 inches (102 by 76 and 127 by 102 mm), respectively, and of 4 inches (102 mm) in diameter. Outlet is NPS 4 (DN 100).

        - Downspout Boots: <Insert drawing designation if any>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Manufactured, ASTM A48/A48M, gray-iron casting, with strap or ears for attaching to building; NPS 4 (DN 100) outlet; and shop-applied bituminous coating.

          - Size: Inlet size to match downspout and NPS 4 (DN 100) outlet.

In "Metal Downspout Nozzles" Paragraph below, nozzles are generally available in NPS 2 to NPS 10 (DN 50 to DN 250).

        - Metal Downspout Nozzles: <Insert drawing designation if any>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Nozzle with wall flange and mounting holes to cover rough opening and serve as anchor.

          - Size: Same as connected downspout.

          - Material: Cast bronze or nickel bronze nozzle and flange.

In "Piping Connection" Subparagraph below, not all manufacturers offer each connection type. Consult manufacturers.

          - Piping Connection Type: [Threaded] [No-hub] [or] [slip on].

          - Finish: <Insert type>.

          - Opening Protection: [Birdscreen] [None].

        - Metal Downspout Nozzles with PVC Insert: <Insert drawing designation if any>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Nozzle with wall flange and mounting holes to cover rough opening and serve as anchor.

          - Size: Same as connected downspout.

          - Material: Cast nickel brass, with integral PVC insert.

          - Piping Connection Type: Solvent welded.

          - Finish: Nickel brass.

          - Opening Protection: [Birdscreen] [None].

In "Polymer Downspout Nozzles" Paragraph below, nozzles are generally available in NPS 3, NPS 4, and NPS 6 (DN 75, DN 100, and DN 150).

        - Polymer Downspout Nozzles <Insert drawing designation if any>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Nozzle with wall flange and mounting holes to cover rough opening and serve as anchor.

          - Size: Same as connected downspout.

          - Material: High-impact, marine-grade polymer.

          - Piping Connection Type: Solvent welded.

          - Finish: Simulated oil-rubbed bronze.

      - CLEANOUTS

Copy this article and re-edit for each product.

If more than one configuration of each cleanout is required, insert drawing designation. Use these designations on Drawings to identify each product. Not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers.

        - Cast-Iron Cleanouts:

          - Cast-Iron Exposed Cleanouts: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.36.2M.

            - Size: Same as connected branch.

            - Body Material: [Hub-and-spigot, cast-iron soil pipe T-branch] [No-hub, cast-iron soil pipe test tee] as required to match connected piping.

            - Closure: [Countersunk] [Countersunk or raised-head] [Raised head], [brass] [cast-iron] [plastic] plug.

            - Closure Plug Size: Same as, or not more than, one size smaller than cleanout size.

          - Cast-Iron Exposed Floor Cleanouts: <Insert drawings designation, if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.36.2M.

            - Size: Same as connected branch.

            - Type: [Adjustable housing] [Cast-iron soil pipe with cast-iron ferrule] [Heavy-duty, adjustable housing] [Threaded, adjustable housing].

            - Body or Ferrule: Cast iron.

            - Outlet Connection: [No-hub] [Hub with inside caulk] [Hub with gasket] [Threaded].

            - Closure: [Brass plug with straight threads and gasket] [Brass plug with tapered threads] [Cast-iron plug] [Plastic plug].

            - Adjustable Housing Material: [Cast iron] [Plastic] <Insert material> with [threads] [setscrews or other device].

            - Frame and Cover Material and Finish: [Nickel-bronze, copper alloy] [Painted cast iron] [Polished bronze] [Rough bronze] <Insert material and finish>.

            - Frame and Cover Shape: [Round] [Square] <Insert shape>.

            - Top Loading Classification: [Extra-Heavy] [Heavy] [Light] [Medium] Duty.

            - Riser: ASTM A74, [Extra-Heavy] [Service] Class, cast-iron drainage pipe fitting and riser to cleanout.

In "Options" Subparagraph below, not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers. Retain options below to suit Project.

            - Options:

              - Clamping device.

              - <Insert option>.

          - Cast-Iron Wall Cleanouts: <Insert drawing designation, if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.36.2M. Include wall access.

            - Size: Same as connected drainage piping.

            - Body: [Hub-and-spigot, cast-iron soil pipe T-branch] [No-hub, cast-iron soil pipe test tee] as required to match connected piping.

            - Closure Plug:

              - Material: [Brass] [Cast iron].

              - Head: [Countersunk] [or] [raised].

              - Drilled and threaded for cover attachment screw.

              - Size: Same as, or not more than, one size smaller than cleanout size.

Retain "Wall-Access Cover Plate" Subparagraph below for cover plate; retain "Wall-Access Frame and Cover" Subparagraph for frame and cover to be installed in drywall.

            - Wall-Access Cover Plate: Round, [deep, chrome-plated bronze] [flat, chrome-plated brass or stainless steel] cover plate with screw.

            - Wall-Access Frame and Cover: [Round] [Square], [nickel-bronze, copper-alloy, or stainless steel] <Insert material> wall-installation frame and cover.

          - Cast-Iron Test Tees: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.36.2M and ASTM A74, ASTM A888, or CISPI 301.

            - Size: Same as connected drainage piping.

            - Body Material: Hub-and-spigot, cast-iron soil-pipe T-branch or no-hub, cast-iron soil-pipe test tee as required to match connected piping.

            - Closure Plug: [Countersunk] [or] [raised head], [brass] <Insert material>.

            - Closure Plug Size: Same as, or not more than, one size smaller than cleanout size.

        - Plastic Cleanouts:

          - Plastic Cleanouts: <Insert drawing designation, if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Size: Same as connected branch.

            - Body Material: [PVC] [ABS].

            - Closure Plug: [PVC] [ABS] <Insert type>.

            - Type: [Wall] [and] [floor].

            - Frame and Cover Material and Finish: [Nickel-bronze, copper alloy] [Polished bronze] [Rough bronze] <Insert material and finish>.

            - Frame and Cover Shape: [Round] [Square] <Insert shape>.

            - Riser: Drainage pipe fitting and riser to cleanout of same material as drainage piping.

      - BACKWATER VALVES

Copy this article and re-edit for each product.

If more than one configuration of each valve is required, insert drawing designation. Use these designations on Drawings to identify each product.

        - Cast-Iron Backwater Valves:

          - Cast-Iron, Horizontal Backwater Valves: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.14.1.

            - Size: Same as connected piping.

            - Body Material: Cast iron.

            - Cover: Cast iron with [bolted] [or] [threaded] to access check valve.

            - End Connections: Hub and spigot or no-hub.

            - Check Valve: Removable, bronze, swing check, factory assembled or field modified to hang [closed] [open for airflow unless subject to backflow condition].

            - Extension: ASTM A74, Service Class; full-size, cast-iron soil-pipe extension to field-installed cleanout at floor; replaces backwater valve cover.

          - Cast-Iron, Drain-Outlet Backwater Valves: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.14.1.

            - Size: Same as floor drain outlet.

            - Body Material: Cast iron or bronze made for vertical installation in bottom outlet of floor drain.

            - Check Valve: Removable ball float.

            - Inlet: Threaded or no-hub.

            - Outlet: Threaded, no-hub, or spigot.

Plastic backwater valves in "Plastic, Horizontal Backwater Valves" Paragraph below are available in NPS 2 to NPS 6 (DN 50 to DN 150). Most are made of PVC.

        - Plastic, Horizontal Backwater Valves:

          - Plastic, Horizontal Backwater Valves: <Insert drawing designation if any>.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASME A112.14.1.

            - Size: Same as connected piping.

            - Body Material: [ABS] [PVC].

            - Cover: Same material as body with threaded access to check valve.

            - Check Valve: Removable swing check.

            - End Connections: Socket type.

      - TRENCH DRAINS

Copy this article and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Trench Drains: <Insert drawing designation if any>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: ASME A112.6.3.

          - Body Material: [Cast iron] <Insert material>.

          - Dimensions of Frame and Grate: <Insert dimensions: Include those for body, sump, and grate if required>.

          - Top-Loading Classification: [Extra-Heavy] [Heavy] [Light] [Medium] Duty.

          - Grate Material: [Ductile iron] [Cast iron] [or] [stainless steel] <Insert material>.

          - Grate Finish: [Painted] [Not required] <Insert finish>.

          - Flange: [Anchor] [Seepage] [Not required].

          - Outlet: [Bottom] [End] [Side] <Insert location>.

          - Outlet Type: [Inside caulk] <Insert type>.

In "Options" Subparagraph below, not all manufacturers offer all options and not all options are available in each combination. Consult manufacturers. Retain options below to suit Project.

          - Options:

            - Clamping device.

            - <Insert option>.

      - CHANNEL DRAINAGE SYSTEMS

Copy this article and re-edit for each product.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Narrow, Sloped-Invert, Polymer-Concrete, Channel Drainage Systems: <Insert drawing designation if any>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Modular system of channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

            - Channel Sections: Narrow, interlocking-joint, sloped-invert, polymer-concrete modular units with end caps.

              - Include rounded bottom, with built-in invert slope of 0.6 percent and with outlets in number, sizes, and locations indicated.

              - Include extension sections necessary for required depth.

              - Dimensions: [5-inch (127-mm)] <Insert dimension> inside width and [9-3/4-inch (248-mm)] <Insert dimension> inside depth. Include number of units required to form total lengths indicated.

              - Frame: [Galvanized steel or cast iron for grates] [Not required] <Insert material>.

            - Grates: Manufacturer's designation "[Heavy] [Medium] Duty," with slots or perforations, and of width and thickness that fit recesses in channel sections.

              - Material: [Ductile iron] [Fiberglass] [Galvanized steel] [Cast iron] [Stainless steel] <Insert material>.

              - Locking Mechanism: [Manufacturer's standard device for securing grates to channel sections] [Not required].

Indicate locations and lengths of covers on Drawings.

            - Covers: Solid [ductile or cast iron] <Insert material>, of width and thickness that fit recesses in channel sections, and of lengths indicated.

            - Supports, Anchors, and Setting Devices: Manufacturer's standard unless otherwise indicated.

            - Channel-Section Joining and Fastening Materials: As recommended by system manufacturer.

        - Narrow, Level-Invert, Polymer-Concrete, Channel Drainage Systems: <Insert drawing designation if any>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Modular system of channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

            - Channel Sections: Narrow, interlocking-joint, precast, polymer-concrete modular units with end caps.

              - Include rounded bottom, with level invert and with outlets in number, sizes, and locations indicated.

              - Dimensions: [5-inch (127-mm)] <Insert dimension> inside width and [9-3/4-inch (248-mm)] <Insert dimension> inside depth. Include number of units required to form total lengths indicated.

              - Frame: [Galvanized steel or cast iron for grates] [Not required] <Insert material>.

            - Grates: Manufacturer's designation "[Heavy] [Medium] Duty," with slots or perforations, and of width and thickness that fit recesses in channel sections.

              - Material: [Ductile iron] [Fiberglass] [Galvanized steel] [Cast iron] [Stainless steel] <Insert material>.

              - Locking Mechanism: [Manufacturer's standard device for securing grates to channel sections] [Not required].

Indicate locations and lengths of covers on Drawings.

            - Covers: Solid [ductile or cast iron] <Insert material>, of width and thickness that fit recesses in channel sections, and of lengths indicated.

            - Supports, Anchors, and Setting Devices: Manufacturer's standard unless otherwise indicated.

            - Channel-Section Joining and Fastening Materials: As recommended by system manufacturer.

        - Wide, Level-Invert, Polymer-Concrete, Channel Drainage Systems: <Insert drawing designation if any>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Modular system of channel sections, grates, and appurtenances; designed so grates fit into channel recesses without rocking or rattling.

            - Channel Sections: Wide, interlocking-joint, precast, polymer-concrete modular units with end caps.

              - Include flat or rounded bottom, with level invert and with outlets in number, sizes, and locations indicated.

              - Dimensions: [8-inch (203-mm)] <Insert dimension> inside width and [13-3/4-inch (350-mm)] <Insert dimension> inside depth. Include number of units required to form total lengths indicated.

              - Frame: [Galvanized steel or cast iron for grates] [Not required] <Insert material>.

            - Grates: Manufacturer's designation "[Heavy] [Medium] Duty," with slots or perforations, and of width and thickness that fit recesses in channel sections.

              - Material: [Ductile iron] [Fiberglass] [Galvanized steel] [Cast iron] [Stainless steel] <Insert material>.

              - Locking Mechanism: [Manufacturer's standard device for securing grates to channel sections] [Not required].

Indicate locations and lengths of covers on Drawings.

            - Covers: Solid [ductile or cast iron] <Insert material>, of width and thickness that fit recesses in channel sections, and of lengths indicated.

            - Supports, Anchors, and Setting Devices: Manufacturer's standard unless otherwise indicated.

            - Channel-Section Joining and Fastening Materials: As recommended by system manufacturer.

- EXECUTION

      - INSTALLATION

Additional instructions may be required for special applications. Indicate locations of specialties in plans, details, and schematics on Drawings.

        - Install roof drains in accordance with roof membrane manufacturer's written installation instructions at low points of roof areas.

          - Install flashing collar or flange of roof drain to maintain integrity of waterproof membranes where penetrated.

          - Install expansion joints, if indicated, in roof drain outlets.

          - Position roof drains for easy access and maintenance.

        - Install downspout adapters on outlet of back-outlet parapet roof drains and connect to sheet metal downspouts.

        - Install downspout boots at grade with top [6 inches (152 mm)] [12 inches (305 mm)] [18 inches (457 mm)] <Insert dimension> above grade. Secure to building wall.

        - Install downspout nozzles at exposed bottom of conductors where they spill onto grade.

        - Install cleanouts in aboveground piping and building drain piping in accordance with the following instructions unless otherwise indicated:

          - Use cleanouts the same size as drainage piping up to NPS 4 (DN 100). Use NPS 4 (DN 100) for larger drainage piping unless larger cleanout is indicated.

          - Locate cleanouts at each change in direction of piping greater than 45 degrees.

          - Locate cleanouts at minimum intervals of [50 ft. (15 m)] <Insert dimension> for piping NPS 4 (DN 100) and smaller and 100 ft. (30 m) for larger piping.

          - Locate cleanouts at base of each vertical storm piping conductor.

        - For floor cleanouts for piping below floors, install cleanout deck plates with top flush with finished floor.

        - For cleanouts located in concealed piping, install cleanout wall access covers, of types indicated, with frame and cover flush with finished wall.

        - Install horizontal backwater valves in floor with cover flush with floor.

        - Install drain-outlet backwater valves in outlet of drains.

        - Install test tees in vertical conductors and near floor.

        - Install wall cleanouts in vertical conductors. Install access door in wall if indicated.

        - Install trench drains at low points of surface areas to be drained. Set grates of drains flush with finished surface unless otherwise indicated.

        - Assemble channel drainage system components in accordance with manufacturer's written instructions. Install on support devices so that top will be flush with adjacent surface.

        - Install through-penetration firestop assemblies for penetrations of fire- and smoke-rated assemblies.

          - Comply with requirements in Section 078413 "Penetration Firestopping."

      - CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Comply with requirements for piping specified in Section 221414 "Storm Drainage Piping." Drawings indicate general arrangement of piping, fittings, and specialties.

      - INSTALLATION OF FLASHING

        - Fabricate flashing from single piece of metal unless large pans, sumps, or other drainage shapes are required.

        - Install sheet flashing on pipes, sleeves, and specialties passing through or embedded in floors and roofs with waterproof membrane.

        - Set flashing on floors and roofs in solid coating of bituminous cement.

        - Secure flashing into sleeve and specialty clamping ring or device.

      - CLEANING

        - Clean piping specialties during installation and remove dirt and debris as work progresses.

      - PROTECTION

        - Protect piping specialties during remainder of construction period to avoid clogging with dirt or debris and to prevent damage from traffic and construction work.

        - Place plugs in ends of uncompleted piping at end of each day and when work stops.

END OF SECTION 221423