Copyright 2022 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 221429 - SUMP PUMPS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Access Manufacturer-Provided, AIA MasterSpec-Based Sections:

<Double click here for this Section based on specific manufacturer’s products set as Basis-of-Design at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

Terminology and descriptions for pumps used in this Section are from HI 14.1-14.2.

          - Sump pumps - submersible.

          - Sump pumps - wet-pit volute.

          - Oil-sensing sump pumps and controllers.

          - Sump pumps - pedestal.

          - Sump-pump basins and basin covers.

          - Packaged drainage-pump units - submersible.

        - Related Requirements:

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 221329 "Sanitary Sewerage Pumps" for effluent and sewage pumps.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

          - Sump pumps - submersible.

          - Sump pumps - wet-pit volute.

          - Oil-sensing sump pumps and controllers.

          - Sump pumps - pedestal.

          - Sump-pump basins and basin covers.

          - Packaged drainage-pump units - submersible.

        - Product Data Submittals: For each product.

          - Construction details, material descriptions, dimensions of individual components and profiles.

          - Rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

        - Shop Drawings:

          - Include plans, elevations, sections, and [mounting] [attachment] details.

          - Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

          - Include diagrams for power, signal, and control wiring.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For pumps and controls.

          - Indicate actual installed items by marking submittals with an arrow or box.

      - DELIVERY, STORAGE, AND HANDLING

        - Retain shipping flange protective covers and protective coatings during storage.

        - Protect bearings and couplings against damage.

        - Comply with manufacturer's written instructions for handling.

      - WARRANTY

When warranties are required and available, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

        - Manufacturer Warranty: [Manufacturer agrees] [Installer agrees] [Manufacturer and Installer agree] to repair or replace sump pumps that fail in materials or workmanship within specified warranty period.

          - Failures include, but are not limited to, the following:

            - Faulty operation of <Insert components>.

            - Deterioration of metals, metal finishes, and other materials beyond normal [weathering] [use].

            - <Insert conditions relating to specified products>.

            - <Insert failure modes>.

Verify warranty periods for sump pumps and components.

          - Warranty Period: [1] <Insert number> year(s) from date of Substantial Completion.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

If Project has more than one type or configuration of sump pump and/or sump-pump basin/cover, copy appropriate article and re-edit for each product. Alternately, a schedule can be provided on Drawings or in the Specifications. See sample schedules in the Evaluations.

      - SOURCE LIMITATIONS

        - Obtain each type of sump pump from single source from single manufacturer.

      - PERFORMANCE REQUIREMENTS

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by an NRTL, and marked for intended location and use.

        - UL Compliance: Comply with UL 778 for motor-operated water pumps.

      - SUMP PUMPS - SUBMERSIBLE

Retain "Sump-Pump Basins and Basin Covers" Article if retaining this article.

Insert drawing designation. Use these designations on Drawings to identify each product.

If Project has more than one type or configuration of sump pump, coordinate first paragraph below with schedule on Drawings. See sample sump-pump schedule in the Evaluations.

        - Sump Pumps - Submersible, Fixed Position, Single Seal: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Factory-assembled and -tested sump-pump unit.

          - Pump Type: Submersible, end-suction, single-stage, close-coupled, overhung-impeller, centrifugal sump pump as defined in HI 14.1-14.2 and HI 14.3.

          - Pump Casing: Cast iron, with strainer inlet; legs that elevate pump to permit flow into impeller; and vertical discharge for piping connection.

Insert text in "Impeller" Subparagraph below if other than manufacturer's standard material is required for a specific application. If each manufacturer's standard material is acceptable, retain "(manufacturer's standard)" option. Verify that manufacturers have alternative material.

          - Impeller: Statically and dynamically balanced, [manufacturer's standard] <Insert material> designed for clear wastewater handling, and keyed and secured to shaft.

          - Pump and Motor Shaft: Stainless steel[ or steel], with factory-sealed, grease-lubricated ball bearings.

          - Seal: Mechanical.

          - Motor: Hermetically sealed, capacitor-start type; with built-in overload protection; lifting eye or lug; and three-conductor, waterproof power cable of length required and with grounding plug and cable-sealing assembly for connection at pump.

Verify that pump selected has motor feature in "Motor Housing Fluid" Subparagraph below, if either option is required, or delete subparagraph.

            - Motor Housing Fluid: [Air] [Oil].

          - Capacities and Characteristics:

            - Unit Capacity: <Insert gpm (L/min.)>.

            - Number of Pumps: [One] [Two] <Insert number>.

            - Each Pump:

              - Capacity: <Insert gpm (L/min.)>.

              - Total Dynamic Head: <Insert feet (kPa)>.

              - Speed: <Insert rpm>.

              - Discharge Size: <Insert NPS (DN)>.

              - Electrical Characteristics:

                - Motor Horsepower: <Insert value> hp.

                - Volts: [120] [240] [277] [480] <Insert value> V ac.

                - Phases: [Single] [Three].

                - Hertz: 60.

            - Unit Electrical Characteristics:

              - Full-Load Amperes: <Insert value> A.

              - Minimum Circuit Ampacity: <Insert value> A.

              - Maximum Overcurrent Protection: <Insert value> A.

Retain "Controls, Rod-and-Float Type" or "Controls, Float- and Pressure-Switch Type" Subparagraph below.

          - Controls, Rod-and-Float Type:

            - Enclosure: NEMA 250, [Type 1] [Type 4X] <Insert type>.

            - Switch Type: Pedestal-mounted float switch with float rods and rod buttons.

Retain "Automatic Alternator" Subparagraph below for duplex pump units. Revise if unit includes three or more pumps.

            - Automatic Alternator: Start pumps on successive cycles and start multiple pumps if one cannot handle load.

            - Float Guides: Pipe or other restraint for floats and rods in basins of depth greater than 60 inches (1500 mm).

            - High-Water Alarm: Cover-mounted, compression-probe alarm, with electric bell; 120 V ac, with transformer and contacts for remote alarm bell.

          - Controls, Float- and Pressure-Switch Type:

            - Enclosure: NEMA 250, [Type 1] [Type 4X] <Insert type>; [pedestal] [wall] mounted.

            - Switch Type: [Mechanical-float] [Mercury-float] [Pressure] <Insert type> type, in NEMA 250, Type 6 enclosures with mounting rod and electric cables.

Retain "Automatic Alternator" Subparagraph below for duplex pump units. Revise if unit includes three or more pumps.

            - Automatic Alternator: Start pumps on successive cycles and start multiple pumps if one cannot handle load.

            - High-Water Alarm: Rod-mounted, NEMA 250, Type 6 enclosure with [mechanical-float, mercury-float, or pressure] <Insert type> switch matching control and electric bell; 120 V ac, with transformer and contacts for remote alarm bell.

Retain "Control-Interface Features" Subparagraph below for optional features if applicable to Project.

          - Control-Interface Features:

            - Remote Alarm Contacts: For remote alarm interface.

            - Building Automation System Interface: Auxiliary contacts in pump controls for interface to building automation system and capable of providing the following:

              - On-off status of pump.

              - Alarm status.

        - Sump Pumps - Submersible, Fixed Position, Double Seal: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Factory-assembled and -tested sump-pump unit.

          - Pump Type: Submersible, end-suction, single-stage, close-coupled, overhung-impeller, centrifugal sump pump as defined in HI 14.1-14.2 and HI 14.3.

          - Pump Casing: Cast iron, with strainer inlet; legs that elevate pump to permit flow into impeller; and vertical discharge for piping connection.

Insert text in "Impeller" Subparagraph below if other than manufacturer's standard material is required for a specific application. If each manufacturer's standard material is acceptable, retain "(manufacturer's standard)" option. Verify that manufacturers have alternative material.

          - Impeller: Statically and dynamically balanced, [manufacturer's standard] <Insert material> designed for clear wastewater handling, and keyed and secured to shaft.

          - Pump and Motor Shaft: Stainless steel[ or steel], with factory-sealed, grease-lubricated ball bearings.

          - Seals: Mechanical.

Verify that pump selected has feature in "Moisture-Sensing Probe" Subparagraph below, if required, or delete subparagraph.

          - Moisture-Sensing Probe: Internal moisture sensor and moisture alarm.

          - Motor: Hermetically sealed, capacitor-start type; with built-in overload protection; lifting eye or lug; and three-conductor, waterproof power cable of length required and with grounding plug and cable-sealing assembly for connection at pump.

Verify that pump selected has motor feature in "Motor Housing Fluid" Subparagraph below, if either option is required, or delete subparagraph.

            - Motor Housing Fluid: [Air] [Oil].

          - Unit Capacity: <Insert gpm (L/min.)>.

            - Number of Pumps: [One] [Two] <Insert number>.

            - Each Pump:

              - Capacity: <Insert gpm (L/min.)>.

              - Total Dynamic Head: <Insert feet (kPa)>.

              - Speed: <Insert rpm>.

              - Discharge Size: <Insert NPS (DN)>.

              - Electrical Characteristics:

                - Motor Horsepower: <Insert value> hp.

                - Volts: [120] [240] [277] [480] <Insert value> V ac.

                - Phases: [Single] [Three].

                - Hertz: 60.

            - Unit Electrical Characteristics:

              - Full-Load Amperes: <Insert value> A.

              - Minimum Circuit Ampacity: <Insert value> A.

              - Maximum Overcurrent Protection: <Insert value> A.

Retain "Controls, Rod-and-Float Type" or "Controls, Float- and Pressure-Switch Type" Subparagraph below.

          - Controls, Rod-and-Float Type:

            - Enclosure: NEMA 250, [Type 1] [Type 4X] <Insert type>.

            - Switch Type: Pedestal-mounted float switch with float rods and rod buttons.

Retain "Automatic Alternator" Subparagraph below for duplex pump units. Revise if unit includes three or more pumps.

            - Automatic Alternator: Start pumps on successive cycles and start multiple pumps if one cannot handle load.

            - Float Guides: Pipe or other restraint for floats and rods in basins of depth greater than 60 inches (1500 mm).

            - High-Water Alarm: Cover-mounted, compression-probe alarm, with electric bell; 120 V ac, with transformer and contacts for remote alarm bell.

          - Controls, Float- and Pressure-Switch Type:

            - Enclosure: NEMA 250, [Type 1] [Type 4X] <Insert type>; [pedestal] [wall] mounted.

            - Switch Type: [Mechanical-float] [Mercury-float] [Pressure] <Insert type> type, in NEMA 250, Type 6 enclosures with mounting rod and electric cables.

Retain "Automatic Alternator" Subparagraph below for duplex pump units. Revise if unit includes three or more pumps.

            - Automatic Alternator: Start pumps on successive cycles and start multiple pumps if one cannot handle load.

            - High-Water Alarm: Rod-mounted, NEMA 250, Type 6 enclosure with [mechanical-float, mercury-float, or pressure] <Insert type> switch matching control and electric bell; 120 V ac, with transformer and contacts for remote alarm bell.

Retain "Control-Interface Features" Subparagraph below for optional features if applicable to Project.

          - Control-Interface Features:

            - Remote Alarm Contacts: For remote alarm interface.

            - Building Automation System Interface: Auxiliary contacts in pump controls for interface to building automation system and capable of providing the following:

              - On-off status of pump.

              - Alarm status.

      - SUMP PUMPS - WET-PIT VOLUTE

Retain "Sump-Pump Basins and Basin Covers" Article if retaining this article.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Sump Pumps - Wet-Pit Volute: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Factory-assembled and -tested sump-pump unit.

          - Pump Type: Wet-pit-volute, single-stage, separately coupled, overhung-impeller, centrifugal sump pump as defined in HI 14.1-14.2 and HI 14.3.

          - Pump Casing: Cast iron, with strainer inlet and threaded connection for NPS 2 (DN 50) and smaller and flanged connection for NPS 2-1/2 (DN 65) and larger discharge piping.

Insert text in "Impeller" Subparagraph below if other than manufacturer's standard material is required for a specific application. If each manufacturer's standard material is acceptable, retain "(manufacturer's standard)" option. Verify that manufacturers have alternative material.

          - Impeller: Statically and dynamically balanced, [manufacturer's standard] <Insert material> designed for clear wastewater handling, and keyed and secured to shaft.

          - Sleeve Bearings: Bronze. Include oil-lubricated, intermediate sleeve bearings at 48-inch- (1200-mm-) maximum intervals if basin depth is more than 48 inches (1200 mm), and grease-lubricated, ball-type thrust bearings.

          - Pump and Motor Shaft Coupling: Flexible, capable of absorbing torsional vibration and shaft misalignment.

          - Pump Discharge Piping: Factory- or field-fabricated, [galvanized, ASTM A53/A53M, Schedule 40, steel pipe with ASME B16.1, Class 125, cast-iron flanges and flanged fittings or ASME B16.4, Class 125, gray-iron threaded fittings] <Insert pipe material>.

          - Support Plate: Cast iron or coated steel; strong enough to support pumps, motors, and controls. See "Sump-Pump Basins and Basin Covers" Article for requirements.

          - Shaft Seal: Stuffing box, with graphite-impregnated braided-yarn rings and bronze packing gland.

          - Motor: Single speed; grease-lubricated ball bearings and mounting on vertical, cast-iron pedestal.

          - Unit Capacity: <Insert gpm (L/min.)>.

            - Number of Pumps: [One] [Two] <Insert number>.

            - Each Pump:

              - Capacity: <Insert gpm (L/min.)>.

              - Total Dynamic Head: <Insert feet (kPa)>.

              - Speed: <Insert rpm>.

              - Discharge Size: <Insert NPS (DN)>.

              - Electrical Characteristics:

                - Motor Horsepower: <Insert value> hp.

                - Volts: [120] [240] [277] [480] <Insert value> V ac.

                - Phases: [Single] [Three].

                - Hertz: 60.

            - Unit Electrical Characteristics:

              - Full-Load Amperes: <Insert value> A.

              - Minimum Circuit Ampacity: <Insert value> A.

              - Maximum Overcurrent Protection: <Insert value> A.

Retain "Controls, Rod-and-Float Type" or "Controls, Float- and Pressure-Switch Type" Subparagraph below.

          - Controls, Rod-and-Float Type:

            - Enclosure: NEMA 250, [Type 1] [Type 4X] <Insert type>.

            - Switch Type: Pedestal-mounted float switch with float rods and rod buttons.

Retain "Automatic Alternator" Subparagraph below for duplex pump units. Revise if unit includes three or more pumps.

            - Automatic Alternator: Start pumps on successive cycles and start multiple pumps if one cannot handle load.

            - Float Guides: Pipe or other restraint for floats and rods in basins of depth greater than 60 inches (1500 mm).

            - High-Water Alarm: Cover-mounted, compression-probe alarm, with electric bell; 120 V ac, with transformer and contacts for remote alarm bell.

          - Controls, Float- and Pressure-Switch Type:

            - Enclosure: NEMA 250, [Type 1] [Type 4X] <Insert type>; [pedestal] [wall] mounted.

            - Switch Type: [Mechanical-float] [Mercury-float] [Pressure] <Insert type> type, in NEMA 250, Type 6 enclosures with mounting rod and electric cables.

Retain "Automatic Alternator" Subparagraph below for duplex pump units. Revise if unit includes three or more pumps.

            - Automatic Alternator: Start pumps on successive cycles and start multiple pumps if one cannot handle load.

            - High-Water Alarm: Rod-mounted, NEMA 250, Type 6 enclosure with [mechanical-float, mercury-float, or pressure] <Insert type> switch matching control and electric bell; 120 V ac, with transformer and contacts for remote alarm bell.

Retain "Control-Interface Features" Subparagraph below for optional features if applicable to Project.

          - Control-Interface Features:

            - Remote Alarm Contacts: For remote alarm interface.

            - Building Automation System Interface: Auxiliary contacts in pump controls for interface to building automation system and capable of providing the following:

              - On-off status of pump.

              - Alarm status.

      - OIL-SENSING SUMP PUMPS AND CONTROLLERS

Oil-sensing sump pumps and controllers are available in a packaged unit and as a control system only. These units are typically used for applications such as elevator sump pits, for transformer containment areas, and for areas where water removal below a layer of oil/hydrocarbons is required. Verify, with authorities having jurisdiction, the acceptability of using this product and regulations on where pump discharge should terminate. Revise this article to suit Project.

Retain "Sump-Pump Basins and Basin Covers" Article if retaining this article.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Oil-Sensing Sump Pumps and Controllers: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Factory-assembled and -tested sump-pump unit. ASME A17.1 compliant.

          - Pump Type: Submersible, end-suction, single-stage, close-coupled, overhung-impeller, centrifugal sump pump as defined in HI 14.1-14.2 and HI 14.3.

          - Pump Casing: Cast iron, with strainer inlet; legs that elevate pump to permit flow into impeller; and vertical discharge for piping connection.

          - Unit Capacity: <Insert gpm (L/min.)>.

            - Number of Pumps: [One] [Two] <Insert number>.

            - Each Pump:

              - Capacity: <Insert gpm (L/min.)>.

              - Total Dynamic Head: <Insert feet (kPa)>.

              - Speed: <Insert rpm>.

              - Discharge Size: <Insert NPS (DN)>.

              - Electrical Characteristics:

                - Motor Horsepower: <Insert value> hp.

                - Volts: [120] [240] [277] [480] <Insert value> V ac.

                - Phases: [Single] [Three].

                - Hertz: 60.

            - Unit Electrical Characteristics:

              - Full-Load Amperes: <Insert value> A.

              - Minimum Circuit Ampacity: <Insert value> A.

              - Maximum Overcurrent Protection: <Insert value> A.

          - Controls:

            - Industrial-grade switch(es) with internal [20] <Insert number> A relay and Type 304 stainless steel sensor probes.

            - Liquid/oil sensor that differentiates and indicates the presence of oil and/or water under high-water conditions.

            - Alarm Panel:

              - High-oil-level alarm.

              - High-water-level alarm.

              - Audible and visual alarms for each alarm condition.

              - Dry contacts for remote monitoring of oil, water, and high liquid conditions.

            - Control Panel:

              - [Simplex] [Duplex].

              - Enclosure: NEMA 250, Type 4X.

              - HOA switch(es).

              - Green pump run light; power on light.

              - Pump circuit breaker(s).

      - SUMP PUMPS - PEDESTAL

Units in this article are complete with a pump and controls, and are typically installed in a pit.

Retain "Sump-Pump Basins and Basin Covers" Article if retaining this article.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Sump Pumps - Pedestal: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Factory-assembled and -tested, automatic-operation, freestanding, sump-pump unit.

          - Pump Type: Wet-pit-volute, single-stage, separately coupled, overhung-impeller centrifugal sump pump, configured as a pedestal pump. Sump pump to be as defined in HI 14.1-14.2 and HI 14.3.

          - Pump Casing: Corrosion-resistant material, with strainer inlet; design that permits flow into impeller; and vertical discharge for piping connection.

          - Impeller: Aluminum, brass, or plastic.

          - Motor: With built-in overload protection and mounted vertically on sump-pump column.

          - Power Cord: Three-conductor waterproof cable of length required, but not less than 72 inches (1830 mm), with grounding plug and cable-sealing assembly for connection at pump.

          - Capacities and Characteristics:

            - Capacity: <Insert gpm (L/min.)>.

            - Total Dynamic Head: <Insert feet (kPa)>.

            - Speed: <Insert rpm>.

            - Discharge Size: <Insert NPS (DN)>.

            - Electrical Characteristics:

              - Motor Horsepower: <Insert value> hp.

              - Volts: [120] [240] [277] [480] <Insert value> V ac.

              - Phases: [Single] [Three].

              - Hertz: 60.

          - Control: Float switch.

      - SUMP-PUMP BASINS AND BASIN COVERS

Retain this article if retaining "Sump Pumps - Submersible," "Sump Pumps - Wet-Pit Volute," or "Sump Pumps - Pedestal" articles.

Insert drawing designation. Use these designations on Drawings to identify each product.

Sump-pump basins are typically round with space for simplex or duplex pumps.

        - Basins <Insert drawing designation>: Factory-fabricated, watertight, cylindrical, basin sump with top flange and sidewall openings for pipe connections.

          - Material: [Cast iron] [Fiberglass] [Polyethylene] <Insert material>.

          - Reinforcement: Mounting plates for pumps, fittings, and accessories.

Retain "Anchor Flange" Subparagraph below if required to anchor basin to concrete slab in case of ground-water problems.

          - Anchor Flange: Same material as or compatible with basin sump, cast in or attached to sump, and in location and of size required to anchor basin in concrete slab.

Sump-pump basin covers are typically round with openings for simplex or duplex pumps.

        - Basin Covers: Fabricate metal cover with openings having gaskets, seals, and bushings; for access to pumps, pump shafts, control rods, discharge piping, vent connections, and power cables.

          - Reinforcement: Steel or cast iron, capable of supporting foot traffic for basins installed in foot-traffic areas.

        - Capacities and Characteristics:

          - Capacity: <Insert gal. (L)>.

          - Diameter: <Insert inches (mm)>.

          - Depth: <Insert inches (mm)>.

          - Inlet No. 1:

            - Drainage Pipe Size: <Insert NPS (DN)>.

            - Bottom of Sump to Centerline: <Insert inches (mm)>.

            - Type: [Flanged] [Hubbed] [Threaded] outside.

          - Inlet No. 2:

            - Drainage Pipe Size: <Insert NPS (DN)>.

            - Bottom of Sump to Centerline: <Insert inches (mm)>.

            - Type: [Flanged] [Hubbed] [Threaded] outside.

          - Inlet No. 3:

            - Drainage Pipe Size: <Insert NPS (DN)>.

            - Bottom of Sump to Centerline: <Insert inches (mm)>.

            - Type: [Flanged] [Hubbed] [Threaded] outside.

          - Sidewall Outlet:

            - Discharge Pipe Size: <Insert NPS (DN)>.

            - Bottom of Sump to Centerline: <Insert inches (mm)>.

            - Type: [Hubbed inside] [Hubbed outside] <Insert type>.

          - Cover Material: [Cast iron] [Steel with bituminous coating] [Cast iron or steel with bituminous coating] <Insert material>.

          - Cover Diameter: <Insert inches (mm)>, but not less than OD of basin top flange.

          - Manhole Required in Cover: [Yes] [No].

          - Vent Size: <Insert NPS (DN)>.

      - PACKAGED DRAINAGE-PUMP UNITS - SUBMERSIBLE

Units in this article are complete with a pump, basin and cover, piping, and controls.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Packaged Drainage-Pump Units - Submersible: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Factory-assembled and -tested, automatic-operation, basin-mounted, sump-pump unit.

          - Pump Type: Submersible, end-suction, single-stage, close-coupled, overhung-impeller centrifugal pump as defined in HI 14.1-14.2 and HI 14.3.

          - Casing: [Metal] <Insert material>.

          - Impeller: [Brass] <Insert material>.

          - Pump Seal: Mechanical.

          - Motor: Hermetically sealed, capacitor-start type, with built-in overload protection.

          - Power Cord: Three-conductor waterproof cable of length required, but not less than 72 inches (1830 mm), with grounding plug and cable-sealing assembly for connection at pump.

          - Pump Discharge Piping: Factory- or field-fabricated, [galvanized, ASTM A53/A53M, Schedule 40, steel pipe with ASME B16.4, Class 125, gray-iron threaded fittings] <Insert pipe material>.

          - Control: Motor-mounted float switch.

          - Basin: Plastic.

          - Capacities and Characteristics:

            - Capacity: <Insert gpm (L/min.)>.

            - Total Dynamic Head: <Insert feet (kPa)>.

            - Speed: <Insert rpm>.

            - Discharge Pipe Size: <Insert NPS (DN)>.

            - Electrical Characteristics:

              - Motor Horsepower: <Insert value> hp.

              - Volts: [120] [240] [277] [480] <Insert value> V.

              - Phases: [Single] [Three].

              - Hertz: 60.

              - Full-Load Amperes: <Insert value> A.

              - Minimum Circuit Ampacity: <Insert value> A.

              - Maximum Overcurrent Protection: <Insert value> A.

            - Basin:

              - Capacity: [2 gal. (7.6 L)] [5 gal. (18.9 L)] <Insert value> minimum.

              - Inlet Connection: [NPS 1-1/2 (DN 40)] <Insert pipe size> minimum.

      - MOTORS

Default motor characteristics are specified in Section 220513 "Common Motor Requirements for Plumbing Equipment."

        - Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Section 220513 "Common Motor Requirements for Plumbing Equipment."

          - Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

        - Motors for submersible pumps are to be hermetically sealed.

- EXECUTION

      - EARTHWORK

        - Excavation and filling are specified in Section 312000 "Earth Moving."

      - EXAMINATION

        - Examine roughing-in for plumbing piping to verify actual locations of storm drainage piping connections before sump-pump installation.

      - INSTALLATION

        - Pump Installation Standards: Comply with HI 14.4 for installation of sump pumps.

        - Equipment Mounting:

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic control device type and minimum deflection in supported equipment schedule on Drawings.

          - Comply with requirements for vibration isolation and seismic control devices specified in Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment."

          - Comply with requirements for vibration isolation devices specified in Section 220548.13 "Vibration Controls for Plumbing Piping and Equipment."

Retain "Wiring Method" Paragraph below for pumps with wall-mounted controls and coordinate with Drawings. Delete if wiring methods for system are indicated on Drawings.

        - Wiring Method: Comply with requirements in Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

        - Wiring within Enclosures: Bundle, lace, and train conductors to terminal points with no excess and without exceeding manufacturer's limitations on bending radii. Provide and use lacing bars and distribution spools.

      - PIPING CONNECTIONS

Coordinate pump installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Comply with requirements for piping specified in Section 221414 "Storm Drainage Piping." Drawings indicate general arrangement of piping, fittings, and specialties.

        - Where installing piping adjacent to equipment, allow space for service and maintenance.

      - STARTUP SERVICE

        - [Engage a factory-authorized service representative to perform] [Perform] startup service.

          - Complete installation and startup checks in accordance with manufacturer's written instructions.

          - <Insert startup steps if any>.

      - ADJUSTING

        - Adjust pumps to function smoothly, and lubricate as recommended by manufacturer.

        - Adjust control set points.

      - FIELD QUALITY CONTROL

Retain first option in "Testing Agency" Paragraph below if Owner hires an independent testing agency.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain "Manufacturer's Field Service" Paragraph below to require a factory-authorized service representative to perform tests, inspections, and adjustments.

        - Manufacturer's Field Service: Engage a factory-authorized service representative to test, inspect, and adjust components, assemblies, and equipment installations, including connections.

        - Tests and inspections:

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

          - Perform each visual and mechanical inspection.

          - Leak Test: After installation, charge system and test for leaks. Repair leaks and retest until no leaks exist.

          - Operational Test: After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

          - Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

          - Pumps and controls will be considered defective if they do not pass tests and inspections.

        - Prepare test and inspection reports.

      - DEMONSTRATION

        - [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain[ controls and] pumps.

END OF SECTION 221429