Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 221513 - GENERAL-SERVICE COMPRESSED-AIR PIPING

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Access Manufacturer-Provided, AIA MasterSpec-Based Sections:

<Double click here for this Section based on specific manufacturer’s products set as Basis-of-Design at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provision for LEED 2009, LEED v4, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using hypertext links.

- GENERAL

      - SUMMARY

        - Section includes piping and related specialties for general-service compressed-air systems, as follows:

          - Pipes, tubes, and fittings.

          - Joining materials.

          - Valves.

          - Dielectric fittings.

          - Flexible pipe connectors.

          - Specialties.

          - Quick couplings.

          - Hose assemblies.

        - Related Requirements:

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 221519 "General-Service Packaged Air Compressors and Receivers" for general-service air compressors and accessories.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - CR: Chlorosulfonated polyethylene synthetic rubber.

        - EPDM: Ethylene-propylene-diene terpolymer rubber.

        - HDPE: High-density polyethylene plastic.

        - High-Pressure, Compressed-Air Piping: System of compressed-air piping and specialties operating at pressures between 150 and 200 psig (1035 and 1380 kPa).

        - Low-Pressure, Compressed-Air Piping: System of compressed-air piping and specialties operating at pressures of 150 psig (1035 kPa) or less.

        - NBR: Nitrile butadiene rubber.

        - PE: Polyethylene plastic.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

          - Plastic pipes, fittings, and valves.

          - Dielectric fittings.

          - Flexible pipe connectors.

          - Safety valves.

          - Pressure regulators. Include rated capacities and operating characteristics.

          - Automatic drain valves.

          - Filters. Include rated capacities and operating characteristics.

          - Lubricators. Include rated capacities and operating characteristics.

          - Quick couplings.

          - Hose assemblies.

      - INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

        - Certificates:

          - [Brazing] [and] [welding] certificates.

        - Field Quality-Control Submittals:

Retain "Field quality-control reports" Subparagraph below if Contractor is responsible for field quality-control testing and inspecting.

          - Field quality-control reports.

Coordinate "Qualification Statements" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article. If inserting additional entities or specialist, add qualifications to "Quality Assurance" Article.

        - Qualification Statements: For Installer.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For general-service compressed-air piping specialties to include in emergency, operation, and maintenance manuals.

      - QUALITY ASSURANCE

        - Installer Qualifications:

          - Extruded-Tee Outlet Procedure: Qualify operators according to training provided by respective manufacturer, for making branch outlets.

          - Press-Seal Joining Procedure for Copper Tubing: Qualify operators according to training provided by respective manufacturer.

          - Pressure-Seal Joining Procedure for Steel Piping. Qualify operators according to training provided by respective manufacturer.

          - Joining Procedures for Aluminum Piping Systems: Qualify installers according to training provided by respective manufacturer.

Retain "Certificates" Paragraph in "Informational Submittals" Article if retaining "Brazing" Paragraph below.

        - Brazing: Qualify processes and operators in accordance with ASME Boiler and Pressure Vessel Code: Section IX, "Welding and Brazing Qualifications," or with AWS B2.2, "Standard for Brazing Procedure and Performance Qualification."

Retain "Certificates" Paragraph in "Informational Submittals" Article if retaining "Welding" Paragraph below.

        - Welding: Qualify processes and operators in accordance with ASME Boiler and Pressure Vessel Code: Section IX.

      - PROJECT CONDITIONS

Retain this article if interruption of existing compressed-air service is required.

        - Interruption of Existing Compressed-Air Service: Do not interrupt compressed-air service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary compressed-air service according to requirements indicated:

          - Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of compressed-air service.

          - Do not proceed with interruption of compressed-air service without [Architect's] [Construction Manager's] [Owner's] written permission.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - SOURCE LIMITATIONS

Retain this article to limit sources for the entire Section. Source limitations may also be specified in individual articles if so desired.

        - Obtain each product type from single source from single manufacturer.

      - PERFORMANCE REQUIREMENTS

Retain "Seismic Performance" Paragraph below for projects requiring seismic design. Delete paragraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

        - Seismic Performance: Compressed-air piping system to withstand the effects of earthquake motions determined in accordance with [ASCE/SEI 7] <Insert requirement>. See Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment."

Retain first subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

          - The term "withstand" means "the piping system will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the piping system will be fully operational after the seismic event]."

For life-safety components required to function after an earthquake (such as fire-sprinkler systems, components that contain hazardous content, and storage racks in structures open to the public), the Component Importance Factor is 1.5. For other components, the Component Importance Factor is 1.0 unless the structure is in Seismic Use Group III and component is necessary for continued operation of facility or failure of component could impair continued operation of facility, in which case the Component Importance Factor is 1.5.

          - Component Importance Factor: [1.5] [1.0].

See ASCE/SEI 7, Coefficients for Architectural Component Table and Seismic Coefficients for Mechanical and Electrical Components Table, for requirements to be inserted in subparagraph below.

          - <Insert requirements for Component Amplification Factor and Component Response Modification Factor>.

        - ASME Compliance:

          - Comply with ASME B31.1, "Power Piping," for high-pressure, compressed-air piping.

          - Comply with ASME B31.3, "Process Piping," for high- and low-pressure, compressed-air piping.

          - Comply with ASME B31.9, "Building Services Piping," for low-pressure, compressed-air piping.

      - PIPES, TUBES, AND FITTINGS

Retain piping materials in this article to match those retained in "Piping Applications" Article.

        - Schedule 40, Steel Pipe: ASTM A53/A53M, Type E or S, Grade B, black or hot-dip zinc coated with ends threaded in accordance with ASME B1.20.1.

          - Steel Nipples: ASTM A733, made of ASTM A53/A53M or ASTM A106, Schedule 40, galvanized seamless steel pipe. Include ends matching joining method.

          - Malleable-Iron Fittings: ASME B16.3, Class 150 or 300, threaded.

          - Malleable-Iron Unions: ASME B16.39, Class 150 or 300, threaded.

          - Steel Flanges, Threaded: ASME B16.5, Class 150 or 300, carbon steel, threaded.

          - Wrought-Steel, Butt-Welding Fittings: ASME B16.9, Schedule 40.

          - Steel Flanges: ASME B16.5, Class 150 or 300, carbon steel.

          - Grooved-End Fittings and Couplings, Steel:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Grooved-End Fittings: ASTM A47/A47M, malleable-iron castings or ASTM A536, ductile-iron castings; with grooves in accordance with AWWA C606 and dimensions matching steel pipe.

            - Grooved-End Couplings: AWWA C606 or UL 213, for steel-pipe dimensions and rated for 300 psig (2070 kPa) minimum working pressure. Include ferrous housing sections, gasket suitable for compressed air, and bolts and nuts. Provide EDPM gaskets for oil-free compressed air. Provide NBR gaskets if compressed air contains oil or oil vapor.

        - Schedule 5, Steel Pipe: ASTM A135, carbon steel with plain ends and zinc-plated finish.

Retain seal material in "Press-Type, Schedule 5 Steel, Fittings" Subparagraph below to match quality of compressed air. Do not retain EPDM seals if compressed air contains oil or oil vapor.

          - Press-Type, Schedule 5 Steel, Fittings: Listed and labeled by qualified testing agency and FM Global-approved, carbon-steel, pressure-seal housing with O-ring end seals suitable for compressed-air piping and rated for 300 psig (2070 kPa) minimum working pressure. Provide EDPM seals for oil-free compressed air. Provide NBR seals if compressed air contains oil or oil vapor.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Copper Tube: [ASTM B88, Type K or L (ASTM B88M, Type A or B)] seamless, drawn-temper, water tube.

          - Wrought-Copper Fittings: ASME B16.22, solder-joint pressure type or MSS SP-73, wrought copper with dimensions for brazed joints.

          - Cast-Copper-Alloy Flanges: ASME B16.24, Class 150 or 300.

          - Copper Unions: ASME B16.22 or MSS SP-123.

          - Press-Type, Copper Tube, Fittings, NPS 2 (DN 50) and Smaller: Wrought-copper fitting with EPDM O-ring seal in each end.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Press-Type, Copper Tube, Fittings, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Bronze fitting with stainless steel grip ring and EPDM O-ring seal in each end.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Extruded-Tee Outlets: Procedure for making branch outlets in copper tube in accordance with ASTM F2014.

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Grooved-End Fittings and Couplings, Copper:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Grooved-End Fittings: ASTM B75/B75M, copper tube or ASTM B584, bronze castings.

            - Grooved-End Couplings: Copper-tube dimensions and design similar to AWWA C606. Include ferrous housing sections, gasket suitable for compressed air, and bolts and nuts. Provide EDPM gasket for oil-free compressed air. Provide NBR gasket if compressed air contains oil or oil vapor.

        - Transition Couplings for Metal Piping: Metal coupling or other manufactured fitting same size as, with pressure rating at least equal to and ends compatible with, piping to be joined.

        - Aluminum Piping System: Aluminum pipe, Alloy Grade AA 6035-T5, for push-connect bite ring couplings, and roll-groove couplings.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Pressure and Temperature Range: Aluminum piping and related specialties for general-service compressed-air systems operating at 220 psig (1517 kPa) or less, across a temperature range of minus 4 to plus 176 deg F (minus 20 to plus 80 deg C).

          - Tubing, 14 to 273 mm: Aluminum pipe, Alloy Grade AA 6063-T5.

          - Pipe Coating: Powder-coated paint that is certified nontoxic to AAMA 603 and AAMA 605, blue for compressed air.

          - Provide tubing that is quality controlled to comply with tolerances specified by roll-groove or push-to-connect coupling manufacturer. Tubing manufacturer follows ISO 9001:2000 quality standards.

          - Pipe Identification: Decal with maximum working pressure and temperature on each length of pipe.

Available sizes of couplings in first subparagraph below are 14, 20, 25, 32, 40, 50, and 63 mm, which correspond approximately to NPS 1/4, NPS 1/2, NPS 3/4, NPS 1, NPS 1-1/4, NPS 1-1/2, and NPS 2 (DN 8, DN 15, DN 20, DN 25, DN 32, DN 40, and DN 50).

          - Push-Connect Bite Ring Couplings, 14 to 63 mm: Solid-brass and nickel-plated body, NBR O-ring seal in excess of 36 percent, and AISI Type 304 stainless steel clamping washer.

          - Fittings: Solid brass and nickel plated.

Available sizes of couplings in first subparagraph below are 73, 90, 115, 168, 220, and 273 mm, which correspond approximately to NPS 2-1/2, NPS 3, NPS 4, NPS 6, NPS 8, and NPS 10 (DN 65, DN 80, DN 100, DN 150, DN 200, and DN 250).

          - Roll-Groove Couplings, 73 to 273 mm: Solid ductile-iron, galvanized, ASTM A536 Grade 65-45-12, NBR standard seals, and fluoroelastomer seals for high-temperature applications.

Retain first two subparagraphs below if valves are supplied with aluminum piping system or delete both if specified in "Valves" Article.

          - Ball Valves, 20 to 63 mm: NPT ends, or push-connect bite ring ends.

          - Butterfly Valves, 73 to 273 mm: Tube to tube, with two roll-groove end couplings.

          - Flanges, 73 to 273 mm: ASME B16.5, Class 150.

Retain only one of "Blue ABS Piping System," "Green ABS Piping System," and "HDPE Piping System" paragraphs below if plastic piping is required. Do not combine different plastic piping.

Sizes of piping in "Blue ABS Piping System" Paragraph below are 20, 25, 32, 50, 63, 90, and 110 mm, which correspond approximately to NPS 1/2, NPS 3/4, NPS 1, NPS 1-1/2, NPS 2, NPS 3, and NPS 4 (DN 15, DN 20, DN 25, DN 40, DN 50, DN 80, and DN 100).

        - Blue ABS Piping System: Made of ASTM D3965, ABS-resin modified to provide shatter-resistant pipe for compressed-air service. Pipe and fittings are light blue and sizes are in millimeters.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Transition Fittings, 20 to 63 mm: Composite union with ABS socket end, CR O-ring, and malleable-iron union nut and threaded end; with construction similar to MSS SP-107, transition union.

          - Transition Fittings, 90 to 110 mm: Flange assembly with ABS flange, CR gasket, and metal flange of material matching piping to be connected.

Retain first subparagraph below if metal valves are not required for this system.

          - Valves, 20 to 63 mm: ABS union ball valve with socket ends.

          - Valves, 90 to 110 mm: ABS butterfly valve with lever handle.

        - Green ABS Piping System: Made of ASTM D3965, ABS-resin modified to provide shatter-resistant pipe for compressed-air service. Pipe and fittings are dark green with SDR of 9.0 and same OD as ASTM A53/A53M, steel pipe.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Transition Fittings, NPS 1/2 to NPS 2 (DN 15 to DN 50): Composite union with ABS socket end, CR O-ring, ABS union nut, and brass solder-joint end; with construction similar to MSS SP-107, transition union.

          - Transition Fittings, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): ABS flange, CR gasket, and metal flange of material matching piping to be connected.

Retain first subparagraph below if metal valves are not required for this system.

          - Valves, NPS 1/2 to NPS 2 (DN 15 to DN 50): Union ball valve with socket ends.

          - Valves, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Union ball valve with flanged ends. Include safety exhaust feature in "Valve Applications" Article if required.

        - HDPE Piping System: Made of ASTM D1248, HDPE resin to provide shatter-resistant pipe for compressed-air service. Pipe and fittings are dark blue with pipe dimensions about the same OD as ASTM D3035, PE pipe.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Transition Fittings, NPS 1/2 to NPS 2 (DN 15 to DN 50): HDPE adapter with one socket end and one end with threaded brass insert.

          - Transition Fittings, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): HDPE flange, CR gasket, and metal flange of material matching piping to be connected.

Retain subparagraph below if metal valves are not required for this system. Use metal valves for NPS 4 (DN 100).

          - Valves, NPS 1/2 to NPS 3 (DN 15 to DN 80): HDPE union ball valve with socket ends.

      - JOINING MATERIALS

        - Pipe-Flange Gasket Materials: Suitable for compressed-air piping system contents.

          - ASME B16.21, nonmetallic, flat, asbestos free, 1/8-inch (3.2-mm) maximum thickness unless thickness or specific material is indicated.

            - Full-Face Type: For flat-face, Class 125, cast-iron and cast-bronze flanges.

            - Narrow-Face Type: For raised-face, Class 250, cast-iron and steel flanges.

        - Flange Bolts and Nuts: ASME B18.2.1, carbon steel, unless otherwise indicated.

        - Plastic Pipe-Flange Gasket, Bolts, and Nuts: Type and material recommended by piping system manufacturer unless otherwise indicated.

        - Solder Filler Metals: ASTM B32, lead-free alloys. Include water-flushable flux in accordance with ASTM B813.

        - Brazing Filler Metals: AWS A5.8/A5.8M, BCuP Series, copper-phosphorus alloys for general-duty brazing, unless otherwise indicated.

        - Welding Filler Metals: Comply with AWS D10.12/D10.12M for welding materials appropriate for wall thickness and chemical analysis of steel pipe being welded.

        - Solvent Cements for Joining Plastic Piping:

          - ABS Piping: ASTM D2235.

      - VALVES

        - Metal Ball, Butterfly, Check, and Gate Valves: Comply with requirements in Section 220523.12 "Ball Valves for Plumbing Piping," Section 220523.13 "Butterfly Valves for Plumbing Piping," Section 220523.14 "Check Valves for Plumbing Piping," and Section 220523.15 "Gate Valves for Plumbing Piping."

      - DIELECTRIC FITTINGS

        - General Requirements: Assembly of copper alloy and ferrous materials with separating nonconductive insulating material. Include end connections compatible with pipes to be joined.

Unions in "Dielectric Unions" Paragraph below are available in at least NPS 1/2 to NPS 2 (DN 15 to DN 50).

        - Dielectric Unions:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: ASSE 1079.

Revise pressure rating and temperature in "Pressure Rating" Subparagraph below to suit Project, or insert other options for specific applications.

            - Pressure Rating: [125 psig (860 kPa) minimum at 180 deg F (82 deg C)] [150 psig (1035 kPa)] [250 psig (1725 kPa)].

            - End Connections: Solder-joint copper alloy and threaded ferrous.

Flanges in "Dielectric Flanges" Paragraph below are available in at least NPS 1-1/2 to NPS 4 (DN 40 to DN 100).

        - Dielectric Flanges:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: ASSE 1079.

            - Factory-fabricated, bolted, companion-flange assembly.

Revise pressure rating and temperature in "Pressure Rating" Subparagraph below to suit Project, or insert other options for specific applications.

            - Pressure Rating: [125 psig (860 kPa) minimum at 180 deg F (82 deg C)] [150 psig (1035 kPa)] [175 psig (1200 kPa)] [300 psig (2070 kPa)].

            - End Connections: Solder-joint copper alloy and threaded ferrous; threaded solder-joint copper alloy and threaded ferrous.

Flanges in "Dielectric-Flange Insulating Kits" Paragraph below are available in at least NPS 1/2 to NPS 48 (DN 15 to DN 1200).

        - Dielectric-Flange Insulating Kits:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Nonconducting materials for field assembly of companion flanges.

Revise pressure rating in "Pressure Rating" Subparagraph below to suit Project, or insert other options for specific applications.

            - Pressure Rating: [150 psig (1035 kPa)] <Insert pressure>.

            - Gasket: Neoprene or phenolic.

            - Bolt Sleeves: Phenolic or polyethylene.

            - Washers: Phenolic with steel backing washers.

      - FLEXIBLE PIPE CONNECTORS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Bronze-Hose Flexible Pipe Connectors: Corrugated-bronze tubing with bronze wire-braid covering and ends brazed to inner tubing.

          - Working-Pressure Rating: [200 psig (1380 kPa)] [250 psig (1725 kPa)] minimum.

          - End Connections, NPS 2 (DN 50) and Smaller: Threaded copper pipe or plain-end copper tube.

          - End Connections, NPS 2-1/2 (DN 65) and Larger: Flanged copper alloy.

        - Stainless Steel-Hose Flexible Pipe Connectors: Corrugated, stainless steel tubing with stainless steel wire-braid covering and ends welded to inner tubing.

          - Working-Pressure Rating: [200 psig (1380 kPa)] [250 psig (1725 kPa)] minimum.

          - End Connections, NPS 2 (DN 50) and Smaller: Threaded steel pipe nipple.

          - End Connections, NPS 2-1/2 (DN 65) and Larger: Flanged steel nipple.

      - SPECIALTIES

        - Safety Valves: ASME Boiler and Pressure Vessel Code: Section VIII, "Pressure Vessels," construction; National Board certified, labeled, and factory sealed; constructed of bronze body with poppet-type safety valve for compressed-air service.

          - Pressure Settings: Higher than discharge pressure and same or lower than receiver pressure rating.

Retain "Air-Main Pressure Regulators" Paragraph below for large-capacity regulators on compressed-air mains. Indicate capacities on Drawings.

        - Air-Main Pressure Regulators: Bronze body, direct acting, spring-loaded manual pressure-setting adjustment, and rated for [250 psig (1725 kPa)] <Insert pressure> inlet pressure, unless otherwise indicated.

          - Type: Pilot operated.

Retain "Air-Line Pressure Regulators, Bronze Body" or "Air-Line Pressure Regulators, Aluminum Alloy or Plastic Body" Paragraph below for regulators on compressed-air branch piping to equipment. Indicate capacities on Drawings.

        - Air-Line Pressure Regulators, Bronze Body: [Diaphragm] [or] [pilot] operated, bronze body, direct acting, spring-loaded manual pressure-setting adjustment, and rated for [200 psig (1380 kPa)] <Insert pressure> minimum inlet pressure, unless otherwise indicated.

        - Air-Line Pressure Regulators, Aluminum Alloy or Plastic Body: Diaphragm operated, aluminum alloy or plastic body, direct acting, spring-loaded manual pressure-setting adjustment, and rated for [200 psig (1380 kPa)] <Insert pressure> minimum inlet pressure, unless otherwise indicated.

        - Automatic Drain Valves: Stainless steel body and internal parts, rated for [200 psig (1380 kPa)] <Insert pressure> minimum working pressure, capable of automatic discharge of collected condensate.[ Include mounting bracket if wall mounting is indicated.]

Indicate on Drawings capacities of filters in "Coalescing Filters" and "Mechanical Filters" paragraphs below.

        - Coalescing Filters: Coalescing type with activated carbon capable of removing water and oil aerosols; with color-change dye to indicate when carbon is saturated and warning light to indicate when selected maximum pressure drop has been exceeded.[ Include mounting bracket if wall mounting is indicated.]

        - Mechanical Filters: Two-stage, mechanical-separation, air-line filters. Equip with deflector plates, resin-impregnated-ribbon filters with edge filtration, and drain cock.[ Include mounting bracket if wall mounting is indicated.]

Retain "Air-Line Lubricators" Paragraph below if oil feed is required in compressed air for air-operated valve, cylinder, or tool lubrication. Indicate capacities of lubricators on Drawings.

        - Air-Line Lubricators: With drip chamber and sight dome for observing oil drop entering airstream; with oil-feed adjustment screw and quick-release collar for easy bowl removal.[ Include mounting bracket if wall mounting is indicated.]

          - Provide with automatic feed device for supplying oil to lubricator.

      - QUICK COUPLINGS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - General Requirements for Quick Couplings: Assembly with locking-mechanism feature for quick connection and disconnection of compressed-air hose.

Retain "Automatic-Shutoff Quick Couplings" or "Valveless Quick Couplings" Paragraph below, or both. Indicate location of each type on Drawings if both types of quick couplings are required.

        - Automatic-Shutoff Quick Couplings: Straight-through brass body with O-ring or gasket seal and stainless steel or nickel-plated-steel operating parts.

          - Socket End: With one-way valve and threaded inlet for connection to piping or threaded hose fitting.

Check-valve plug end in first option in "Plug End" Subparagraph below is recommended for safety but is not available from all manufacturers.

          - Plug End: [Flow-sensor-bleeder, check-valve] [Straight-through] type with barbed outlet for attaching hose.

        - Valveless Quick Couplings: Straight-through brass body with stainless steel or nickel-plated-steel operating parts.

          - Socket End: With O-ring or gasket seal, without valve, and with barbed inlet for attaching hose.

          - Plug End: With barbed outlet for attaching hose.

      - HOSE ASSEMBLIES

        - Description: Compatible hose, clamps, couplings, and splicers suitable for compressed-air service, of nominal diameter indicated, and rated for [300 psig (2070 kPa)] <Insert pressure> minimum working pressure, unless otherwise indicated.

          - Hose: Reinforced [single-] [or] [double]-wire-braid, CR-covered hose for compressed-air service.

          - Hose Clamps: Stainless steel clamps or bands.

          - Hose Couplings: Two-piece, straight-through, threaded brass or stainless steel O-ring or gasket-seal swivel coupling with barbed ends for connecting two sections of hose.

          - Hose Splicers: One-piece, straight-through brass or stainless steel fitting with barbed ends for connecting two sections of hose.

- EXECUTION

      - PIPING APPLICATIONS

Revise Part 2 to retain piping materials retained in this article.

Delete "Compressed-Air Piping between Air Compressors and Receivers" Paragraph below if receivers are factory packaged with air compressors.

Retain "one of" option in paragraph to allow Contractor to select piping materials from those retained. Piping materials below are rated for at least 200 psig (1380 kPa).

        - Compressed-Air Piping between Air Compressors and Receivers: Use[ one of] the following piping materials for each size range:

Retain one or more of first five subparagraphs below.

          - [NPS 2 (DN 50)] <Insert pipe size> and Smaller, Threaded: Schedule 40, [black] [galvanized]-steel pipe; threaded, malleable-iron fittings; and threaded joints.

          - [NPS 2 (DN 50)] <Insert pipe size> and Smaller, Pressure-Sealed: Schedule 5, galvanized-steel pipe; pressure-seal fittings; and press-seal joints.

          - [NPS 2 (DN 50)] <Insert pipe size> and Smaller, Welded: Schedule 40, black-steel pipe; wrought-steel fittings; and welded joints.

          - [NPS 2 (DN 50)] <Insert pipe size> and Smaller, Brazed: Type K or L (Type A or B), copper tube; wrought-copper fittings; and brazed joints.

Sizes in first subparagraph below are 14-, 20-, 25-, 32-, 40-, 50-, and 63-mm outside tube diameter, which correspond approximately to NPS 1/4, NPS 1/2, NPS 3/4, NPS 1, NPS 1-1/4, NPS 1-1/2, and NPS 2 (DN 8, DN 15, DN 20, DN 25, DN 32, DN 40, and DN 50).

          - [NPS 2 (DN 50)] [63 mm] <Insert pipe size> and Smaller: Aluminum pipe; solid-brass nickel-plated fittings; and push-connect bite ring couplings.

Retain one or more of first six subparagraphs below.

          - [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>, Threaded: Schedule 40, [black] [galvanized]-steel pipe; threaded, malleable-iron fittings; and threaded joints.

          - [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>, Grooved-End: Schedule 40, [black] [galvanized]-steel pipe; grooved-end fittings; couplings; and grooved joints.

          - [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>, Welded: Schedule 40, black-steel pipe; wrought-steel fittings; and welded joints.

          - [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>, Brazed: Type K or L (Type A or B), copper tube; wrought-copper fittings; and brazed joints.

          - [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>, Grooved-End, Copper: Type K or L (Type A or B), copper tube; grooved-end copper fittings; couplings; and grooved joints.

Sizes in first subparagraph below are 73-, 90-, and 115-mm outside tube diameter, which correspond approximately to NPS 2-1/2, NPS 3, and NPS 4 (DN 65, DN 80, and DN 100).

          - [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] [73 to 115 mm] <Insert pipe size range>: Aluminum pipe; and roll-groove couplings.

Retain one or more of five subparagraphs below.

          - [NPS 5 (DN 125)] <Insert pipe size> and Larger, Threaded: Schedule 40, [black] [galvanized]-steel pipe; threaded, malleable-iron fittings; and threaded joints.

          - [NPS 5 (DN 125)] <Insert pipe size> and Larger, Grooved-End: Schedule 40, [black] [galvanized]-steel pipe; grooved-end fittings; couplings; and grooved joints.

          - [NPS 5 (DN 125)] <Insert pipe size> and Larger, Welded: Schedule 40, black-steel pipe; wrought-steel fittings; and welded joints.

          - [NPS 5 (DN 125)] <Insert pipe size> and Larger, Grooved-End, Copper: Grooved-end, ASTM B88, Type K or L (ASTM B88M, Type A or B), copper tube; grooved-end copper fittings; couplings; and grooved joints.

Sizes in subparagraph below are 168-, 220-, and 273-mm outside tube diameter, which correspond approximately to NPS 6, NPS 8, and NPS 10 (DN 150, DN 200, and DN 250).

          - [NPS 6 (DN 150)] [168 mm] <Insert pipe size> and Larger: Aluminum pipe; and roll-groove couplings.

Retain "one of" option in "Low-Pressure Compressed-Air Distribution Piping" Paragraph below to allow Contractor to select piping materials from those retained.

        - Low-Pressure Compressed-Air Distribution Piping: Use[ one of] the following piping materials for each size range:

Retain one or more of first eight subparagraphs below.

          - [NPS 2 (DN 50)] <Insert pipe size> and Smaller, Threaded: Schedule 40, [black] [galvanized]-steel pipe; threaded, malleable-iron fittings; and threaded joints.

          - [NPS 2 (DN 50)] <Insert pipe size> and Smaller, Pressure-Sealed, Steel: Schedule 5, galvanized-steel pipe; pressure-seal fittings; and pressure-sealed joints.

          - [NPS 2 (DN 50)] <Insert pipe size> and Smaller, Brazed[ or Soldered]: Type K or L (Type A or B), copper tube; wrought-copper fittings; and brazed[ or soldered] joints.

          - [NPS 2 (DN 50)] <Insert pipe size> and Smaller, Pressure-Sealed, Copper: Type K or L (Type A or B), copper tube; press-type fittings; and pressure-sealed joints.

Sizes in first subparagraph below are 14-, 20-, 25-, 32-, 40-, 50-, and 63-mm outside tube diameter, which correspond approximately to NPS 1/4, NPS 1/2, NPS 3/4, NPS 1, NPS 1-1/4, NPS 1-1/2, and NPS 2 (DN 8, DN 15, DN 20, DN 25, DN 32, DN 40, and DN 50).

          - [NPS 2 (DN 50)] [63 mm] <Insert pipe size> and Smaller: Aluminum pipe; solid-brass nickel-plated fittings; and push-connect bite ring couplings.

          - [NPS 2 (DN 50)] <Insert pipe size> and Smaller, Solvent-Fitted, Blue ABS: 63-mm and smaller, blue ABS pipe and fittings; transition fittings; valves; and solvent-cemented joints.

          - [NPS 2 (DN 50)] <Insert pipe size> and Smaller, Solvent-Fitted, Green ABS: Pipe and fittings, transition fittings, and valves; and solvent-cemented joints.

          - [NPS 2 (DN 50)] <Insert pipe size> and Smaller, Heat-Fused: HDPE pipe, fittings, and valves; and heat-fusion joints.

Retain one or more of first nine subparagraphs below.

          - [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>, Threaded: Schedule 40, [black] [galvanized]-steel pipe; threaded, malleable-iron fittings; and threaded joints.

          - [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>, Grooved-End: Schedule 40, [black] [galvanized]-steel pipe; grooved-end fittings; couplings; and grooved joints.

          - [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>, Brazed[ or Soldered]: Type K or L (Type A or B), copper tube; wrought-copper fittings; and brazed[ or soldered] joints.

          - [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>, Grooved-End, Copper: Type K or L (Type A or B), copper tube; grooved-end copper fittings; couplings; and grooved joints.

          - [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>, Pressure-Sealed: Type K or L (Type A or B), copper tube; press-type fittings; and pressure-sealed joints.

Sizes in first subparagraph below are 73-, 90-, and 115-mm outside tube diameter, which correspond approximately to NPS 2-1/2, NPS 3, and NPS 4 (DN 65, DN 80, and DN 100).

          - [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] [73 to 115 mm] <Insert pipe size range>: Aluminum pipe; and roll-groove couplings.

Piping in first three subparagraphs below is available in NPS 4 (DN 100) and smaller.

          - [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>, Solvent-Fitted, Blue ABS: 90- and 110-mm, blue ABS pipe and fittings; transition fittings; and solvent-cemented joints. Include butterfly valves and flanged joints.

          - [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>, Solvent-Fitted, Green ABS: NPS 3 and NPS 4 (DN 80 and DN 100), green ABS pipe and fittings; transition fittings; and solvent-cemented joints. Include ball valves and flanged joints.

          - [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>, Heat-Fused: NPS 3 and NPS 4 (DN 80 and DN 100), HDPE pipe and fittings; valves; and heat-fusion joints.

Retain one or more of four subparagraphs below.

          - [NPS 5 and NPS 6 (DN 125 and DN 150)] <Insert pipe size range>: Schedule 40, [black] [galvanized]-steel pipe; threaded, malleable-iron fittings; and threaded joints.

          - [NPS 5 (DN 125)] <Insert pipe size> and Larger: Schedule 40, [black] [galvanized]-steel pipe; grooved-end fittings; couplings; and grooved joints.

          - [NPS 5 to NPS 8 (DN 125 to DN 200)] <Insert pipe size range>: Type K or L (Type A or B), copper tube; grooved-end copper fittings; couplings; and grooved joints.

Sizes in subparagraph below are 168-, 220-, and 273-mm outside tube diameter, which correspond approximately to NPS 6, NPS 8, and NPS 10 (DN 150, DN 200, and DN 250).

          - [NPS 6 to NPS 10 (DN 150 to DN 250)] [168 to 273 mm] <Insert pipe size range>: Aluminum pipe; and roll-groove couplings.

Retain "one of" option in "High-Pressure Compressed-Air Distribution Piping" Paragraph below to allow Contractor to select piping materials from those retained.

        - High-Pressure Compressed-Air Distribution Piping: Use[ one of] the following piping materials for each size range:

Retain one or more of first five subparagraphs below.

          - [NPS 2 (DN 50)] <Insert pipe size> and Smaller, Threaded: Schedule 40, [black] [galvanized]-steel pipe; threaded, malleable-iron fittings; and threaded joints.

          - [NPS 2 (DN 50)] <Insert pipe size> and Smaller, Pressure-Sealed: Schedule 5, galvanized-steel pipe; pressure-seal fittings; and pressure-sealed joints.

          - [NPS 2 (DN 50)] <Insert pipe size> and Smaller, Welded: Schedule 40, black-steel pipe; wrought-steel fittings; and welded joints.

          - [NPS 2 (DN 50)] <Insert pipe size> and Smaller, Brazed[ or Soldered]: Type K or L (Type A or B), copper tube; wrought-copper fittings; and brazed[ or soldered] joints.

Sizes in first subparagraph below are 14-, 20-, 25-, 32-, 40-, 50-, and 63-mm outside tube diameter, which correspond approximately to NPS 1/4, NPS 1/2, NPS 3/4, NPS 1, NPS 1-1/4, NPS 1-1/2, and NPS 2 (DN 8, DN 15, DN 20, DN 25, DN 32, DN 40, and DN 50).

          - [NPS 2 (DN 50)] [63 mm] <Insert pipe size> and Smaller: Aluminum pipe; solid-brass nickel-plated fittings; and push-connect bite ring couplings.

Retain one or more of first seven subparagraphs below.

          - [NPS 2-1/2 to NPS 6 (DN 65 to DN 150)] <Insert pipe size range>, Threaded: Schedule 40, [black] [galvanized]-steel pipe; threaded, malleable-iron fittings; and threaded joints.

          - [NPS 2-1/2 to NPS 6 (DN 65 to DN 150)] <Insert pipe size range>, Grooved-End: Schedule 40, [black] [galvanized]-steel pipe; grooved-end fittings; couplings; and grooved joints.

          - [NPS 2-1/2 to NPS 6 (DN 65 to DN 150)] <Insert pipe size range>, Welded: Schedule 40, black-steel pipe; wrought-steel fittings; and welded joints.

          - [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>: Type K or L (Type A or B), copper tube; wrought-copper fittings; and brazed[ or soldered] joints.

          - [NPS 2-1/2 to NPS 6 (DN 65 to DN 150)] <Insert pipe size range>, Brazed: Type K or L (Type A or B), copper tube; wrought-copper fittings; and brazed joints.

          - [NPS 2-1/2 to NPS 6 (DN 65 to DN 150)] <Insert pipe size range>, Grooved-End, Copper: Type K or L (Type A or B), copper tube; grooved-end copper fittings; couplings; and grooved joints.

Sizes in first subparagraph below are 73-, 90-, 115-, and 168-mm outside tube diameter, which correspond approximately to NPS 2-1/2, NPS 3, NPS 4, and NPS 6 (DN 65, DN 80 DN 100, and DN 150).

          - [NPS 2-1/2 to NPS 6 (DN 65 to DN 150)] [73 to 168 mm] <Insert pipe size range>: Aluminum pipe; and roll-groove couplings.

Retain one or more of four subparagraphs below.

          - [NPS 8 (DN 200)] <Insert pipe size> and Larger, Grooved: Schedule 40, [black] [galvanized]-steel pipe; grooved-end fittings; couplings; and grooved joints.

          - [NPS 8 (DN 200)] <Insert pipe size> and Larger, Welded: Schedule 40, black-steel pipe; wrought-steel fittings; and welded joints.

          - [NPS 8 (DN 200)] <Insert pipe size>, Grooved-End: Type K or L (Type A or B), copper tube; grooved-end copper fittings; couplings; and grooved joints.

Sizes in subparagraph below are 220- and 273-mm outside tube diameter, which correspond approximately to NPS 8 and NPS 10 (DN 200 and DN 250).

          - [NPS 8 and NPS 10 (DN 200 and DN 250)] [220 and 273 mm] <Insert pipe size range>: Aluminum pipe; and roll-groove couplings.

Retain "one of" option in "Drain Piping" Paragraph below to allow Contractor to select piping materials from those retained.

        - Drain Piping: Use[ one of] the following piping materials:

Retain one of two subparagraphs below, or both.

          - [NPS 2 (DN 50)] <Insert pipe size> and Smaller: Type M (Type C) copper tube; wrought-copper fittings; and brazed or soldered joints.

Sizes in subparagraph below are 14-, 20-, 25, 32-, 40-, 50-, and 63-mm outside tube diameter, which correspond approximately to NPS 1/4, NPS 1/2, NPS 3/4, NPS 1, NPS 1-1/4, NPS 1-1/2, and NPS 2 (DN 8, DN 15, DN 20, DN 25, DN 32, DN 40, and DN 50).

          - [NPS 2 (DN 50)] [63 mm] <Insert pipe size> and Smaller: Aluminum pipe; solid-brass nickel-plated fittings; and push-connect bite ring couplings.

      - VALVE APPLICATIONS

        - Metal General-Duty Valves: Comply with requirements and use valve types specified in "Valve Applications" Article in Section 220523.12 "Ball Valves for Plumbing Piping," Section 220523.13 "Butterfly Valves for Plumbing Piping," Section 220523.14 "Check Valves for Plumbing Piping," and Section 220523.15 "Gate Valves for Plumbing Piping," according to the following:

          - Low-Pressure Compressed Air: Valve types specified for low-pressure compressed air.

          - High-Pressure Compressed Air: Valve types specified for high-pressure compressed air.

          - Equipment Isolation NPS 2 (DN 50) and Smaller: Safety-exhaust, copper-alloy ball valve with exhaust vent and pressure rating at least as great as piping system operating pressure.

          - Grooved-end valves may be used with grooved-end piping and grooved joints.

Retain "General-Duty Valves for Aluminum Piping System" Paragraph below for valves to be provided with aluminum piping systems in this Section.

        - General-Duty Valves for Aluminum Piping System: Provide valves, made by piping system manufacturer, that are compatible with piping.

          - Ball Valves, [NPS 2 (DN 50)] [63 mm] and Smaller: NPT ends, or push-connect bite ring ends.

          - Butterfly Valves, [NPS 2-1/2 (DN 65)] [73 mm] and Larger: Tube to tube, with two roll-groove end couplings.

Retain "Plastic General-Duty Valves" Paragraph below if plastic valves are required. Use only plastic valves with plastic low-pressure compressed-air piping and within manufacturer's temperature and pressure limits.

        - Plastic General-Duty Valves: Provide valves, made by piping manufacturer, that are compatible with piping. Do not use plastic valves between air compressors and receivers.

          - Blue ABS Piping System: Ball and butterfly valves.

          - Green ABS Piping System: Ball valves.

          - HDPE Piping System: Ball valves.

      - INSTALLATION OF PIPING, GENERAL

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified. If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Drawing plans, schematics, and diagrams indicate general location and arrangement of compressed-air piping. Indicated locations and arrangements were used to size pipe and calculate friction loss, expansion, air-compressor sizing, and other design considerations. Install piping as indicated unless deviations to layout are approved on Coordination Drawings.

        - Install piping concealed from view and protected from physical contact by building occupants, unless otherwise indicated and except in equipment rooms and service areas.

        - Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls. Diagonal runs are prohibited unless otherwise indicated.

        - Install piping above accessible ceilings to allow sufficient space for ceiling panel removal and to coordinate with other services occupying that space.

        - Where installing piping adjacent to equipment and machines, allow space for service and maintenance.

        - Install air and drain piping with 1 percent slope downward in direction of flow.

        - Install nipples, flanges, unions, transition and special fittings, and valves with pressure ratings same as or higher than system pressure rating unless otherwise indicated.

        - Equipment and Specialty Flanged Connections:

          - Use steel companion flange with gasket for connection to steel pipe.

          - Use cast-copper-alloy companion flange with gasket and brazed[ or soldered] joint for connection to copper tube. Do not use soldered joints for connection to air compressors or to equipment or machines producing shock or vibration.

        - Extended-tee outlets with brazed branch connection may be used for copper tubing, within extruded-tee connection diameter to run tube diameter ratio for tube type, in accordance with Extruded Tee Connections Sizes and Wall Thickness for Copper Tube (Inches) Table in ASTM F2014.

        - Install eccentric reducers where compressed-air piping is reduced in direction of flow, with bottoms of both pipes and reducer fitting flush.

        - Install branch connections to compressed-air mains from top of main. Provide drain leg and drain trap at end of each main and branch and at low points.

        - Install pressure gauge on discharge piping from each air compressor and on each receiver. Comply with requirements in Section 220519 "Meters and Gages for Plumbing Piping."

        - Install piping to permit valve servicing.

        - Install piping free of sags and bends.

        - Install fittings for changes in direction and branch connections.

Retain first paragraph below if piping is required to withstand specific design loads.

        - Install seismic restraints on piping. Seismic-restraint devices are specified in Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment."

        - Install sleeves for piping penetrations of walls, ceilings, and floors. Comply with requirements for sleeves specified in Section 220517 "Sleeves and Sleeve Seals for Plumbing Piping."

Retain first paragraph below for piping that penetrates an exterior concrete wall or concrete slab.

        - Install sleeve seals for piping penetrations of concrete walls and slabs. Comply with requirements for sleeve seals specified in Section 220517 "Sleeves and Sleeve Seals for Plumbing Piping."

        - Install escutcheons for piping penetrations of walls, ceilings, and floors. Comply with requirements for escutcheons specified in Section 220518 "Escutcheons for Plumbing Piping."

      - INSTALLATION OF ALUMINUM PIPING SYSTEMS

        - Install aluminum piping systems in accordance with manufacturer's written instructions, using manufacturer's recommended tools, accessories, and methods.

        - Install branch connections [NPS 2-1/2 (DN 65)] [73 mm] and larger, to compressed-air mains from top of main. Provide drain leg and drain trap at end of each main and branch and at low points.

        - Install branch connections [NPS 2 (DN 50)] [63 mm] and smaller, to compressed-air mains using aluminum piping system reducing outlet tee with water trapping capabilities. Provide drain leg and drain trap at end of each main and branch and at low points.

        - Support aluminum pipe using manufacturer's hangers and supports, designed for use with the system.

        - Allow for expansion and contraction of aluminum piping system.

        - Do not use plastic components or plastic fittings of any kind within pressurized aluminum piping system. This limitation applies to main headers, branches, and drops.

      - JOINT CONSTRUCTION

        - Ream ends of pipes and tubes and remove burrs. Bevel plain ends of steel pipe.

        - Remove scale, slag, dirt, and debris from inside and outside of pipe and fittings before assembly.

        - Threaded Joints: Thread pipe with tapered pipe threads in accordance with ASME B1.20.1. Cut threads full and clean using sharp dies. Ream threaded pipe ends to remove burrs and restore full ID. Join pipe fittings and valves as follows:

          - Apply appropriate tape or thread compound to external pipe threads unless dry seal threading is specified.

          - Damaged Threads: Do not use pipe or pipe fittings with threads that are corroded or damaged. Do not use pipe sections that have cracked or open welds.

        - Welded Joints for Steel Piping: Join in accordance with AWS D10.12/D10.12M.

        - Brazed Joints for Copper Tubing: Join in accordance with AWS's "Brazing Handbook," "Pipe and Tube" Chapter.

        - Soldered Joints: Apply ASTM B813, water-flushable flux, unless otherwise indicated, to tube end. Join in accordance with ASTM B828 or CDA's "Copper Tube Handbook."

        - Extruded-Tee Outlets for Copper Tubing: Form branches in accordance with ASTM F2014, with tools recommended by procedure manufacturer, and using operators qualified in accordance with "Quality Assurance" Article.

        - Flanged Joints: Use asbestos-free, nonmetallic gasket suitable for compressed air. Join flanges with gasket and bolts in accordance with ASME B31.9 for bolting procedure.

        - Grooved Joints: Assemble couplings with housing, gasket, lubricant, and bolts. Join in accordance with AWWA C606 for grooved joints. Do not apply lubricant to prelubricated gaskets.

        - Heat-Fusion Joints for PE Piping: Clean and dry joining surfaces by wiping with clean cloth or paper towels. Join in accordance with ASTM D2657 for socket-fusion joints.

        - Press-Sealed Joints: Join with tools recommended by fitting manufacturer, using operators qualified in accordance with "Quality Assurance" Article.

        - Solvent-Cemented Joints for ABS Piping: Clean and dry joining surfaces. Join according to the following:

          - Comply with ASTM F402 for safe-handling practice of cleaners, primers, and solvent cements.

          - Join in accordance with ASME B31.9 for solvent-cemented joints and with ASTM D2235 Appendix.

        - Dissimilar Metal Piping Material Joints: Use dielectric fittings.

      - INSTALLATION OF VALVES

        - General-Duty Valves: Comply with requirements in Section 220523.12 "Ball Valves for Plumbing Piping," Section 220523.13 "Butterfly Valves for Plumbing Piping," Section 220523.14 "Check Valves for Plumbing Piping," and Section 220523.15 "Gate Valves for Plumbing Piping."

      - INSTALLATION OF DIELECTRIC FITTINGS

        - Install dielectric fittings in piping at connections of dissimilar metal piping and tubing.

Fittings in first paragraph below are available in NPS 2 (DN 50) and smaller.

        - [NPS 2 (DN 50)] <Insert pipe size> and Smaller: Use dielectric unions.

Fittings in first paragraph below are typically available in NPS 2-1/2 to NPS 4 (DN 65 to DN 100). At least one manufacturer makes larger sizes.

        - [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>: Use dielectric flanges.

Kits in paragraph below are available in NPS 1/2 (DN 15) and larger.

        - [NPS 5 (DN 125)] <Insert pipe size>and Larger: Use dielectric flange kits.

      - INSTALLATION OF FLEXIBLE PIPE CONNECTORS

        - Install flexible pipe connectors in discharge piping[ and in inlet air piping from remote air-inlet filter] of each air compressor.

        - Install bronze-hose flexible pipe connectors in copper compressed-air tubing.

        - Install stainless steel-hose flexible pipe connectors in steel compressed-air piping.

      - INSTALLATION OF SPECIALTIES

        - Install safety valves on receivers in quantity and size to relieve at least the capacity of connected air compressors.

        - Install air-main pressure regulators in compressed-air piping at or near air compressors.

        - Install air-line pressure regulators in branch piping to equipment[ and tools].

        - Install mechanical filters in compressed-air piping at or near air compressors and downstream from coalescing filters.[ Mount on wall at locations indicated.]

        - Install air-line lubricators in branch piping to machine tools.[ Mount on wall at locations indicated.]

        - Install quick couplings at piping terminals for hose connections.

        - Install hose assemblies at hose connections.

      - PIPING CONNECTIONS

        - Install unions, in piping NPS 2 (DN 50) and smaller, adjacent to each valve and at final connection to each piece of equipment and machine.

        - Install flanges, in piping NPS 2-1/2 (DN 65) and larger, adjacent to flanged valves and at final connection to each piece of equipment and machine.

      - INSTALLATION OF HANGERS AND SUPPORTS

Retain first paragraph below for projects in areas that require seismic restraints.

        - Comply with requirements for seismic-restraint devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

        - Comply with requirements in Section 220529 "Hangers and Supports for Plumbing Piping and Equipment" for hangers, supports, and anchor devices.

        - Install hangers for [copper tubing] [and] [steel piping], with maximum horizontal spacing and minimum rod diameters, to comply with MSS SP-58, locally enforced codes, and authorities having jurisdiction requirements, whichever are most stringent.

        - Install hangers for [ABS] [HDPE] [aluminum] piping, with maximum horizontal spacing and minimum rod diameters, to comply with manufacturer's written instructions, locally enforced codes, and authorities having jurisdiction requirements, whichever are most stringent.

        - Support horizontal piping within [12 inches (300 mm)] <Insert dimension> of each fitting and coupling.

        - Support vertical runs of [copper tubing] [and] [steel piping] to comply with MSS SP-58, locally enforced codes, and authorities having jurisdiction requirements, whichever are most stringent.

        - Support vertical runs of [ABS] [HDPE] [aluminum] piping to comply with manufacturer's written instructions, locally enforced codes, and authorities having jurisdiction requirements, whichever are most stringent.

        - Individual, Straight, Horizontal Piping Runs:

          - 100 Ft. (30 m) or Less: MSS Type 1, adjustable, steel clevis hangers.

          - Longer Than 100 Ft. (30 m): MSS Type 43, adjustable roller hangers.

        - Multiple, Straight, Horizontal Piping Runs 100 Ft. (30 m) or Longer: MSS Type 44, pipe rolls. Support pipe rolls on trapeze.

        - Base of Vertical Piping: MSS Type 52, spring hangers.

        - Install vinyl-coated hangers for [ABS] [HDPE] piping.

      - LABELING AND IDENTIFICATION

        - Install identifying labels and devices for general-service compressed-air piping, valves, and specialties. Comply with requirements in Section 220553 "Identification for Plumbing Piping and Equipment."

      - FIELD QUALITY CONTROL

        - Perform field tests and inspections.

        - Tests and Inspections:

          - Piping Leak Tests for Metal Compressed-Air Piping: Test new and modified parts of existing piping. Cap and fill general-service compressed-air piping with oil-free dry air or gaseous nitrogen to pressure of 50 psig (345 kPa) above system operating pressure, but not less than [150 psig (1035 kPa)] <Insert pressure>. Isolate test source and let stand for four hours to equalize temperature. Refill system, if required, to test pressure; hold for two hours with no drop in pressure.

          - Piping Leak Tests for Aluminum Compressed-Air Piping: Test new piping system and modified parts of existing piping system. Cap and fill general-service compressed-air piping system to pressure of 15 psig (105 kPa), hold pressure for 10 minutes. Repeat until reaching required operating pressure, not to exceed 220 psig (1515 kPa). Once desired operating pressure is met, let stand for one hour.

          - Piping Leak Tests for ABS Compressed-Air Piping: Test new and modified parts of existing piping. Cap and fill general-service compressed-air piping with oil-free dry air or gaseous nitrogen, at temperature of 110 deg F (43 deg C) or less, to pressure of [40 psig (275 kPa)] <Insert pressure> above system operating pressure, but not less than [80 psig (550 kPa)] [100 psig (690 kPa)] <Insert pressure> or more than 120 psig (825 kPa). Isolate test source and let stand for four hours to equalize temperature. Refill system, if required, to test pressure; hold for two hours with no drop in pressure.

          - Piping Leak Tests for HDPE Compressed-Air Piping: Test new and modified parts of existing piping. Cap and fill general-service compressed-air piping with oil-free dry air or gaseous nitrogen, at temperature of 100 deg F (38 deg C) or less, to pressure of [40 psig (275 kPa)] <Insert pressure> above system operating pressure, but not less than [100 psig (690 kPa)] [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert pressure> or more than 180 psig (1240 kPa). Isolate test source and let stand for four hours to equalize temperature. Refill system, if required, to test pressure; hold for two hours with no drop in pressure.

          - Repair leaks and retest until no leaks exist.

          - Inspect [filters] [lubricators] [and] [pressure regulators] for proper operation.

        - Prepare test and inspection reports.

END OF SECTION 221513