Copyright 2022 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 223200 - DOMESTIC WATER FILTRATION EQUIPMENT

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Access Manufacturer-Provided, AIA MasterSpec-Based Sections:

<Double click here for this Section based on specific manufacturer’s products set as Basis-of-Design at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Filters - bag type.

          - Filters - cartridge type, freestanding.

          - Filters - cartridge type, off floor.

          - Filters - carbon type.

          - Filters - sand type, circulating.

          - Filters - sand type, multimedia.

          - Filters - greensand type.

          - Separators.

        - Related Requirements:

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 221119 "Domestic Water Piping Specialties" for plumbing piping strainers.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

          - Filters - bag type.

          - Filters - cartridge type, freestanding.

          - Filters - cartridge type, off floor.

          - Filters - carbon type.

          - Filters - sand type, circulating.

          - Filters - sand type, multimedia.

          - Filters - greensand type.

          - Separators.

        - Product Data Submittals: For each product.

          - Construction details, material descriptions, dimensions of individual components and profiles, and finishes.

          - Rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

        - Shop Drawings: For water filtration equipment. Include plans, elevations, sections, details, and attachments to other work.

          - Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Retain "Wiring Diagrams" Subparagraph below if carbon-type filters, and/or sand-type filters, and/or separators are included for the Project.

          - Wiring Diagrams: For power, signal, and control wiring.

      - INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Retain "Seismic Qualification Certificates" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Sections specifying mechanical vibration, supports, and seismic controls. See ASCE/SEI 7 for certification requirements for equipment and components.

        - Seismic Qualification Certificates: For [bag-type filters,] [freestanding cartridge-type filters,] [carbon-type filters,] [circulating sand-type filters,] [multimedia sand-type filters,] [greensand-type filters,] [separators,] accessories, and components, from manufacturer.

          - Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

          - Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

          - Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain "Certificates of Shop Inspections and Data Reports" Paragraph below only if required.

        - Certificates of Shop Inspections and Data Reports: For products required to have ASME label, signed by product manufacturer.

Retain "Welding certificates" Paragraph below if retaining "Welding Qualifications" Paragraph in "Quality Assurance" Article.

        - Welding certificates.

        - Source quality-control reports.

Retain "Field Quality-Control Reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For water filtration equipment to include in emergency, operation, and maintenance manuals.

          - Indicate the actual installed items by marking the submittals with an arrow or box.

      - MATERIALS MAINTENANCE SUBMITTALS

See Section 017700 "Closeout Procedures" for submission of maintenance material items.

Extra materials may not be allowed for publicly funded projects.

        - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Bag-Type Filter Bags: Bags for bag-type filters equal to [200] [400] <Insert number> percent of amount installed for each size and media indicated.

          - Cartridge-Filter Elements: Elements for cartridge filters equal to [200] [400] <Insert number> percent of amount installed for each size and media indicated.

      - QUALITY ASSURANCE

Retain "Welding Qualifications" Paragraph below if shop or field welding is required. If retaining, also retain "Welding certificates" Paragraph in "Informational Submittals" Article.

        - Welding Qualifications: Qualify processes and operators in accordance with ASME Boiler and Pressure Vessel Code.

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

      - PROJECT CONDITIONS

        - Feedwater Analysis:

          - Alkalinity: <Insert ppm (mg/L)>.

          - Arsenic: <Insert ppm (mg/L)>.

          - Calcium: <Insert ppm (mg/L)>.

          - Chlorine: <Insert ppm (mg/L)>.

          - Color: <Insert nephelometric turbidity units>.

          - Hydrogen-Ion Concentration: <Insert pH>.

          - Hardness: <Insert ppm (mg/L)>.

          - Hydrogen Sulfide: <Insert ppm (mg/L)>.

          - Iron: <Insert ppm (mg/L)>.

          - Lead: <Insert ppm (mg/L)>.

          - Magnesium: <Insert ppm (mg/L)>.

          - Manganese: <Insert ppm (mg/L)>.

          - Potassium: <Insert ppm (mg/L)>.

          - Sand: <Insert ppm (mg/L)>.

          - Silt: <Insert ppm (mg/L)>.

          - Sodium: <Insert ppm (mg/L)>.

          - Total Dissolved Solids: <Insert ppm (mg/L)>.

          - Turbidity: <Insert ppm (mg/L)>.

          - <Insert characteristic>: <Insert value>.

        - Feedwater Properties:

          - Inlet Water Pressure: <Insert psig (kPa)>.

          - Water Temperature: <Insert deg F (deg C)>.

      - COORDINATION

        - Coordinate size and location of concrete bases with actual equipment provided.

      - WARRANTY

When warranties are required and available, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

        - Manufacturer Warranty: [Manufacturer agrees] [Installer agrees] [Manufacturer and Installer agree] to repair or replace water filtration components that fail in materials or workmanship within specified warranty period.

Verify warranty periods of each type of water filtration equipment.

        - Warranty Period: [1] <Insert number> year(s) from date of Substantial Completion.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - SOURCE LIMITATIONS

        - Obtain each type of water filtration equipment through one source from a single manufacturer.

      - PERFORMANCE REQUIREMENTS

The U.S. Safe Drinking Water Act has required national compliance with <=0.25% weighted average lead content at wetted surfaces for pipe, fittings, and devices intended to convey or dispense water for human consumption since January 2014. The International Plumbing Code and Uniform Plumbing Code have the same requirements. Items in compliance with NSF 61 and NSF 372 also comply with this requirement. Some manufacturers choose to meet this requirement through independent testing and have "certified lead-free" products, which may or may not have NSF 61 or NSF 372 certification.

        - Domestic water filtration equipment intended to convey or dispense water for human consumption are to comply with the U.S. Safe Drinking Water Act, with requirements of authorities having jurisdiction, and with NSF 61 and NSF 372, or be certified in compliance with NSF 61 and NSF 372 by an ANSI-accredited third-party certification body, in that the weighted average lead content at wetted surfaces is less than or equal to 0.25 percent.

Retain "Seismic Performance" Paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Delete paragraph below if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

        - Seismic Performance: [Bag-type filters,] [Freestanding cartridge-type filters,] [Carbon-type filters,] [Circulating sand-type filters,] [Multimedia sand-type filters,] [Greensand-type filters,] [and] [separators] is to withstand the effects of earthquake motions determined in accordance with [ASCE/SEI 7] <Insert requirement> See Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment."

Retain first subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

          - The term "withstand" means that "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

For life-safety components required to function after an earthquake (such as fire-sprinkler systems, components that contain hazardous content, system components serving critical healthcare functions, and storage racks in structures open to the public), the Component Importance Factor is 1.5. For other components, the Component Importance Factor is 1.0 unless the structure is in Seismic Use Group III and component is necessary for continued operation of facility or failure of component could impair continued operation of facility, in which case the Component Importance Factor is 1.5.

          - Component Importance Factor: [1.5] [1.0].

See ASCE/SEI 7, Coefficients for Architectural Component Table and Seismic Coefficients for Mechanical and Electrical Components Table, for requirements to be inserted in subparagraph below.

          - <Insert requirements for Component Amplification Factor and Component Response Modification Factor>.

      - FILTERS - BAG TYPE <Insert drawing designation>

Insert drawing designation. Use these designations on Drawings to identify each product.

Not all manufacturers listed below offer multiple-bag filters. Verify availability.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Simplex, floor-mounted housing with [single-bag filter] [multiple-bag filter] for removing suspended particles from water.

          - Housing: Corrosion resistant; designed to separate feedwater from filtrate and to direct feedwater through bag-type water filter(s); with bag support and base, feet, or skirt.

Retain "Material" Subparagraph below unless multiple filter types are scheduled on Drawings. Stainless steel housing material is most commonly used.

            - Material: [Carbon steel with NSF 61/NSF 372 lining material] [Plastic] [Stainless steel].

            - Seals: [NBR] <Insert material>.

            - Bag Support: Top lock ring and perforated [stainless steel] <Insert material> basket.

            - Pipe Connections NPS 2 (DN 50) and Smaller: Threaded in accordance with ASME B1.20.1.

            - Steel Housing Pipe Connections NPS 2-1/2 (DN 65) and Larger: Steel, Class 150 flanges in accordance with ASME B16.5 or grooved in accordance with AWWA C606. Provide stainless steel flanges if housing is stainless steel.

            - Plastic Housing Pipe Connections NPS 2-1/2 (DN 65) and Larger: 150 psig (1035 kPa) plastic flanges.

          - Bag: Replaceable, of shape to fit housing.

        - Capacity and Characteristics:

          - Filtrate Design Concentrations:

Retain only required data in list below; insert other data as needed.

            - Alkalinity: <Insert ppm (mg/L)>.

            - Chlorine: <Insert ppm (mg/L)>.

            - Color: <Insert nephelometric turbidity units>.

            - Hydrogen Sulfide: <Insert ppm (mg/L)>.

            - Iron: <Insert ppm (mg/L)>.

            - Manganese: <Insert ppm (mg/L)>.

            - Sand: <Insert ppm (mg/L)>.

            - Silt: <Insert ppm (mg/L)>.

            - Turbidity: <Insert ppm (mg/L)>.

            - <Insert characteristic>: <Insert value>.

          - Filter Design:

            - Continuous Flow: <Insert gpm (L/s)>.

            - Peak Flow: <Insert gpm (L/s)>.

            - Filtration Efficiency: [98] <Insert number> percent retention of suspended particles [10] [20] <Insert size> microns and larger from feedwater of listed filtrate design concentrations.

            - Pressure Drop, Clean: Not to exceed [2 psig (14 kPa)] <Insert value> at filter design flow rate when clean.

            - Pressure Drop, Dirty: Not to exceed <Insert value> when dirty.

          - Housing:

            - Pressure Rating: <Insert psig (kPa)>.

            - Diameter: <Insert inches (mm)>.

            - Height or Length: <Insert inches (mm)>.

            - Inlet and Outlet Size: <Insert NPS (DN)>.

            - Drain Size: [Not applicable] <Insert NPS (DN)>.

          - Bag:

            - Nominal Diameter: <Insert inches (mm)>.

            - Nominal Length: <Insert inches (mm)>.

            - Media: [Cotton] [Polyester] [PP] <Insert material>; [felt, filament, or mesh] [felt] [filament] [mesh] construction.

      - FILTERS - CARTRIDGE TYPE

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Filters - Cartridge Type, Freestanding: <Insert drawing designation>

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Simplex, floor-mounted housing with replaceable element(s) for removing suspended particles from water.

            - Housing: Corrosion resistant; designed to separate feedwater from filtrate and to direct feedwater through water filter element(s); with element support(s) and base, feet, or skirt.

Retain first subparagraph below for projects in seismic areas.

              - Fabricate supports and base, feet, or skirt and attachment to housing with reinforcement strong enough to resist filter movement during a seismic event when filter base is anchored to building structure.

              - Pipe Connections NPS 2 (DN 50) and Smaller: Threaded in accordance with ASME B1.20.1.

              - Steel Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger: Steel, Class 150 flanges in accordance with ASME B16.5 or grooved in accordance with AWWA C606. Provide stainless steel flanges if housing is stainless steel.

              - Plastic Housing Pipe Connections NPS 2-1/2 (DN 65) and Larger: 150 psig (1035 kPa) plastic flanges.

            - Element(s): Replaceable; of shape to fit housing.

          - Capacity and Characteristics:

            - Filtrate Design Concentrations:

Retain only required data in list below; insert other data as needed.

              - Alkalinity: <Insert ppm (mg/L)>.

              - Chlorine: <Insert ppm (mg/L)>.

              - Color: <Insert nephelometric turbidity units>.

              - Hydrogen Sulfide: <Insert ppm (mg/L)>.

              - Iron: <Insert ppm (mg/L)>.

              - Manganese: <Insert ppm (mg/L)>.

              - Sand: <Insert ppm (mg/L)>.

              - Silt: <Insert ppm (mg/L)>.

              - Turbidity: <Insert ppm (mg/L)>.

              - <Insert characteristic>: <Insert value>.

            - Filter Design:

              - Continuous Flow: <Insert gpm (L/s)>.

              - Peak Flow: <Insert gpm (L/s)>.

              - Filtration Efficiency: [98] <Insert number> percent retention of suspended particles [1] [10] [20] <Insert size> microns and larger from feedwater of listed filtrate design concentrations.

              - Pressure Drop, Clean: Not to exceed [2 psig (14 kPa)] <Insert value> at filter design flow rate when clean.

              - Pressure Drop, Dirty: Not to exceed <Insert value> when dirty.

            - Housing:

              - Material: [Plastic] [Stainless steel] <Insert material>.

              - Pressure Rating: <Insert psig (kPa)>.

              - Seals: [NBR] <Insert material>.

              - Diameter: <Insert inches (mm)>.

              - Height or Length: <Insert inches (mm)>.

              - Inlet and Outlet Size: <Insert NPS (DN)>.

              - Drain Size: [Not applicable] <Insert NPS (DN)>.

            - Elements:

              - Number Required: [One] [Two] <Insert number>.

              - Nominal Diameter: <Insert inches (mm)>.

              - Nominal Length: <Insert inches (mm)>.

              - Media:

Retain one of four subparagraphs below.

                - [Activated charcoal] [or] [ground charcoal].

                - [Pleated polyester] [or] [pleated PP].

                - [Wound polyester] [or] [wound PP].

                - <Insert material>.

        - Filters - Cartridge Type, Off Floor: <Insert drawing designation>

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Simplex, [in-line] [wall-mounted] housing with replaceable element for removing suspended particles from water.

            - Housing: Corrosion resistant; designed to separate feedwater from filtrate and to direct feedwater through water filter element; with element support.

              - Pipe Connections: Threaded in accordance with ASME B1.20.1.

Retain "Support" Subparagraph below only if filters are wall-mounted type.

              - Support: Wall bracket.

            - Element: Replaceable; of shape to fit housing.

          - Capacity and Characteristics:

            - Filtrate Design Concentrations:

Retain only required data in list below; insert other data as needed.

              - Alkalinity: <Insert ppm (mg/L)>.

              - Chlorine: <Insert ppm (mg/L)>.

              - Color: <Insert nephelometric turbidity units>.

              - Hydrogen Sulfide: <Insert ppm (mg/L)>.

              - Iron: <Insert ppm (mg/L)>.

              - Manganese: <Insert ppm (mg/L)>.

              - Sand: <Insert ppm (mg/L)>.

              - Silt: <Insert ppm (mg/L)>.

              - Turbidity: <Insert ppm (mg/L)>.

              - <Insert characteristic>: <Insert value>.

            - Filter Design:

              - Continuous Flow: <Insert gpm (L/s)>.

              - Peak Flow: <Insert gpm (L/s)>.

              - Filtration Efficiency: [98] <Insert number> percent retention of suspended particles [1] [10] [20] <Insert size> microns and larger from feedwater of listed filtrate design concentrations.

              - Pressure Drop, Clean: Not to exceed [2 psig (14 kPa)] <Insert value> at filter design flow rate when clean.

              - Pressure Drop, Dirty: Not to exceed <Insert value> when dirty.

            - Housing:

              - Material: [PE or PP] [Plastic] [Stainless steel] <Insert material>.

              - Pressure Rating: <Insert psig (kPa)>.

              - Seals: [NBR] <Insert material>.

              - Diameter: <Insert inches (mm)>.

              - Height or Length: <Insert inches (mm)>.

              - Inlet and Outlet Size: <Insert NPS (DN)>.

              - Drain Size: [Not applicable] <Insert NPS (DN)>.

            - Element:

              - Nominal Diameter: <Insert inches (mm)>.

              - Nominal Length: <Insert inches (mm)>.

              - Media:

Retain one of four subparagraphs below.

                - [Activated charcoal] [or] [ground charcoal].

                - [Pleated polyester] [or] [pleated PP].

                - [Wound polyester] [or] [wound PP].

                - <Insert material>.

      - FILTERS - CARBON TYPE <Insert drawing designation>

Insert drawing designation. Use these designations on Drawings to identify each product.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Simplex carbon-type filter, with media tank, media, and automatic backwash for [removing chlorine from] [and] [improving color, odor, and taste of] <Insert application> water.

          - Media Tank: Corrosion resistant with distribution system and media.

            - Construction:

Retain first subparagraph below to require steel or stainless steel tanks to be ASME labeled; delete for non-code construction.

              - Fabricate and label steel filter tanks to comply with ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.

Retain first subparagraph below to require FRP tanks to be ASME labeled; delete for non-code construction.

              - Fabricate and label FRP filter tanks to comply with ASME Boiler and Pressure Vessel Code, Section X, if indicated.

Retain first subparagraph below for projects in seismic areas.

              - Fabricate supports, base, and attachment to tank with reinforcement strong enough to resist filter movement during a seismic event when filter base is anchored to building structure.

              - Pipe Connections NPS 2 (DN 50) and Smaller: Threaded in accordance with ASME B1.20.1.

              - Steel Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger: Steel, Class 150 flanges in accordance with ASME B16.5 or grooved in accordance with AWWA C606. Provide stainless steel flanges if tank is stainless steel.

              - FRP Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger: Type A, integral; [Designation E, 125 psig (0.862 MPa)] [or] [Designation F, 150 psig (1.034 MPa)] pressure category flanges of grade same as tank material in accordance with ASTM D5421.

              - Support: Base, feet, or skirt.

          - Controls: Automatic for control of backwash; factory wired for single, external electrical connection.

            - Panel: NEMA 250, [Type 4] <Insert type> enclosure.

            - Backwash Initiation Device: [Differential pressure gauges] [Electric time clock] [Water meter].

        - Capacity and Characteristics:

          - Filtrate Design Concentrations:

Retain only required data in list below. For public utility water, only chlorine concentration may be required. For water from a well, all or most data may be required.

            - Alkalinity: <Insert ppm (mg/L)>.

            - Chlorine: <Insert ppm (mg/L)>.

            - Color: <Insert nephelometric turbidity units>.

            - Hydrogen-Ion Concentration: <Insert pH>.

            - Hydrogen Sulfide: <Insert ppm (mg/L)>.

            - Iron: <Insert ppm (mg/L)>.

            - Manganese: <Insert ppm (mg/L)>.

            - Total Dissolved Solids: <Insert ppm (mg/L)>.

            - Turbidity: <Insert ppm (mg/L)>.

            - <Insert characteristic>: <Insert value>.

          - Filter Design:

            - Continuous Flow: <Insert gpm (L/s)>.

            - Flow Rate: <Insert gpm/sq. ft. (L/s per sq. m)> of media cross-sectional area.

            - Peak Flow: <Insert gpm (L/s)>.

            - Filtration Efficiency: [98] <Insert number> percent retention of suspended particles [20] [40] <Insert size> microns and larger from feedwater of listed filtrate design concentrations.

            - Pressure Drop, Clean: Not to exceed [2 psig (14 kPa)] <Insert value> at filter design flow rate when clean.

            - Pressure Drop, Dirty: Not to exceed <Insert value> when dirty.

            - Backwash Flow: <Insert gpm (L/s)>.

          - Filter Backwash Interval:

Retain one of first three subparagraphs below to match backwash initiation device retained above.

            - <Insert psig (kPa)> pressure drop measured by differential pressure gauges.

            - <Insert number> days measured by time clock.

            - <Insert gal. (cu. m)> measured by water meter.

          - Media Tank:

            - Material: [Carbon steel with NSF 61/NSF 372 lining material] [FRP] [Stainless steel].

            - Pressure Rating: <Insert psig (kPa)>.

            - Media: [Activated charcoal] [Ground charcoal] <Insert material>.

            - Media Quantity: <Insert cu. ft. (cu. m)>.

            - Diameter: <Insert inches (mm)>.

            - Height: <Insert inches (mm)>.

            - Inlet and Outlet Size: <Insert NPS (DN)>.

          - Unit Electrical Characteristics:

            - Volts: [120] [240] [277] [480] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: [60] <Insert value>.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

      - FILTERS - SAND TYPE

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Filters - Sand Type, Circulating: <Insert drawing designation>

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Factory-fabricated and -tested, simplex, sand-filter system of filter tank, media, strainer, circulating pump, piping, and controls for removing sediment particles from water.

            - Filter Tank: Corrosion resistant with distribution system and media.

              - Construction:

Retain first subparagraph below to require steel or stainless steel tanks to be ASME labeled; delete for non-code construction.

                - Fabricate and label steel filter tanks to comply with ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.

Retain first subparagraph below to require FRP tanks to be ASME labeled; delete for non-code construction.

                - Fabricate and label FRP filter tanks to comply with ASME Boiler and Pressure Vessel Code, Section X, if indicated.

Retain first subparagraph below for projects in seismic areas.

                - Fabricate supports, base, and attachment to tank with reinforcement strong enough to resist filter movement during a seismic event when filter base is anchored to building structure.

              - Pipe Connections NPS 2 (DN 50) and Smaller: Threaded in accordance with ASME B1.20.1.

              - Steel Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger: Steel, Class 150 flanges in accordance with ASME B16.5 or grooved in accordance with AWWA C606.

              - FRP Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger: Type A, integral; [Designation E, 125 psig (0.862 MPa)] [or] [Designation F, 150 psig (1.034 MPa)] pressure category flanges of grade same as tank material in accordance with ASTM D5421.

            - Strainer: Basket type.

              - Pipe Connections:

                - Connections NPS 2 (DN 50) and Smaller: Threaded in accordance with ASME B1.20.1.

                - Connections NPS 2-1/2 (DN 65) and Larger: Cast-iron, Class 125 flanges in accordance with ASME B16.1.

            - Piping:

Retain one of first two subparagraphs below.

              - [Galvanized steel pipe, galvanized cast-iron fittings] [Stainless steel pipe, stainless steel fittings], and flanged, grooved, or threaded joints.

              - ASTM B88, Type L (ASTM B88M, Type B) copper water tube, copper-alloy solder-joint fittings, and brazed, flanged, or grooved joints.

            - Safety Valves: Automatic and manual pressure relief.

            - Circulating Pump: Overhung impeller, close coupled, single stage, end suction, centrifugal. Comply with UL 778 and with HI 1.1-1.2 and HI 1.3.

              - Pump Construction: Bronze fitted.

                - Casing: Radially split, cast iron.

                - Pressure Rating: [125 psig (860 kPa)] [150 psig (1035 kPa)] minimum.

                - Impeller: ASTM B584, cast bronze; statically and dynamically balanced, closed, and keyed to shaft.

                - Shaft and Shaft Sleeve: Steel shaft, with copper-alloy shaft sleeve.

                - Seal: Mechanical.

Motor characteristics, such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency, are specified in Section 220513 "Common Motor Requirements for Plumbing Equipment." If different characteristics are required, insert subparagraphs below to suit Project.

              - Motor: General requirements for motors are specified in Section 220513 "Common Motor Requirements for Plumbing Equipment."

            - Controls: Automatic for control of circulating pump and tank backwash; factory wired for single, external electrical connection.

              - Panel: NEMA 250, [Type 4] <Insert type> enclosure with time clock and pressure gauges.

              - Pump: Automatic and manual.

              - Backwash: Automatic; with [time-clock] [differential-pressure-switch] initiation device.

              - Backwash Valve: Tank mounted.

            - Support: Skid mounting.

          - Capacity and Characteristics:

            - Filtrate Design Concentrations:

              - Sand: <Insert ppm (mg/L)>.

              - Silt: <Insert ppm (mg/L)>.

              - <Insert characteristic>: <Insert value>.

            - Filter Design:

              - Continuous Flow: <Insert gpm (L/s)> at [5 psig (34.5 kPa)] <Insert value> pressure drop.

              - Flow Rate: <Insert gpm/sq. ft. (L/s per sq. m)> of media cross-sectional area.

              - Peak Flow: <Insert gpm (L/s)>.

              - Filtration Efficiency: [98] <Insert number> percent removal of [1.8] <Insert number> minimum specific-gravity suspended particles [5] [10] [20] [45] <Insert size> microns and larger from feedwater of listed filtrate design concentrations.

            - Filter Tank: With internal distribution piping.

              - Material: [Carbon steel with NSF 61/NSF 372 lining material] [FRP] <Insert material>.

              - Pressure Rating: <Insert psig (kPa)>.

              - Diameter: <Insert inches (mm)>.

              - Height: <Insert inches (mm)>.

              - Inlet and Outlet Size: <Insert NPS (DN)>.

              - Purge Size: <Insert NPS (DN)>.

            - Filter Media: [Graded silica sand] <Insert media>.

            - Filter Backwash Interval:

Retain one of first two subparagraphs below to match backwash initiation device retained above.

              - <Insert psig (kPa)> pressure drop measured by differential pressure gauges.

              - <Insert number> days measured by time clock.

            - Circulating Pump:

              - Capacity: <Insert gpm (L/s)>.

              - Total Dynamic Head: <Insert feet (kPa)>.

              - Speed: <Insert rpm>.

              - Inlet Size: <Insert NPS (DN)>.

              - Outlet Size: <Insert NPS (DN)>.

            - Pump Motor Size and Electrical Characteristics:

              - Horsepower: <Insert value>.

              - Volts: [120] [208] [240] [277] [480] <Insert value>.

              - Phase: [Single] [Three].

              - Hertz: [60] <Insert value>.

            - Unit Electrical Characteristics:

              - Full-Load Amperes: <Insert value>.

              - Minimum Circuit Ampacity: <Insert value>.

              - Maximum Overcurrent Protection: <Insert amperage> A.

        - Filters - Sand Type, Multimedia: <Insert drawing designation>

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Factory-fabricated and -tested, [simplex] [duplex] [triplex], multimedia, sand-filter system of filter tank(s), media, piping, and controls for removing sediment particles from water.

            - Tank Construction:

Retain first subparagraph below to require steel or stainless steel tanks to be ASME labeled; delete for non-code construction.

              - Fabricate and label steel filter tanks to comply with ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.

Retain first subparagraph below to require FRP tanks to be ASME labeled; delete for non-code construction.

              - Fabricate and label FRP filter tanks to comply with ASME Boiler and Pressure Vessel Code, Section X, if indicated.

Retain first subparagraph below for projects in seismic areas.

              - Fabricate supports and base and attachment to tank with reinforcement strong enough to resist filter movement during a seismic event when filter base is anchored to building structure.

            - Pipe Connections NPS 2 (DN 50) and Smaller: Threaded in accordance with ASME B1.20.1.

            - Steel Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger: Steel, Class 150 flanges in accordance with ASME B16.5 or grooved in accordance with AWWA C606.

            - FRP Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger: Type A, integral; [Designation E, 125 psig (0.862 MPa)] [or] [Designation F, 150 psig (1.034 MPa)] pressure category flanges of grade same as tank material in accordance with ASTM D5421.

            - Service Valve(s): Diaphragm type [hydraulically] [pneumatically] operated.

            - Piping:

Retain one of first three subparagraphs below.

              - [Galvanized steel pipe, galvanized cast-iron fittings] [Stainless steel pipe, stainless steel fittings], and flanged, grooved, or threaded joints.

              - ASTM B88, Type L (ASTM B88M, Type B) copper water tube, copper-alloy solder-joint fittings, and brazed, flanged, or grooved joints.

              - Schedule 80 ABS or PVC pipe and fittings with solvent-cemented joints.

            - Safety Valves: Automatic air vent.

Retain "Controls for Simplex Tank System" or "Controls for Duplex and Triplex Tank Systems" Subparagraph below, or both.

            - Controls for Simplex Tank System: Automatic, electric time clock for control of filter system flow and backwash cycles; factory wired for single, external electrical connection.

            - Controls for Duplex and Triplex Tank Systems: Automatic, electric time clock for control of filter system flow and backwash cycles; factory wired for single, external electrical connection. System operation is to be continuous with bypass piping and not more than one tank in backwash cycle at same time.

            - Support: Skid mounting.

          - Capacity and Characteristics:

            - Filtrate Design Concentrations:

Retain only required data in list below; insert other data as needed.

              - Chlorine: <Insert ppm (mg/L)>.

              - Color: <Insert nephelometric turbidity units>.

              - Iron: <Insert ppm (mg/L)>.

              - Manganese: <Insert ppm (mg/L)>.

              - Total Dissolved Solids: <Insert ppm (mg/L)>.

              - Turbidity: <Insert ppm (mg/L)>.

              - <Insert characteristic>: <Insert value>.

            - Filter Design:

              - Continuous Flow: <Insert gpm (L/s)> at <Insert psig (kPa)> pressure drop.

              - Peak Flow: <Insert gpm (L/s)> at <Insert psig (kPa)> pressure drop.

              - Filtration Efficiency: [98] <Insert number> percent removal of suspended particles [10] [20] [40] <Insert size> microns and larger from feedwater of listed filtrate design concentrations.

              - Backwash Flow: <Insert gpm (L/s)> at <Insert psig (kPa)> pressure drop.

            - Media Tanks:

Retain one of first two subparagraphs below.

              - Single with controls.

              - [Two] [Three] with manifolded inlet, outlet, and drain piping and controls.

            - Each Media Tank:

              - Material: [Carbon steel with NSF 61 Annex lining material] [FRP] <Insert material>.

              - Pressure Rating: <Insert psig (kPa)> minimum.

              - Distribution System: Factory-installed plastic.

              - Temperature Rating: <Insert deg F (deg C)> minimum.

              - Diameter: <Insert inches (mm)>.

              - Height: <Insert inches (mm)>.

              - Service Valve Size: <Insert NPS (DN)>.

              - Inlet and Outlet Size: <Insert NPS (DN)>.

              - Drain Size: <Insert NPS (DN)>.

            - Filter Media: [Graded silica sand] <Insert media>.

        - Filters - Greensand Type: <Insert drawing designation>

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Greensand-type filter system of piping, and controls for removing [iron] [iron and manganese] [manganese] from water.

            - Tank Construction:

Retain first subparagraph below to require steel or stainless steel tanks to be ASME labeled; delete for non-code construction.

              - Fabricate and label steel filter tanks to comply with ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.

Retain first subparagraph below to require FRP tanks to be ASME labeled; delete for non-code construction.

              - Fabricate and label FRP filter tanks to comply with ASME Boiler and Pressure Vessel Code, Section X.

Retain first subparagraph below for projects in seismic areas.

              - Fabricate supports, base, and attachment to tank with reinforcement strong enough to resist filter movement during a seismic event when filter base is anchored to building structure.

            - Pipe Connections NPS 2 (DN 50) and Smaller: Threaded in accordance with ASME B1.20.1.

            - Steel Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger: Steel, Class 150 flanges in accordance with ASME B16.5 or grooved in accordance with AWWA C606.

            - FRP Tank Pipe Connections NPS 2-1/2 (DN 65) and Larger: Type A, integral; [Designation E, 125 psig (0.862 MPa)] [or] [Designation F, 150 psig (1.034 MPa)] pressure category flanges of grade same as tank material in accordance with ASTM D5421.

            - Service Valve(s): Diaphragm type [hydraulically] [pneumatically] operated.

            - Piping:

Retain one of first three subparagraphs below.

              - [Galvanized steel pipe, galvanized cast-iron fittings] [Stainless steel pipe, stainless steel fittings], and flanged, grooved, or threaded joints.

              - ASTM B88, Type L (ASTM B88M, Type B) copper water tube, copper-alloy solder-joint fittings, and brazed, flanged, or grooved joints.

              - Schedule 80 ABS or PVC pipe and fittings with solvent-cemented joints.

            - Safety Valves: Automatic air vent.

Retain "Controls for Simplex Tank System" or "Controls for Tank System" Subparagraph below, or both.

            - Controls for Simplex Tank System: Automatic, electric time clock for control of filter system flow and backwash cycles; factory wired for single, external electrical connection.

            - Controls for Tank System: [Duplex] [Triplex] <Insert type>. Automatic, electric time clock controls filter system flow and backwash cycles; factory wired for single, external electrical connection. System operation is to be continuous with bypass piping and not more than one tank in backwash cycle at same time.

            - Support: Skid mounting.

          - Capacity and Characteristics:

            - Filtrate Design Concentrations:

              - Iron: <Insert ppm (mg/L)>.

              - Manganese: <Insert ppm (mg/L)>.

              - <Insert characteristic>: <Insert value>.

            - Filter Design:

              - Continuous Flow: <Insert gpm (L/s)> at <Insert psig (kPa)> pressure drop.

              - Peak Flow: <Insert gpm (L/s)> at <Insert psig (kPa)> pressure drop.

              - Filtration Efficiency: [98] <Insert number> percent removal of suspended particles [10] [20] [40] <Insert size> microns and larger from feedwater of listed filtrate design concentrations.

              - Backwash Flow: <Insert gpm (L/s)> at <Insert psig (kPa)> pressure drop.

            - Media Tanks:

Retain one of first two subparagraphs below.

              - Single with controls.

              - [Two] [Three] with manifolded inlet, outlet, and drain piping and controls.

            - Each Media Tank:

              - Material: [Carbon steel with NSF 61 Annex lining material] [FRP] <Insert material>.

              - Pressure Rating: <Insert psig (kPa)> minimum.

              - Distribution System: Factory-installed plastic.

              - Temperature Rating: <Insert deg F (deg C)> minimum.

              - Diameter: <Insert inches (mm)>.

              - Height: <Insert inches (mm)>.

              - Service Valve Size: <Insert NPS (DN)>.

              - Inlet and Outlet Size: <Insert NPS (DN)>.

              - Drain Size: <Insert NPS (DN)>.

            - Filter Media: [Graded silica sand] <Insert media>.

      - SEPARATORS <Insert drawing designation>

Insert drawing designation. Use these designations on Drawings to identify each product.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description:

Retain one of two subparagraphs below.

          - Simplex separator housing with baffles and chambers for removing sediment particles from water by centrifugal action and gravity.

          - Factory-fabricated and -tested, simplex separator system of housing with baffles and chambers, strainer, circulating pump, piping, and controls for removing sediment particles from water by centrifugal action and gravity.

Retain "Housing" Paragraph below with either of last two subparagraphs above.

        - Housing: With manufacturer's proprietary system of baffles and chambers.

          - Construction:

Retain first subparagraph below to require steel or stainless steel tanks to be ASME labeled; delete for non-code construction.

            - Fabricate and label steel separator housing to comply with ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.

Retain first subparagraph below for projects in seismic areas.

            - Fabricate supports, base, and attachment to separator housing with reinforcement strong enough to resist separator movement during a seismic event when separator base is anchored to building structure.

          - Inlet: Designed with tangential entry to produce centrifugal flow of feedwater.

          - Vortex Chamber: Designed for downward vortex flow and gravity separation of particles.

          - Collection Chamber: Designed to hold separated particles.

          - Outlet: Near top of unit.

          - Purge: At bottom of collection chamber.

          - Pipe Connections NPS 2 (DN 50) and Smaller: Threaded in accordance with ASME B1.20.1.

          - Pipe Connections NPS 2-1/2 (DN 65) and Larger: ASME B16.1; steel, Class 150 flanges in accordance with ASME B16.5 or grooved in accordance with AWWA C606. Provide stainless steel flanges if tank is stainless steel.

Retain "Strainer" Paragraph below only if separator is circulating type.

        - Strainer: Basket type.

          - Pipe Connections NPS 2 (DN 50) and Smaller: Threaded in accordance with ASME B1.20.1.

          - Pipe Connections NPS 2-1/2 (DN 65) and Larger: Cast-iron, Class 125 flanges in accordance with ASME B16.1.

        - Piping:

Retain one of two subparagraphs below.

          - [Galvanized steel pipe, galvanized cast-iron fittings] [Stainless steel pipe, stainless steel fittings], and flanged, grooved, or threaded joints.

          - ASTM B88, Type L (ASTM B88M, Type B) copper water tube, copper-alloy solder-joint fittings, and brazed, flanged, or grooved joints.

        - Safety Valves: Automatic and manual pressure relief.

        - Circulating Pump: Overhung impeller, close coupled, single stage, end suction, centrifugal. Comply with UL 778 and with HI 1.1-1.2 and HI 1.3.

          - Pump Construction: Bronze fitted.

            - Casing: Radially split, cast iron.

            - Pressure Rating: [125 psig (860 kPa)] [150 psig (1035 kPa)] minimum.

            - Impeller: ASTM B584, cast bronze; statically and dynamically balanced, closed, and keyed to shaft.

            - Shaft and Shaft Sleeve: Steel shaft, with copper-alloy shaft sleeve.

            - Seal: Mechanical.

Motor characteristics, such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency, are specified in Section 220513 "Common Motor Requirements for Plumbing Equipment." If different characteristics are required, insert subparagraphs below to suit Project.

          - Motor: General requirements for motors are specified in Section 220513 "Common Motor Requirements for Plumbing Equipment."

        - Controls: Automatic for control of circulating pump and separator purge; factory wired for single, external electrical connection.

          - Panel: NEMA 250, [Type 4] <Insert type> enclosure.

          - Pump: Automatic and manual.

          - Separator Purge: Automatic and manual.

        - Support: Skid mounting.

        - Capacity and Characteristics:

          - Filtrate Design Concentrations:

            - Sand: <Insert ppm (mg/L)>.

            - Silt: <Insert ppm (mg/L)>.

            - <Insert characteristic>: <Insert value>.

          - Separator Design:

            - Continuous Flow: <Insert gpm (L/s)> at [5 psig (34.5 kPa)] <Insert value> pressure drop.

            - Peak Flow: <Insert gpm (L/s)>.

            - Separator Efficiency: [98] <Insert number> percent removal of listed [1.8] <Insert number> minimum specific-gravity suspended particles [5] [10] [20] [45] <Insert size> microns and larger from feedwater of listed filtrate design concentrations.

          - Housing:

            - Material: [Carbon] [Stainless] steel.

            - Pressure Rating: <Insert psig (kPa)>.

            - Diameter: <Insert inches (mm)>.

            - Height: <Insert inches (mm)>.

            - Inlet and Outlet Size: <Insert NPS (DN)>.

            - Purge Size: <Insert NPS (DN)>.

Retain "Circulating Pump" Subparagraph below only if separator is circulating type.

          - Circulating Pump:

            - Capacity: <Insert gpm (L/s)>.

            - Total Dynamic Head: <Insert feet (kPa)>.

            - Speed: <Insert rpm>.

            - Inlet Size: <Insert NPS (DN)>.

            - Outlet Size: <Insert NPS (DN)>.

          - Pump Motor Size and Electrical Characteristics:

            - Horsepower: <Insert value>.

            - Volts: [120] [208] [240] [277] [480] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: [60] <Insert value>.

          - Unit Electrical Characteristics:

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage> A.

      - SOURCE QUALITY CONTROL

Retain first paragraph below for carbon and sand filters and for separators.

        - Before shipping, hydrostatically test [carbon-type filters,] [circulating sand-type filters,] [multimedia sand-type filters,] [greensand-type filters,] [and] [separators] to minimum of one and one-half times pressure rating.

        - Prepare test reports.

- EXECUTION

      - EXAMINATION

        - Examine areas and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of [filters] [and] [separators].

        - Examine roughing-in for piping systems to verify actual locations of piping connections before equipment installation.

        - Examine walls and floors for suitable conditions where [filters] [and] [separators] will be installed.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - EQUIPMENT MOUNTING

Retain "Equipment Mounting" Paragraph below for equipment supported on slabs-on-grade.

        - Equipment Mounting: Install [filters, except wall-mounted cartridge-type filters,] [and] [separators] on concrete bases. Comply with requirements for concrete bases specified in Section 033000 "Cast-in-Place Concrete."

          - Install dowel rods to connect concrete base to concrete floor. Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around full perimeter of concrete base.

          - For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

          - Place and secure anchorage devices. Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

          - Install anchor bolts to elevations required for proper attachment to supported equipment.

      - INSTALLATION OF BAG-TYPE FILTER

        - Install bag-type filters level and plumb, in accordance with layout drawings, original design, and referenced standards. Maintain manufacturer's recommended clearances. Arrange units so controls and devices needing service are accessible.

Retain "Equipment Mounting" Paragraph below for cast-in-place concrete equipment base.

        - Equipment Mounting: Install filters on concrete base. Comply with requirements for concrete base specified in Section 033000 "Cast-in-Place Concrete."

        - Install filter media bags.

Retain paragraph below for Project in a seismic area. Insert special requirements for seismic restraints here or detail on Drawings.

        - Install seismic restraints for bag-type filter housings and anchor to building structure.

      - INSTALLATION OF CARTRIDGE-TYPE FILTER

        - Install cartridge-type filters level and plumb, in accordance with layout drawings, original design, and referenced standards. Maintain manufacturer's recommended clearances. Arrange units so controls and devices needing service are accessible.

Retain "Equipment Mounting" Paragraph below for cast-in-place concrete equipment base.

        - Equipment Mounting: Install freestanding cartridge-type filters on concrete base. Comply with requirements for concrete base specified in Section 033000 "Cast-in-Place Concrete."

          - Exception: Omit concrete bases if installation directly on floor is indicated.

        - Attach wall brackets for off-floor, wall-mounted, cartridge filter to vertical surface. Attach housing(s), and base if any, to wall bracket.

        - Install housings for off-floor, in-line, cartridge filters in piping.

        - Install filter elements in cartridges.

Retain paragraph below for Project in a seismic area. Insert special requirements for seismic restraints here or detail on Drawings.

        - Install seismic restraints for freestanding cartridge-filter housings and anchor to building structure.

      - INSTALLATION OF CARBON-TYPE FILTER

        - Install carbon-type filters level and plumb, in accordance with layout drawings, original design, and referenced standards. Maintain manufacturer's recommended clearances. Arrange units so controls and devices needing service are accessible.

Retain "Equipment Mounting" Paragraph below for cast-in-place concrete equipment base.

        - Equipment Mounting: Install carbon-type filters on concrete base. Comply with requirements for concrete base specified in Section 033000 "Cast-in-Place Concrete."

        - Prepare carbon-filter tank distribution system and underbed, if any, for filter media, and place specified media into tanks.

Retain paragraph below for Project in a seismic area. Insert special requirements for seismic restraints here or detail on Drawings.

        - Install seismic restraints for carbon-filter housings and anchor to building structure.

      - INSTALLATION OF SAND-TYPE FILTER

        - Install sand-type filters level and plumb, in accordance with layout drawings, original design, and referenced standards. Maintain manufacturer's recommended clearances. Arrange units so controls and devices needing service are accessible.

Retain "Equipment Mounting" Paragraph below for cast-in-place concrete equipment base.

        - Equipment Mounting: Install sand-filter tanks on concrete base. Comply with requirements for concrete base specified in Section 033000 "Cast-in-Place Concrete."

        - Prepare sand-filter tank distribution system and underbed for filter media, and place specified sand and other media into tanks.

Retain paragraph below for Project in a seismic area. Insert special requirements for seismic restraints here or detail on Drawings.

        - Install seismic restraints for sand-filter tanks and accessories and anchor to building structure.

      - INSTALLATION OF SEPARATOR

        - Install separators level and plumb, in accordance with layout drawings, original design, and referenced standards. Maintain manufacturer's recommended clearances. Arrange units so controls and devices needing service are accessible.

Retain "Equipment Mounting" Paragraph below for cast-in-place concrete equipment base.

        - Equipment Mounting: Install separators on concrete base. Comply with requirements for concrete base specified in Section 033000 "Cast-in-Place Concrete."

Retain paragraph below for Project in a seismic area. Insert special requirements for seismic restraints here or detail on Drawings.

        - Install seismic restraints for separators and accessories and anchor to building structure.

      - PIPING CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Comply with requirements for piping specified in Section 221116 "Domestic Water Piping." Drawings indicate general arrangement of piping, fittings, and specialties.

        - Install piping adjacent to equipment to allow service and maintenance.

        - Make piping connections between water filtration equipment and dissimilar-metal water piping with dielectric fittings. Comply with requirements for dielectric fittings specified in Section 221116 "Domestic Water Piping."

        - Install shutoff valves on feedwater-inlet and filtrate-outlet piping of each water filtration equipment [filter] [and] [separator] [ and on inlet and outlet headers].

          - Comply with requirements for metal general-duty valves specified in Section 220523.12 "Ball Valves for Plumbing Piping," Section 220523.13 "Butterfly Valves for Plumbing Piping," and Section 220523.15 "Gate Valves for Plumbing Piping."

          - Comply with requirements for plastic valves specified in Section 221116 "Domestic Water Piping."

Retain "Exception, Shutoff Valve Installation" Subparagraph below if factory-installed valves are acceptable.

          - Exception, Shutoff Valve Installation: Water filtration equipment with factory-installed shutoff valves at locations indicated.

        - Install pressure gauges on feedwater-inlet and filtrate-outlet piping of each water filtration equipment [filter] [and] [separator]. Comply with requirements for pressure gauges specified in Section 220519 "Meters and Gauges for Plumbing Piping."

          - Exception, Pressure Gauge Installation:

Retain first subparagraph below if factory-installed pressure gauges are acceptable.

            - Water filtration equipment with factory-installed pressure gauges.

Retain subparagraph below if pressure gauges are not required.

            - Cartridge-type water filters.

        - Install valved bypass water piping around each water filtration equipment [filter] [and] [separator].

          - Comply with requirements for metal general-duty valves specified in Section 220523.12 "Ball Valves for Plumbing Piping," Section 220523.13 "Butterfly Valves for Plumbing Piping," Section 220523.14 "Check Valves for Plumbing Piping," and Section 220523.15 "Gate Valves for Plumbing Piping."

          - Comply with requirements for plastic valves specified in Section 221116 "Domestic Water Piping."

          - Comply with requirements for water piping specified in Section 221116 "Domestic Water Piping."

          - Exception, Valved Bypass Water Piping Installation:

Retain one of or both subparagraphs below if bypass is not required.

            - Bag-type water filtration equipment.

            - Cartridge-type water filtration equipment.

Confirm size of drain is adequate to receive discharge of equipment drains during backwash function without splashing or overflowing.

        - Install drains as indirect wastes to spill into open drains or over floor drains.

      - IDENTIFICATION

        - Identify system components. Comply with requirements for identification specified in Section 220553 "Identification for Plumbing Piping and Equipment."

      - STARTUP SERVICE

        - [Engage a factory-authorized service representative to perform] [Perform] startup service for [circulating sand-type filters,] [multimedia sand-type filters,] [greensand-type filters,] [and] [separators].

          - Complete installation and startup checks according to manufacturer's written instructions.

          - <Insert additional startup steps if any>.

        - Sample [filter] [and] [separator] filtrate after startup and at three consecutive seven-day intervals (total of four samples), and prepare certified test reports for required water performance characteristics.

      - FIELD QUALITY CONTROL

Retain first option in "Testing Agency" Paragraph below if Owner hires an independent testing agency.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain "Manufacturer Field Services" Paragraph below to require a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

        - Manufacturer's Field Service, Including Testing: Engage a factory-authorized service representative to [support] [supervise] field tests and inspections.

Retain "Tests and Inspections" Paragraph below to describe tests and inspections to be performed.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Tests and Inspections:

          - Leak Test: After installation, charge system and test for leaks. Repair leaks and retest until no leaks exist.

Retain "Operational Test" Subparagraph below only for units with pump, controls, or electrical devices.

          - Operational Test: After electrical circuitry has been energized, start units to confirm proper unit operation.

Retain subparagraph below only for units with controls or other devices.

          - Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Domestic water filtration equipment will be considered defective if it does not pass tests and inspections.

        - Prepare test and inspection reports.

      - DEMONSTRATION

        - [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain [circulating sand-type filters,] [multimedia sand-type filters,] [greensand-type filters,] [and] [separators].

END OF SECTION 223200