Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 224500 - EMERGENCY PLUMBING FIXTURES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Emergency showers.

          - Eyewash equipment.

          - Eye/face wash equipment.

          - Combination units.

          - Laboratory recessed safety station.

          - Supplemental equipment.

          - Water-tempering equipment.

      - DEFINITIONS

Definitions in this article are from standards, references, and model plumbing codes.

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - Accessible Fixture: Emergency plumbing fixture that can be approached, entered, and used by people with disabilities.

        - Plumbed Emergency Plumbing Fixture: Fixture with fixed, potable-water supply.

        - Portable, Self-Contained Emergency Plumbing Fixture: Fixture with flushing-fluid supply.

        - Tepid: Between 60 and 100 deg F (16 and 38 deg C).

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data: For each type of product indicated. Include flow rates and capacities, furnished specialties, and accessories.

        - Shop Drawings:

          - Plans, elevations, sections, and [mounting] [attachment] details.

          - Details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

          - Vibration Isolation Base Details: Detail fabrication including anchorages and attachments to structure and to supported equipment. Include adjustable motor bases, rails, and frames for equipment mounting.

Retain subparagraph below if fixtures include electrical components and wiring.

          - Diagrams for power, signal, and control wiring.

      - INFORMATIONAL SUBMITTALS

Information submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

        - Field Quality-Control Submittals:

Retain "Field quality-control reports" Subparagraph below if Contractor is responsible for field quality-control testing and inspecting.

          - Field quality-control reports.

        - Emergency fixture third-party certification documentation.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For emergency plumbing fixtures.

      - MAINTENANCE MATERIAL SUBMITTALS

See Section 017700 "Closeout Procedures" for submission of maintenance material items.

        - Extra Stock Material: Furnish extra materials to Owner that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Flushing-Fluid Solution: Separate lot and equal to at least [200] <Insert number> percent of amount of solution installed for each self-contained unit.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - PERFORMANCE REQUIREMENTS

        - Comply with ANSI/ISEA Z358.1 for emergency plumbing fixtures including third-party certification of fixtures.

        - Comply with ASSE 1071 for temperature-actuated mixing valves for plumbed emergency fixtures.

        - Comply with ASME A112.18.1/CSA B125.1 for water-supply fittings.

        - Comply with ASME A112.18.2/CSA B125.2 for plumbing waste fittings.

        - Comply with NSF 61 and NSF 372 for fixture materials that will be in contact with potable water.

Retain first paragraph below if fixtures include accessible emergency plumbing fixtures.

        - Comply with requirements in ICC A117.1 for plumbing fixtures for people with disabilities.

Retain "Electrical Components, Devices, and Accessories" Paragraph below for electrical components.

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

      - EMERGENCY SHOWERS

Copy "Emergency Showers - Freestanding, Plumbed" Paragraph below and re-edit for each type of freestanding, plumbed emergency shower required.

Insert drawing designation. Use these designations on Drawings to identify each emergency shower.

        - Emergency Showers - Freestanding, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain emergency showers, freestanding, plumbed, from single manufacturer.

          - Capacity: Not less than 20 gpm (76 L/min.) for at least 15 minutes.

          - Supply Piping: [NPS 1 (DN 25)] [NPS 1-1/4 (DN 32)] [galvanized steel] [chrome-plated brass or stainless steel] [PVC] with flow regulator and stay-open control valve.

          - Control-Valve Actuator: Pull rod.

          - Shower Head: 8-inch- (200-mm-) minimum-diameter, [chrome-plated brass, stainless steel, or plastic] <Insert material>.

          - Mounting: Pedestal[, accessible].

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Modesty curtain.

            - Magnetically actuated proximity switch.

            - 60-inch (1524-mm) pull rod.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

Copy "Emergency Showers - Off Floor, Plumbed" Paragraph below and re-edit for each type of off-floor, plumbed emergency shower required.

Insert drawing designation. Use these designations on Drawings to identify each emergency shower.

        - Emergency Showers - Off Floor, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain emergency showers, off floor, plumbed, from single manufacturer.

          - Capacity: Not less than 20 gpm (76 L/min.) for at least 15 minutes.

          - Supply Piping: NPS 1 (DN 25) [galvanized steel] [chrome-plated brass or stainless steel] [PVC] with flow regulator and stay-open control valve.

          - Control-Valve Actuator: [Pull rod] [Wall-mounted, fully recessed, stainless steel enclosure with vandal-resistant access panel].

          - Shower Head: 8-inch- (200-mm-) minimum-diameter, [chrome-plated brass, stainless steel, or plastic] <Insert material>.

          - Mounting: [Horizontal from wall] [Vertical from ceiling] [, accessible] and supported from structure.

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Modesty curtain.

            - Magnetically actuated proximity switch.

            - 60-inch (1524-mm) pull rod.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

Emergency shower in "Emergency Showers - Freeze Protected, Plumbed" Paragraph below requires data for ambient temperature or heating capacity.

Copy paragraph and re-edit for each type of freeze-protected, plumbed emergency shower required.

Insert drawing designation. Use these designations on Drawings to identify each emergency shower.

        - Emergency Showers - Freeze Protected, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain emergency showers, freeze protected, plumbed, from single manufacturer.

          - Capacity: Not less than 20 gpm (76 L/min.) for at least 15 minutes.

          - Supply Piping: NPS 1 (DN 25) [galvanized steel] [chrome-plated brass or stainless steel] [PVC] with flow regulator and stay-open control valve.

          - Control-Valve Actuator: Wall-mounted push handle.

          - Shower Head: 8-inch- (200-mm-) minimum-diameter, [chrome-plated brass, stainless steel, or plastic] <Insert material>.

          - Mounting: Horizontal from wall[, accessible]. Concealed piping within heated space.

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Modesty curtain.

            - Magnetically actuated proximity switch.

            - 60-inch (1524-mm) pull rod.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

      - EYEWASH EQUIPMENT

Copy "Eyewash Units - Standard, Freestanding, Plumbed" Paragraph below and re-edit for each type of standard, freestanding, plumbed eyewash unit required.

Insert drawing designation. Use these designations on Drawings to identify each eyewash unit.

        - Eyewash Units - Standard, Freestanding, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain eyewash units, standard, freestanding, plumbed, from single manufacturer.

          - Capacity: Not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

          - Supply Piping: NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

          - Control-Valve Actuator: [Paddle] [Treadle] <Insert actuator>.

          - Spray-Head Assembly: Two receptor-mounted spray heads.

          - Receptor: [Chrome-plated brass or stainless steel] [Plastic] bowl.

          - Drain Piping:

            - Size: NPS 1-1/4 (DN 32) minimum.

            - Finish: Chrome-plated brass.

            - Fittings: Receptor drain, P-trap, waste to wall, and wall flange.

          - Mounting: Pedestal.

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Dust covers.

            - Magnetically actuated proximity switch.

            - Scald protection valve.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

Copy "Eyewash Units - Accessible, Freestanding, Plumbed" Paragraph below and re-edit for each type of accessible, freestanding, plumbed eyewash unit required.

Insert drawing designation. Use these designations on Drawings to identify each eyewash unit.

        - Eyewash Units - Accessible, Freestanding, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain eyewash units, accessible, freestanding, plumbed, from single manufacturer.

          - Capacity: Not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

          - Supply Piping: NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

          - Control-Valve Actuator: [Paddle] <Insert actuator>.

          - Spray-Head Assembly: Two receptor-mounted spray heads.

          - Receptor: [Chrome-plated brass or stainless steel] [Plastic] bowl.

          - Drain Piping:

            - Size: NPS 1-1/4 (DN 32) minimum.

            - Finish: Chrome-plated brass.

            - Fittings: Receptor drain, P-trap, waste to wall, and wall flange.

          - Mounting: Offset pedestal.

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Dust covers.

            - Magnetically actuated proximity switch.

            - Scald protection valve.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

Copy "Eyewash Units - Standard, Wall Mounted, Plumbed" Paragraph below and re-edit for each type of standard, wall-mounted, plumbed eyewash unit required.

Insert drawing designation. Use these designations on Drawings to identify each eyewash unit.

        - Eyewash Units - Standard, Wall Mounted, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain eyewash units, standard, wall mounted, plumbed, from single manufacturer.

          - Capacity: Not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

          - Supply Piping: NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

          - Control-Valve Actuator: [Paddle] <Insert actuator>.

          - Spray-Head Assembly: Two receptor-mounted spray heads.

          - Receptor: [Chrome-plated brass or stainless steel] <Insert material> bowl.

          - Drain Piping:

            - Size: NPS 1-1/4 (DN 32) minimum.

            - Finish: Chrome-plated brass.

            - Fittings: Receptor drain, P-trap, waste to wall, and wall flange.

          - Mounting: Wall bracket.

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Dust covers.

            - Magnetically actuated proximity switch.

            - Scald protection valve.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

Copy "Eyewash Units - Accessible, Wall Mounted, Plumbed" Paragraph below and re-edit for each type of accessible, wall-mounted, plumbed eyewash unit required.

Insert drawing designation. Use these designations on Drawings to identify each eyewash unit.

        - Eyewash Units - Accessible, Wall Mounted, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain eyewash units, accessible, wall mounted, plumbed, from single manufacturer.

          - Capacity: Not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

          - Supply Piping: NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

          - Control-Valve Actuator: [Paddle] <Insert actuator>.

          - Spray-Head Assembly: Two receptor-mounted spray heads.

          - Receptor: [Chrome-plated brass or stainless steel] <Insert material> bowl.

          - Drain Piping:

            - Size: NPS 1-1/4 (DN 32) minimum.

            - Finish: Chrome-plated brass.

            - Fittings: Receptor drain, P-trap, waste to wall, and wall flange.

          - Mounting: Wall bracket.

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Dust covers.

            - Magnetically actuated proximity switch.

            - Scald protection valve.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

Copy "Eyewash Units - (Deck) (Wall) Mounted, Swivel Type, Plumbed" Paragraph below and re-edit for each type of deck- or wall-mounted, swivel-type, plumbed eyewash unit required.

Insert drawing designation. Use these designations on Drawings to identify each eyewash unit.

        - Eyewash Units - [Deck] [Wall] Mounted, Swivel Type, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain eyewash units, [deck] [wall] mounted, swivel type, plumbed, from single manufacturer.

          - Capacity: Not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

          - Supply Piping: NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

          - Control-Valve Actuator: Movement of spray-head assembly to position over sink.

          - Spray-Head Assembly: Two spray heads with offset piping.

          - Mounting: [Deck mounted next to sink] [Deck mounted on sink] [Wall mounted behind sink] <Insert mounting>.

Copy "Eyewash Units - Portable, Self-Contained" Paragraph below and re-edit for each type of portable, self-contained eyewash unit required.

Insert drawing designation. Use these designations on Drawings to identify each eyewash unit.

        - Eyewash Units - Portable, Self-Contained: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain eyewash units, portable, self-contained, from single manufacturer.

          - Capacity: Not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

          - Pressure Tank: [10 gal. (38 L)] <Insert value>, stainless steel, cylindrical, with pressure gage, and suitable for on-floor installation.

          - Flushing Fluid: Medically acceptable solution manufactured and labeled in accordance with applicable regulations.

          - Spray-Head Assembly: Chrome-plated copper alloy or stainless steel piping with flow regulator; paddle-actuated, stay-open control valve; and two spray heads mounted on tank.

Hose in "Drench Hose" Subparagraph below is an optional component.

          - Drench Hose: Handheld spray head with squeeze-handle actuation and hose attached to tank.

Copy "Eyewash Units - Standard, Self-Contained" Paragraph below and re-edit for each type of standard, self-contained eyewash unit required.

Insert drawing designation. Use these designations on Drawings to identify each eyewash unit.

        - Eyewash Units - Standard, Self-Contained: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain eyewash units, standard, self-contained, from single manufacturer.

          - Capacity: Not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

          - Gravity Tank: [7 gal. (27 L) minimum] <Insert value>, plastic, and suitable for shelf mounting.

          - Flushing Fluid: Medically acceptable solution manufactured and labeled in accordance with applicable regulations.

          - Actuator: Pull-down front panel or pull strap.

          - Spray Heads: Protected, two mounted on tank.

Copy "Eyewash Units - Freeze Protected, Self-Contained" Paragraph below and re-edit for each type of freeze-protected, self-contained eyewash unit required.

Insert drawing designation. Use these designations on Drawings to identify each eyewash unit.

        - Eyewash Units - Freeze Protected, Self-Contained: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain eyewash units, freeze protected, self-contained, from single manufacturer.

          - Capacity: Not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

          - Gravity Tank: [7 gal. (27 L) minimum] [14 gal. (53 L) minimum] [20 gal. (76 L) minimum] <Insert value>, plastic, and suitable for shelf mounting.

          - Flushing Fluid: Medically acceptable solution manufactured and labeled in accordance with applicable regulations.

          - Actuator: Pull-down front panel or pull strap.

          - Spray Heads: Protected, two mounted on tank.

          - Heating System: Electric, 120 V ac; insulation enclosed in a protective jacket.

      - EYE/FACE WASH EQUIPMENT

Copy "Eye/Face Wash Units - Standard, Freestanding, Plumbed" Paragraph below and re-edit for each type of standard, freestanding, plumbed eye/face wash unit required.

Insert drawing designation. Use these designations on Drawings to identify each eye/face wash unit.

        - Eye/Face Wash Units - Standard, Freestanding, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain eye/face wash units, standard, freestanding, plumbed, from single manufacturer.

          - Capacity: Not less than 3.0 gpm (11.4 L/min.) for at least 15 minutes.

          - Supply Piping: NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

          - Control-Valve Actuator: [Paddle] [Treadle] <Insert actuator>.

          - Spray-Head Assembly: Two or four receptor-mounted spray heads.

          - Receptor: [Chrome-plated brass or stainless steel] [Plastic] bowl.

          - Drain Piping:

            - Size: NPS 1-1/4 (DN 32) minimum.

            - Finish: Chrome-plated brass.

            - Fittings: Receptor drain, P-trap, waste to wall, and wall flange complying with ASME A112.18.2/CSA B125.2.

          - Mounting: Pedestal.

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Dust covers.

            - Magnetically actuated proximity switch.

            - Scald protection valve.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

Copy "Eye/Face Wash Units - Accessible, Freestanding, Plumbed" Paragraph below and re-edit for each type of accessible, freestanding, plumbed eye/face wash unit required.

Insert drawing designation. Use these designations on Drawings to identify each eye/face wash unit.

        - Eye/Face Wash Units - Accessible, Freestanding, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain eye/face wash units, accessible, freestanding, plumbed, from single manufacturer.

          - Capacity: Not less than 3.0 gpm (11.4 L/min.) for at least 15 minutes.

          - Supply Piping: NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

          - Control-Valve Actuator: [Paddle] <Insert actuator>.

          - Spray-Head Assembly: Two or four receptor-mounted spray heads.

          - Receptor: [Chrome-plated brass or stainless steel] [Plastic] bowl.

          - Drain Piping:

            - Size: NPS 1-1/4 (DN 32) minimum.

            - Finish: Chrome-plated brass.

            - Fittings: Receptor drain, P-trap, waste to wall, and wall flange complying with ASME A112.18.2/CSA B125.2.

          - Mounting: Offset pedestal.

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Dust covers.

            - Magnetically actuated proximity switch.

            - Scald protection valve.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

Copy "Eye/Face Wash Units - Standard, Wall Mounted, Plumbed" Paragraph below and re-edit for each type of standard, wall-mounted, plumbed eye/face wash unit required.

Insert drawing designation. Use these designations on Drawings to identify each eye/face wash unit.

        - Eye/Face Wash Units - Standard, Wall Mounted, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain eye/face wash units, standard, wall mounted, plumbed, from single manufacturer.

          - Capacity: Not less than 3.0 gpm (11.4 L/min.) for at least 15 minutes.

          - Supply Piping: NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

          - Control-Valve Actuator: [Paddle] <Insert actuator>.

          - Spray-Head Assembly: Two or four receptor-mounted spray heads.

          - Receptor: [Chrome-plated brass or stainless steel] <Insert material> bowl.

          - Drain Piping:

            - Size: NPS 1-1/4 (DN 32) minimum.

            - Finish: Chrome-plated brass.

            - Fittings: Receptor drain, P-trap, waste to wall, and wall flange complying with ASME A112.18.2/CSA B125.2.

          - Mounting: Wall bracket.

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Dust covers.

            - Magnetically actuated proximity switch.

            - Scald protection valve.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

Copy "Eye/Face Wash Units - Accessible, Wall Mounted, Plumbed" Paragraph below and re-edit for each type of accessible, wall-mounted, plumbed eye/face wash unit required.

Insert drawing designation. Use these designations on Drawings to identify each eye/face wash unit.

        - Eye/Face Wash Units - Accessible, Wall Mounted, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain eye/face wash units, accessible, wall mounted, plumbed, from single manufacturer.

          - Capacity: Not less than 3.0 gpm (11.4 L/min.) for at least 15 minutes.

          - Supply Piping: NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

          - Control-Valve Actuator: [Paddle] <Insert actuator>.

          - Spray-Head Assembly: Two or four receptor-mounted spray heads.

          - Receptor: [Chrome-plated brass or stainless steel] <Insert material> bowl.

          - Mounting: Wall bracket.

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Dust covers.

            - Magnetically actuated proximity switch.

            - Scald protection valve.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

Copy "Eye/Face Wash Units - (Deck) (Wall) Mounted, Swivel Type, Plumbed" Paragraph below and re-edit for each type of deck- or wall-mounted, swivel-type, plumbed eye/face wash unit required.

Insert drawing designation. Use these designations on Drawings to identify each eye/face wash unit.

        - Eye/Face Wash Units - [Deck] [Wall] Mounted, Swivel Type, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain eye/face wash units, [deck] [wall] mounted, swivel type, plumbed, from single manufacturer.

          - Capacity: Not less than 3 gpm (11.4 L/min.) for at least 15 minutes.

          - Supply Piping: NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

          - Control-Valve Actuator: Movement of spray-head assembly to position over sink.

          - Spray-Head Assembly: Two or four spray heads with offset piping.

          - Receptor: [Chrome-plated brass or stainless steel] <Insert material> bowl.

          - Mounting: [Deck mounted next to sink] [Deck mounted on sink] [Wall mounted behind sink] <Insert mounting>.

Copy "Eye/Face Wash Units - Deck Mounted, Plumbed" Paragraph below and re-edit for each type of deck-mounted, plumbed eye/face wash unit required.

Insert drawing designation. Use these designations on Drawings to identify each eye/face wash unit.

        - Eye/Face Wash Units - Deck Mounted, Plumbed: <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain eye/face wash units, deck mounted, plumbed, from single manufacturer.

          - Capacity: Not less than 3 gpm (11.4 L/min.) for at least 15 minutes.

          - Supply Piping: NPS 1/2 (DN 15) chrome-plated brass or stainless steel with flow regulator and stay-open control valve.

          - Control-Valve Actuator: Paddle.

          - Spray-Head Assembly: Two or four spray heads.

          - Receptor: [Chrome-plated brass or stainless steel] <Insert material> bowl.

          - Drain Piping:

            - Size: NPS 1-1/4 (DN 32) minimum.

          - Mounting: Deck.

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Dust covers.

            - Magnetically actuated proximity switch.

            - Scald protection valve.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

      - COMBINATION UNITS

Copy "Combination Units - Emergency Shower with Eyewash, Standard, Plumbed" Paragraph below and re-edit for each type of emergency shower with eyewash, standard, plumbed combination unit required.

Insert drawing designation. Use these designations on Drawings to identify each combination unit.

        - Combination Units - Emergency Shower with Eyewash, Standard, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain combination units, emergency shower with eyewash, standard, plumbed, from single manufacturer.

          - Piping:

            - Material: [Galvanized steel] [Chrome-plated brass or stainless steel] [PVC].

            - Unit Supply: [NPS 1-1/4 (DN 32) minimum] [NPS 1-1/2 (DN 40)].

            - Unit Drain: Outlet at back or side near bottom.

          - Shower:

            - Capacity: Not less than 20 gpm (76 L/min.) for at least 15 minutes.

            - Supply Piping: NPS 1 (DN 25) with flow regulator and stay-open control valve.

            - Control-Valve Actuator: [Pull rod] [Treadle] <Insert actuator>.

            - Shower Head: 8-inch- (200-mm-) minimum diameter, [chrome-plated brass or stainless steel] [plastic].

            - Mounting: Pedestal.

          - Eyewash Unit:

            - Capacity: Not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

            - Supply Piping: NPS 1/2 (DN 15) with flow regulator and stay-open control valve.

            - Control-Valve Actuator: Paddle.

            - Spray-Head Assembly: Two receptor-mounted spray heads.

            - Receptor: [Chrome-plated brass or stainless steel] [Plastic] bowl.

            - Mounting: Attached shower pedestal.

Retain "Drench-Hose Option" Subparagraph below if a drench hose is permitted in place of the eyewash unit.

            - Drench-Hose Option: May be provided instead of eyewash unit.

              - Capacity: Not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

              - Drench Hose: Handheld spray head with squeeze-handle actuator and hose.

              - Mounting: Bracket on shower pedestal.

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Modesty curtain.

            - Magnetically actuated proximity switch.

            - 60-inch (1524-mm) pull rod.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

Copy "Combination Units - Emergency Shower with Eyewash, Accessible, Plumbing" Paragraph below and re-edit for each type of emergency shower with eyewash, accessible, plumbed combination unit required.

Insert drawing designation. Use these designations on Drawings to identify each combination unit.

        - Combination Units - Emergency Shower with Eyewash, Accessible, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain combination units, emergency shower with eyewash, accessible, plumbed, from single manufacturer.

          - Piping:

            - Material: [Galvanized steel] [Chrome-plated brass or stainless steel] [PVC].

            - Unit Supply: [NPS 1-1/4 (DN 32) minimum] [NPS 1-1/2 (DN 40)].

            - Unit Drain: Outlet at back or side near bottom.

          - Shower:

            - Capacity: Not less than 20 gpm (76 L/min.) for at least 15 minutes.

            - Supply Piping: NPS 1 (DN 25) with flow regulator and stay-open control valve.

            - Control-Valve Actuator: [Pull rod] <Insert actuator>.

            - Shower Head: 8-inch- (200-mm-) minimum diameter, [chrome-plated brass or stainless steel] [plastic].

            - Mounting: Pedestal.

          - Eyewash Unit:

            - Capacity: Not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

            - Supply Piping: NPS 1/2 (DN 15) with flow regulator and stay-open control valve.

            - Control-Valve Actuator: Paddle.

            - Spray-Head Assembly: Two receptor-mounted spray heads.

            - Receptor: [Chrome-plated brass or stainless steel] [Plastic] bowl.

            - Mounting: Attached shower pedestal.

Retain "Drench-Hose Option" Subparagraph below if a drench hose is permitted in place of the eyewash unit.

            - Drench-Hose Option: May be provided instead of eyewash unit.

              - Capacity: Not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

              - Drench Hose: Handheld spray head with squeeze-handle actuator and hose.

              - Mounting: Bracket on shower pedestal.

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Modesty curtain.

            - Magnetically actuated proximity switch.

            - 60-inch (1524-mm) pull rod.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

Copy "Combination Units - Emergency Shower with Eye/Face Wash, Standard, Plumbed" Paragraph below and re-edit for each type of emergency shower with eye/face wash, standard, plumbed combination unit required.

Insert drawing designation. Use these designations on Drawings to identify each combination unit.

        - Combination Units - Emergency Shower with Eye/Face Wash, Standard, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain combination units, emergency shower with eye/face wash, standard, plumbed, from single manufacturer.

          - Piping:

            - Material: [Galvanized steel] [Chrome-plated brass or stainless steel] [PVC].

            - Unit Supply: [NPS 1-1/4 (DN 32) minimum] [NPS 1-1/2 (DN 40)].

            - Unit Drain: Outlet at back or side near bottom.

          - Shower:

            - Capacity: Not less than 20 gpm (76 L/min.) for at least 15 minutes.

            - Supply Piping: NPS 1 (DN 25) with flow regulator and stay-open control valve.

            - Control-Valve Actuator: [Pull rod] [Treadle] <Insert actuator>.

            - Shower Head: 8-inch- (200-mm-) minimum diameter, [chrome-plated brass or stainless steel] [plastic].

            - Mounting: Pedestal.

          - Eye/Face Wash Unit:

            - Capacity: Not less than 3.0 gpm (11.4 L/min.) for at least 15 minutes.

            - Supply Piping: NPS 1/2 (DN 15) with flow regulator and stay-open control valve.

            - Control-Valve Actuator: Paddle.

            - Spray-Head Assembly: Two or four receptor-mounted spray heads.

            - Receptor: [Chrome-plated brass or stainless steel] [Plastic] bowl.

            - Mounting: Attached shower pedestal.

Retain "Drench-Hose Option" Subparagraph below if a drench hose is permitted in place of the eye/face wash unit.

            - Drench-Hose Option: May be provided instead of eye/face wash unit.

              - Capacity: Not less than 3.0 gpm (11.4 L/min.) for at least 15 minutes.

              - Drench Hose: Handheld spray head with squeeze-handle actuator and hose.

              - Mounting: Bracket on shower pedestal.

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Modesty curtain.

            - Magnetically actuated proximity switch.

            - 60-inch (1524-mm) pull rod.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

Copy "Combination Units - Emergency Shower with Eye/Face Wash, Accessible, Plumbed" Paragraph below and re-edit for each type of emergency shower with eye/face wash, accessible, plumbed combination unit required.

Insert drawing designation. Use these designations on Drawings to identify each combination unit.

        - Combination Units - Emergency Shower with Eye/Face Wash, Accessible, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain combination units, emergency shower with eye/face wash, accessible, plumbed, from single manufacturer.

          - Piping:

            - Material: [Galvanized steel] [Chrome-plated brass or stainless steel] [PVC].

            - Unit Supply: [NPS 1-1/4 (DN 32) minimum] [NPS 1-1/2 (DN 40)].

            - Unit Drain: Outlet at back or side near bottom.

          - Shower:

            - Capacity: Not less than 20 gpm (76 L/min.) for at least 15 minutes.

            - Supply Piping: NPS 1 (DN 25) with flow regulator and stay-open control valve.

            - Control-Valve Actuator: [Pull rod] <Insert actuator>.

            - Shower Head: 8-inch- (200-mm-) minimum diameter, [chrome-plated brass or stainless steel] [plastic].

            - Mounting: Pedestal.

          - Eye/Face Wash Unit:

            - Capacity: Not less than 3.0 gpm (11.4 L/min.) for at least 15 minutes.

            - Supply Piping: NPS 1/2 (DN 15) with flow regulator and stay-open control valve.

            - Control-Valve Actuator: Paddle.

            - Spray-Head Assembly: Two or four receptor-mounted spray heads.

            - Receptor: [Chrome-plated brass or stainless steel] [Plastic] bowl.

            - Mounting: Attached to shower pedestal.

Retain "Drench-Hose Option" Subparagraph below if a drench hose is permitted in place of the eye/face wash unit.

            - Drench-Hose Option: May be provided instead of eye/face wash unit.

              - Capacity: Not less than 3.0 gpm (11.4 L/min.) for at least 15 minutes.

              - Drench Hose: Handheld spray head with squeeze-handle actuator and hose.

              - Mounting: Bracket on shower pedestal.

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Modesty curtain.

            - Magnetically actuated proximity switch.

            - 60-inch (1524-mm) pull rod.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

Copy "Combination Units - Emergency Shower with (Eyewash) (Eye/Face Wash), Freeze Protected, Plumbed" Paragraph below and re-edit for each type of emergency shower with eyewash or eye/face wash, freeze-protected, plumbed combination unit required.

Insert drawing designation. Use these designations on Drawings to identify each combination unit.

        - Combination Units - Emergency Shower with [Eyewash] [Eye/Face Wash], Freeze Protected, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain combination units, emergency shower with [eyewash] [eye/face wash], freeze protected, plumbed, from single manufacturer.

          - Piping: Galvanized steel.

            - Unit Supply: [NPS 1-1/4 (DN 32) minimum] [NPS 1-1/2 (DN 40)] from bottom.

System in "Heating System" Subparagraph below requires data for ambient temperature or heating capacity.

          - Heating System: Electric, [120] [240] V ac; insulation enclosed in a protective jacket with thermometer.

            - Heating Capacity: [10 deg F (6 deg C)] <Insert temperature> minimum above ambient temperature.

            - Design Ambient Temperature: <Insert temperature>.

          - Shower:

            - Shower Capacity: Not less than 20 gpm (76 L/min.) for at least 15 minutes.

            - Supply Piping: NPS 1 (DN 25) with flow regulator and stay-open control valve.

            - Control-Valve Actuator: [Pull rod] <Insert actuator>.

            - Shower Head: 8-inch- (200-mm-) minimum diameter, [chrome-plated brass or stainless steel] [plastic].

            - Mounting: Pedestal.

Retain "Eyewash Unit" or "Eye/Face Wash Unit" Subparagraph below.

          - Eyewash Unit:

            - Capacity: Not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

            - Supply Piping: NPS 1/2 (DN 15) with flow regulator and stay-open control valve.

            - Control-Valve Actuator: [Paddle] <Insert actuator>.

          - Eye/Face Wash Unit:

            - Capacity: Not less than 3 gpm (11.4 L/min.) for at least 15 minutes.

            - Control-Valve Actuator: [Paddle] <Insert actuator>.

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Modesty curtain.

            - Magnetically actuated proximity switch.

            - 60-inch (1524-mm) pull rod.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

      - LABORATORY RECESSED SAFETY STATIONS

Copy "Laboratory Recessed Safety Station - Emergency Eye/Face Wash with Shower, Accessible, Plumbed" Paragraph below and re-edit for each type of laboratory recessed safety station required.

Insert drawing designation. Use these designations on Drawings to identify each combination unit.

        - Laboratory Recessed Safety Station - Emergency Eye/Face Wash with Shower, Accessible, Plumbed: <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain laboratory recessed safety station, emergency eye/face wash with shower, accessible, plumbed, from single manufacturer.

          - Eye/Face Wash Unit:

            - Capacity: Not less than 3 gpm (11.4 L/min.) for at least 15 minutes.

            - Supply Piping: NPS 1/2 (DN 15) with flow regulator and stay-open control valve.

            - Control-Valve Actuator: Pull handle on face of unit down from vertical to horizontal position.

            - Spray-Head Assembly: Two or four receptor-mounted spray heads.

            - Mounting: Wall-mounted, fully recessed, stainless steel enclosure with vandal-resistant access panel.

          - Shower:

            - Shower Capacity: Not less than 20 gpm (76 L/min.) for at least 15 minutes.

            - Supply Piping: NPS 1 (DN 25) with flow regulator and stay-open control valve.

            - Control-Valve Actuator: Pull handle on face of unit from up to down position.

            - Shower Head: 8-inch- (200-mm-) minimum diameter, [chrome-plated brass or stainless steel] [plastic].

            - Mounting: [Horizontal from wall] [Vertical from ceiling].

Retain "Accessories" Subparagraph below and required accessory(s) to suit Project. Verify availability of specific accessory with manufacturer.

          - Accessories:

            - Electric alarm with flashing light and horn.

            - Thermostatic mixing valve assembly including ball valve shutoffs and outlet temperature gauge.

            - Flow switch; single pole.

            - Modesty curtain.

            - Magnetically actuated proximity switch.

            - <Insert size> stainless steel ball valve.

            - <Insert accessory>.

      - SUPPLEMENTAL EQUIPMENT

Equipment in this article does not have capacity requirements. This equipment is provided in addition to, but not in place of, normally required equipment.

Copy "Personal Eyewash Units - Self-Contained" Paragraph below and re-edit for each type of self-contained, personal eyewash unit required.

Insert drawing designation. Use these designations on Drawings to identify each personal eyewash unit.

        - Personal Eyewash Units - Self-Contained: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain self-contained, personal eyewash units from single manufacturer.

          - Capacity: Not less than 0.4 gpm (1.5 L/min.).

          - Pressure Tank: [5 gal. (19 L)] <Insert value>, stainless steel, cylindrical, with pressure gage and base suitable for on-floor installation.

          - Flushing Fluid: Medically acceptable solution manufactured and labeled in accordance with applicable regulations.

          - Spray-Head Assembly: Chrome-plated copper alloy or stainless steel piping with flow regulator; paddle-actuated, stay-open control valve; and two spray heads mounted on tank.

Copy "Drench Hoses - Deck Mounted, Plumbed" Paragraph below and re-edit for each type of deck-mounted, plumbed drench hose required.

Insert drawing designation. Use these designations on Drawings to identify each drench hose.

        - Drench Hoses - Deck Mounted, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain drench hoses, deck mounted, plumbed, from single manufacturer.

          - Capacity: Not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

          - Supply Fitting: NPS 1/2 (DN 15) brass with flow regulator.

          - Drench Hose: Handheld spray head with [squeeze-handle] [push handle ball valve] actuation and hose.

          - Mounting: In hole on deck.

Copy "Drench Hoses - Wall Mounted, Plumbed" Paragraph below and re-edit for each type of wall-mounted, plumbed drench hose required.

Insert drawing designation. Use these designations on Drawings to identify each drench hose.

        - Drench Hoses - Wall Mounted, Plumbed: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain drench hoses, wall mounted, plumbed, from single manufacturer.

          - Capacity: Not less than 0.4 gpm (1.5 L/min.) for at least 15 minutes.

          - Supply Fitting: NPS 1/2 (DN 15) brass with flow regulator.

          - Drench Hose: Handheld spray head with [squeeze-handle] [push handle ball valve] actuation and hose.

          - Mounting: Wall bracket.

      - WATER-TEMPERING EQUIPMENT

Use equipment in this article only for emergency plumbing fixtures without an integral tempered-water system. Do not use general-use, thermostatic mixing valves or tempering valves. Revise temperatures to suit Project. Indicate capacities on Drawings.

Copy "Water-Tempering Equipment - Hot and Cold Water" Paragraph below and re-edit for each type of hot- and cold-water water-tempering equipment required.

Insert drawing designation. Use these designations on Drawings to identify each water-tempering equipment.

        - Water-Tempering Equipment - Hot and Cold Water: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain water-tempering equipment, hot and cold water, from single manufacturer.

          - Description: Factory-fabricated equipment with thermostatic mixing valve.

            - Thermostatic Mixing Valve: Designed to provide [85 deg F (29 deg C)] <Insert temperature> tepid, potable water at emergency plumbing fixtures, to maintain temperature at plus or minus [5 deg F (3 deg C)] <Insert temperature> throughout required 15-minute test period, and in case of unit failure to continue cold-water flow, with union connections, controls, metal piping, and corrosion-resistant enclosure.

            - Supply Connections: For hot and cold water.

Copy "Water-Tempering Equipment - Steam and Cold Water" Paragraph below and re-edit for each type of steam and cold-water water-tempering equipment required.

Insert drawing designation. Use these designations on Drawings to identify each water-tempering equipment.

        - Water-Tempering Equipment - Steam and Cold Water: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain water-tempering equipment, steam and cold water, from single manufacturer.

          - Description: Factory-fabricated equipment with thermostatic mixing valve.

            - Thermostatic Mixing Valve: Designed to provide [85 deg F (29 deg C)] <Insert temperature> tepid, potable water at emergency plumbing fixtures, to maintain temperature at plus or minus [5 deg F (3 deg C)] <Insert temperature> throughout required 15-minute test period, and in case of unit failure to continue cold-water flow, with union connections, steam controls, heat exchanger, high-temperature-limit and freeze-protection devices, metal piping, and corrosion-resistant enclosure.

            - Supply Connections: For steam and cold water.

Copy "Water-Tempering Equipment - Electric" Paragraph below and re-edit for each type of electric water-tempering equipment required.

Insert drawing designation. Use these designations on Drawings to identify each water-tempering equipment.

        - Water-Tempering Equipment - Electric: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain water-tempering equipment, electric, from single manufacturer.

          - Description: Factory-fabricated equipment with electric heating.

            - Heating System: Electric, designed to provide [85 deg F (29 deg C)] <Insert temperature> tepid, potable water at emergency plumbing fixtures, to maintain temperature at plus or minus [5 deg F (3 deg C)] <Insert temperature> throughout required 15-minute test period, and in case of unit failure to continue cold-water flow, with union connections, controls, heating coils, high-temperature-limit device, metal piping, and corrosion-resistant enclosure.

              - Electrical Characteristics: [208 V ac, single phase] [240 V ac, single phase] [277 V ac, single phase] [208 V ac, 3 phase] [240 V ac, 3 phase] [480 V ac, 3 phase], 60 Hz.

- EXECUTION

      - EXAMINATION

Retain this article for plumbed emergency plumbing fixtures. Delete option in first paragraph below if no direct-connection drain piping is required.

        - Examine roughing-in for water[ and waste] piping systems to verify actual locations of piping connections before plumbed emergency plumbing fixture installation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATON OF EMERGENCY PLUMBING FIXTURE

        - Assemble emergency plumbing fixture piping, fittings, control valves, and other components.

        - Install fixtures level and plumb.

        - Fasten fixtures to substrate.

        - Install shutoff valves in water-supply piping to fixtures, to facilitate maintenance of equipment. Use ball or gate valve if specific type valve is not indicated. Install valves chained or locked in open position if permitted. Install valves in locations where they can easily be reached for operation. Comply with requirements for valves specified in Section 220523.12 "Ball Valves for Plumbing Piping" and Section 220523.15 "Gate Valves for Plumbing Piping."

Retain "Exceptions" Subparagraph below if applicable.

          - Exceptions:

            - Omit shutoff valve on supply to group of plumbing fixtures that includes emergency equipment.

            - Omit shutoff valve on supply to emergency equipment if prohibited by authorities having jurisdiction.

Retain first paragraph below if steam-mixing valve is used.

        - Install shutoff valve and strainer in steam piping and shutoff valve in condensate return piping. Comply with requirements for steam and condensate piping specified in Section 232213 "Steam and Condensate Heating Piping" and Section 232216 "Steam and Condensate Heating Piping Specialties."

        - Install dielectric fitting in supply piping to emergency equipment if piping and equipment connections are made of different metals. Comply with requirements for dielectric fittings specified in Section 221116 "Domestic Water Piping."

        - Install thermometers in supply and outlet piping connections to water-tempering equipment. Comply with requirements for thermometers specified in Section 220519 "Meters and Gages for Plumbing Piping."

Retain first paragraph below if emergency equipment has a direct connection drain.

        - Install trap and waste piping on drain outlet of emergency equipment receptors that are indicated to be directly connected to drainage system. Comply with requirements for waste piping specified in Section 221316 "Sanitary Waste and Vent Piping."

Retain first paragraph below if emergency equipment has an indirect waste connection.

        - Install indirect waste piping on drain outlet of emergency equipment receptors that are indicated to be indirectly connected to drainage system. Comply with requirements for waste piping specified in Section 221316 "Sanitary Waste and Vent Piping."

        - Install escutcheons on piping wall and ceiling penetrations in exposed, finished locations. Comply with requirements for escutcheons specified in Section 220518 "Escutcheons for Plumbing Piping."

        - Fill self-contained fixtures with flushing fluid.

      - PIPING CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

Retain, revise, or delete first six paragraphs below to suit Project.

        - Connect cold-water-supply piping to plumbed emergency plumbing fixtures not having water-tempering equipment. Comply with requirements for cold-water piping specified in Section 221116 "Domestic Water Piping."

        - Connect hot- and cold-water-supply piping to hot- and cold-water, water-tempering equipment. Connect output from water-tempering equipment to emergency plumbing fixtures. Comply with requirements for hot- and cold-water piping specified in Section 221116 "Domestic Water Piping."

Retain first paragraph below if steam mixing valve is used.

        - Connect steam and cold-water-supply and condensate return piping to steam and cold water-tempering equipment. Connect output from water-tempering equipment to emergency plumbing fixtures. Comply with requirements for cold-water piping specified in Section 221116 "Domestic Water Piping" and comply with requirements for steam and condensate piping specified in Section 232213 "Steam and Condensate Heating Piping" and Section 232216 "Steam and Condensate Heating Piping Specialties."

        - Connect cold water and electrical power to electric heating water-tempering equipment. Comply with requirements for cold-water piping specified in Section 221116 "Domestic Water Piping."

        - Directly connect emergency plumbing fixture receptors with trapped drain outlet to sanitary waste and vent piping. Comply with requirements for waste piping specified in Section 221316 "Sanitary Waste and Vent Piping."

        - Indirectly connect emergency plumbing fixture receptors without trapped drain outlet to sanitary waste or storm drainage piping.

        - Where installing piping adjacent to emergency plumbing fixtures, allow space for service and maintenance of fixtures.

      - ELECTRICAL CONNECTIONS

        - Connect wiring in accordance with Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

        - Ground equipment in accordance with Section 260526 "Grounding and Bonding for Electrical Systems."

        - Install electrical devices furnished by manufacturer, but not factory mounted in accordance with NFPA 70.

        - Install nameplate for each electrical connection, indicating electrical equipment designation and circuit number feeding connection.

Retain one of two subparagraphs below. First subparagraph cross-references Section 260553 "Identification for Electrical Systems" and should be retained for consistent electrical identification. Second subparagraph is an abbreviated version of the product specified in Section 260553 "Identification for Electrical Systems."

          - Nameplate to be laminated acrylic or melamine plastic signs, as specified in Section 260553 "Identification for Electrical Systems."

          - Nameplate to be laminated acrylic or melamine plastic signs with a black background and engraved white letters at least [1/2 inch (13 mm)] <Insert dimension> high.

      - IDENTIFICATION

        - Install equipment nameplates or equipment markers on emergency plumbing fixtures and equipment and equipment signs on water-tempering equipment. Comply with requirements for identification materials specified in Section 220553 "Identification for Plumbing Piping and Equipment."

      - FIELD QUALITY CONTROL

        - Mechanical-Component Testing: After plumbing connections have been made, test for compliance with requirements. Verify ability to achieve indicated capacities.

Retain "Test and Inspections" Paragraph below to describe tests and inspections to be performed.

        - Tests and Inspections:

          - Perform each visual and mechanical inspection.

          - Leak Test: After installation, charge system and test for leaks. Repair leaks and retest until no leaks exist.

          - Operational Test: After electrical circuitry has been energized, start units to confirm proper unit operation.

          - Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

          - Emergency plumbing fixtures[ and water-tempering equipment] will be considered defective if they do not pass tests and inspections.

        - Prepare test and inspection reports.

      - ADJUSTING

        - Operate and adjust emergency plumbing fixtures and controls. Replace damaged and malfunctioning fixtures and controls.

        - Adjust or replace fixture flow regulators for proper flow.

        - Adjust equipment temperature settings.

      - CLEANING AND PROTECTION

        - Clean emergency plumbing fixtures with manufacturers' recommended cleaning methods and materials.

        - Install protective covering for installed emergency plumbing fixtures and fittings.

        - Do not allow use of emergency plumbing fixtures for temporary facilities unless approved in writing by Owner.

END OF SECTION 224500