Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 224713 - DRINKING FOUNTAINS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Drinking fountains.

          - Bottle filling stations.

          - Supports.

      - ACTION SUBMITTALS

        - Product Data: For each type of drinking fountain and bottle filling station.

          - Include construction details, material descriptions, dimensions of individual components and profiles, and finishes.

          - Include operating characteristics, and furnished specialties and accessories.

        - Sustainable Design Submittals:

          - <Double click to insert sustainable design text for plumbing fixtures.>

          - <Double click to insert sustainable design text for recycled content.>

        - Shop Drawings:

          - Include diagrams for power wiring.

      - CLOSEOUT SUBMITTALS

        - Maintenance Data: For [drinking fountains] [and] [bottle filling stations] to include in maintenance manuals.

      - MAINTENANCE MATERIAL SUBMITTALS

        - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Filter Cartridges: Equal to <Insert number> percent of quantity installed for each type and size indicated, but no fewer than <Insert number> of each.

- PRODUCTS

Manufacturers and products listed in SpecAgent and MasterWorks Paragraph Builder are neither recommended nor endorsed by the AIA or Deltek. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - PERFORMANCE REQUIREMENTS

        - Standards:

The U.S. Safe Drinking Water Act (SDWA) has required national compliance with less than or equal to 0.25 percent weighted average lead content at wetted surfaces for pipe, fittings, and devices intended to convey or dispense water for human consumption since January 2014. The IPC and UPC have the same requirements. Items in compliance with NSF 61 and NSF 372 also comply with this requirement. Some manufacturers choose to meet this requirement through independent testing and have "Certified Lead Free" products, which may or may not have NSF 61 or NSF 372 certifications.

          - Drinking fountains and bottle filling stations intended to convey or dispense water for human consumption are to comply with the U.S. Safe Drinking Water Act (SDWA), requirements of the Authority Having Jurisdiction (AHJ), and with NSF 61 or NSF 372, or be certified in compliance with NSF 61 or NSF 372 by an ANSI-accredited third-party certification body, that the weighted average lead content at wetted surfaces is less than or equal to 0.25 percent.

Retain first subparagraph below if stainless steel drinking fountains or bottle filling stations are retained.

          - [Comply with ASME A112.19.3/CSA B45.4 for stainless steel drinking fountains and bottle filling stations.]

Retain first subparagraph below if vitreous china drinking fountains are retained.

          - [Comply with ASME A112.19.2/CSA B45.1 for vitreous china drinking fountains.]

          - Comply with NSF 42 and NSF 53 for water filters for drinking fountains and bottle filling stations.

          - Comply with ICC A117.1 for accessible drinking fountains and bottle filling stations.

      - DRINKING FOUNTAINS

Copy "Drinking Fountains - Surface Wall-Mounted, Bronze" Paragraph below and re-edit for each type of drinking fountain required. Surface wall-mounted drinking fountains may be used for interior/exterior applications. Projects requiring exterior fountains may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Surface Wall-Mounted, Bronze: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain surface wall-mounted, bronze drinking fountains from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Receptor(s):

            - Type: [Slab] [With back] [On horizontal support].

            - Shape: [Rectangular] [Round] <Insert shape>.

Retain "Back Panel" Subparagraph below only for slab-type and on-horizontal-support-type drinking fountains and only if required. Include size if necessary.

            - Back Panel: [Stainless steel] <Insert material> wall plate behind drinking fountain.

            - Bubblers: One for each receptor, with adjustable stream regulator, located on deck.

            - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Maximum Water Flow: [0.15 gpm (0.0095 L/s)] [0.5 gpm (0.0316 L/s)] <Insert value>.

          - Control: [Push button] [Push bar] [Sensor] <Insert control>.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) chrome-plated brass P-trap and waste.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

Retain "Electrical Characteristics" Subparagraph below only if retaining "Sensor" option in "Control" Subparagraph. Manual units do not have electrical requirements. Coordinate with electrical engineer to have receptacle placed below unit.

          - Electrical Characteristics:

            - Volts: 120 V ac.

            - Phase: Single.

            - Hertz: 60 Hz.

Coordinate "Support" Subparagraph below with "Supports" Article.

          - Support: Provide manufacturer's mounting plate [and] [drinking fountain carrier] <Insert carrier>.

Retain "High/low - standard/accessible in accordance with ICC A117.1" option in "Drinking Fountain Mounting Height" Subparagraph below for multiple receptor drinking fountains when one receptor will be installed at standard height and one receptor will be installed at accessible height.

          - Drinking Fountain Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1] [High/low - standard/accessible in accordance with ICC A117.1].

Retain "Freeze-Resistant Supply Fitting" Subparagraph below for freeze-resistant drinking fountains. Locate supply fitting shutoff in heated portion of structure where temperature does not drop below 50 deg F (10 deg C).

          - Freeze-Resistant Supply Fittings: Through wall freeze-resistant shutoff and flow-control valve assembly.

Copy "Drinking Fountains - Surface Wall-Mounted, Composite/Granite" Paragraph below and re-edit for each type of drinking fountain required. Surface wall-mounted drinking fountains may be used for interior/exterior applications. Projects requiring exterior fountains may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Surface Wall-Mounted, Composite/Granite: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain surface wall-mounted, composite/granite drinking fountains from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Receptor(s):

            - Type: [Slab] [With back] [On horizontal support].

            - Shape: [Rectangular] [Round] <Insert shape>.

Retain "Back Panel" Subparagraph below only for slab-type and on-horizontal-support-type drinking fountains and only if required. Include size if necessary.

            - Back Panel: [Stainless steel] <Insert material> wall plate behind drinking fountain.

            - Bubblers: One for each receptor, with adjustable stream regulator, located on deck.

            - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Maximum Water Flow: [0.15 gpm (0.0095 L/s)] [0.5 gpm (0.0316 L/s)] <Insert value>.

          - Control: [Push button] [Push bar] [Sensor] <Insert control>.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) chrome-plated brass P-trap and waste.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

Retain "Electrical Characteristics" Subparagraph below only if retaining "Sensor" option in "Control" Subparagraph. Manual units do not have electrical requirements. Coordinate with electrical engineer to have receptacle placed below unit.

          - Electrical Characteristics:

            - Volts: 120 V ac.

            - Phase: Single.

            - Hertz: 60 Hz.

Coordinate "Support" Subparagraph below with "Supports" Article.

          - Support: Provide manufacturer's mounting plate [and] [drinking fountain carrier] <Insert carrier>.

Retain "High/low - standard/accessible in accordance with ICC A117.1" option in "Drinking Fountain Mounting Height" Subparagraph below for multiple receptor drinking fountains when one receptor will be installed at standard height and one receptor will be installed at accessible height.

          - Drinking Fountain Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1] [High/low - standard/accessible in accordance with ICC A117.1].

Retain "Freeze-Resistant Supply Fitting" Subparagraph below for freeze-resistant drinking fountains. Located supply fitting shutoff in heated portion of structure where temperature does not drop below 50 deg F (10 deg C).

          - Freeze-Resistant Supply Fittings: Through wall freeze-resistant shutoff and flow-control valve assembly.

Copy "Drinking Fountains - Surface Wall-Mounted, Concrete" Paragraph below and re-edit for each type of drinking fountain required. Surface wall-mounted drinking fountains may be used for interior/exterior applications. Projects requiring exterior fountains may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains -Surface Wall-Mounted, Concrete: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain surface wall-mounted, concrete drinking fountains from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Receptor(s):

            - Type: [Slab] [With back] [On horizontal support].

            - Shape: [Rectangular] [Round] <Insert shape>.

Retain "Back Panel" Subparagraph below only for slab-type and on-horizontal-support-type drinking fountains and only if required. Include size if necessary.

            - Back Panel: [Stainless steel] <Insert material> wall plate behind drinking fountain.

            - Bubblers: One for each receptor, with adjustable stream regulator, located on deck.

            - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Maximum Water Flow: [0.15 gpm (0.0095 L/s)] [0.5 gpm (0.0316 L/s)] <Insert value>.

          - Control: [Push button] [Push bar] [Sensor] <Insert control>.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) chrome-plated brass P-trap and waste.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

Retain "Electrical Characteristics" Subparagraph below only if retaining "Sensor" option in "Control" Subparagraph. Manual units do not have electrical requirements. Coordinate with electrical engineer to have receptacle placed below unit.

          - Electrical Characteristics:

            - Volts: 120 V ac.

            - Phase: Single.

            - Hertz: 60 Hz.

Coordinate "Support" Subparagraph below with "Supports" Article.

          - Support: Provide manufacturer's mounting plate [and] [drinking fountain carrier] <Insert carrier>.

Retain "High/low - standard/accessible in accordance with ICC A117.1" option in "Drinking Fountain Mounting Height" Subparagraph below for multiple receptor drinking fountains when one receptor will be installed at standard height and one receptor will be installed at accessible height.

          - Drinking Fountain Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1] [High/low - standard/accessible in accordance with ICC A117.1].

Retain "Freeze-Resistant Supply Fitting" Subparagraph below for freeze-resistant drinking fountains. Locate supply fitting shutoff in heated portion of structure where temperature does not drop below 50 deg F (10 deg C).

          - Freeze-Resistant Supply Fittings: Through wall freeze-resistant shutoff and flow-control valve assembly.

Copy "Drinking Fountains - Surface Wall-Mounted, Powder-Coated Metal" Paragraph below and re-edit for each type of drinking fountain required. Surface wall-mounted drinking fountains may be used for interior/exterior applications. Projects requiring exterior fountains may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Surface Wall-Mounted, Powder-Coated Metal: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain surface wall-mounted, powder-coated-metal drinking fountains -from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Receptor(s):

            - Type: [Slab] [With back] [On horizontal support].

            - Shape: [Rectangular] [Round] <Insert shape>.

Retain "Back Panel" Subparagraph below only for slab-type and on-horizontal-support-type drinking fountains and only if required. Include size if necessary.

            - Back Panel: [Stainless steel] <Insert material> wall plate behind drinking fountain.

            - Bubblers: One for each receptor, with adjustable stream regulator, located on deck.

            - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Maximum Water Flow: [0.15 gpm (0.0095 L/s)] [0.5 gpm (0.0316 L/s)] <Insert value>.

          - Control: [Push button] [Push bar] [Sensor] <Insert control>.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) chrome-plated brass P-trap and waste.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

Retain "Electrical Characteristics" Subparagraph below only if retaining "Sensor" option in "Control" Subparagraph. Manual units do not have electrical requirements. Coordinate with electrical engineer to have receptacle placed below unit.

          - Electrical Characteristics:

            - Volts: 120 V ac.

            - Phase: Single.

            - Hertz: 60 Hz.

Coordinate "Support" Subparagraph below with "Supports" Article.

          - Support: Provide manufacturer's mounting plate [and] [drinking fountain carrier] <Insert carrier>.

Retain "High/low - standard/accessible in accordance with ICC A117.1" option in "Drinking Fountain Mounting Height" Subparagraph below for multiple receptor drinking fountains when one receptor will be installed at standard height and one receptor will be installed at accessible height.

          - Drinking Fountain Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1] [High/low - standard/accessible in accordance with ICC A117.1].

Retain "Freeze-Resistant Supply Fitting" Subparagraph below for freeze-resistant drinking fountains. Locate supply fitting shutoff in heated portion of structure where temperature does not drop below 50 deg F (10 deg C).

          - Freeze-Resistant Supply Fittings: Through wall freeze-resistant shutoff and flow-control valve assembly.

Copy "Drinking Fountains - Surface Wall-Mounted, Stainless Steel" Paragraph below and re-edit for each type of drinking fountain required. Surface wall-mounted drinking fountains may be used for interior/exterior applications. Projects requiring exterior fountains may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Surface Wall-Mounted, Stainless Steel: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain surface wall-mounted, stainless steel drinking fountains from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Receptor(s):

            - Type: [Slab] [With back] [On horizontal support].

            - Shape: [Rectangular] [Round] <Insert shape>.

Retain "Back Panel" Subparagraph below only for slab-type and on-horizontal-support-type drinking fountains and only if required. Include size if necessary.

            - Back Panel: [Stainless steel] <Insert material> wall plate behind drinking fountain.

            - Bubblers: One for each receptor, with adjustable stream regulator, located on deck.

            - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Maximum Water Flow: [0.15 gpm (0.0095 L/s)] [0.5 gpm (0.0316 L/s)] <Insert value>.

          - Control: [Push button] [Push bar] [Sensor] <Insert control>.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) chrome-plated brass P-trap and waste.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

Retain "Electrical Characteristics" Subparagraph below only if retaining "Sensor" option in "Control" Subparagraph. Manual units do not have electrical requirements. Coordinate with electrical engineer to have receptacle placed below unit.

          - Electrical Characteristics:

            - Volts: 120 V ac.

            - Phase: Single.

            - Hertz: 60 Hz.

Coordinate "Support" Subparagraph below with "Supports" Article.

          - Support: Provide manufacturer's mounting plate [and] [drinking fountain carrier] <Insert carrier>.

Retain "High/low - standard/accessible in accordance with ICC A117.1" option in "Drinking Fountain Mounting Height" Subparagraph below for multiple receptor drinking fountains when one receptor will be installed at standard height and one receptor will be installed at accessible height.

          - Drinking Fountain Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1] [High/low - standard/accessible in accordance with ICC A117.1].

Retain "Freeze-Resistant Supply Fitting" Subparagraph below for freeze-resistant drinking fountains. Locate supply fitting shutoff in heated portion of structure where temperature does not drop below 50 deg F (10 deg C).

          - Freeze-Resistant Supply Fittings: Through wall freeze-resistant shutoff and flow-control valve assembly.

Copy "Drinking Fountains - Surface Wall-Mounted, Stone Aggregate/Terrazzo" Paragraph below and re-edit for each type of drinking fountain required. Surface wall-mounted drinking fountains may be used for interior/exterior applications. Projects requiring exterior fountains may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Surface Wall-Mounted, Stone Aggregate/Terrazzo: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain surface wall-mounted, stone aggregate/terrazzo drinking fountains from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Receptor(s):

            - Type: [Slab] [With back] [On horizontal support].

            - Shape: [Rectangular] [Round] <Insert shape>.

Retain "Back Panel" Subparagraph below only for slab-type and on-horizontal-support-type drinking fountains and only if required. Include size if necessary.

            - Back Panel: [Stainless steel] <Insert material> wall plate behind drinking fountain.

            - Bubblers: One for each receptor, with adjustable stream regulator, located on deck.

            - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Maximum Water Flow: [0.15 gpm (0.0095 L/s)] [0.5 gpm (0.0316 L/s)] <Insert value>.

          - Control: [Push button] [Push bar] [Sensor] <Insert control>.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) chrome-plated brass P-trap and waste.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

Retain "Electrical Characteristics" Subparagraph below only if retaining "Sensor" option in "Control" Subparagraph. Manual units do not have electrical requirements. Coordinate with electrical engineer to have receptacle placed below unit.

          - Electrical Characteristics:

            - Volts: 120 V ac.

            - Phase: Single.

            - Hertz: 60 Hz.

Coordinate "Support" Subparagraph below with "Supports" Article.

          - Support: Provide manufacturer's mounting plate [and] [drinking fountain carrier] <Insert carrier>.

Retain "High/low - standard/accessible in accordance with ICC A117.1" option in "Drinking Fountain Mounting Height" Subparagraph below for multiple receptor drinking fountains when one receptor will be installed at standard height and one receptor will be installed at accessible height.

          - Drinking Fountain Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1] [High/low - standard/accessible in accordance with ICC A117.1].

Retain "Freeze-Resistant Supply Fitting" Subparagraph below for freeze-resistant drinking fountains. Locate supply fitting shutoff in heated portion of structure where temperature does not drop below 50 deg F (10 deg C).

          - Freeze-Resistant Supply Fittings: Through wall freeze-resistant shutoff and flow-control valve assembly.

Copy "Drinking Fountains - Surface Wall-Mounted, Vitreous China" Paragraph below and re-edit for each type of drinking fountain required. Surface wall-mounted drinking fountains may be used for interior/exterior applications. Projects requiring exterior fountains may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Surface Wall-Mounted, Vitreous China: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain surface wall-mounted, vitreous-china drinking fountains from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Receptor(s):

            - Type: [Slab] [With back] [On horizontal support].

            - Shape: [Rectangular] [Round] <Insert shape>.

Retain "Back Panel" Subparagraph below only for slab-type and on-horizontal-support-type drinking fountains and only if required. Include size if necessary.

            - Back Panel: [Stainless steel] <Insert material> wall plate behind drinking fountain.

            - Bubblers: One for each receptor, with adjustable stream regulator, located on deck.

            - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Maximum Water Flow: [0.15 gpm (0.0095 L/s)] [0.5 gpm (0.0316 L/s)] <Insert value>.

          - Control: [Push button] [Push bar] [Sensor] <Insert control>.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) chrome-plated brass P-trap and waste.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

Retain "Electrical Characteristics" Subparagraph below only if retaining "Sensor" option in "Control" Subparagraph. Manual units do not have electrical requirements. Coordinate with electrical engineer to have receptacle placed below unit.

          - Electrical Characteristics:

            - Volts: 120 V ac.

            - Phase: Single.

            - Hertz: 60 Hz.

Coordinate "Support" Subparagraph below with "Supports" Article.

          - Support: Provide manufacturer's mounting plate [and] [drinking fountain carrier] <Insert carrier>.

Retain "High/low - standard/accessible in accordance with ICC A117.1" option in "Drinking Fountain Mounting Height" Subparagraph below for multiple receptor drinking fountains when one receptor will be installed at standard height and one receptor will be installed at accessible height.

          - Drinking Fountain Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1] [High/low - standard/accessible in accordance with ICC A117.1].

Retain "Freeze-Resistant Supply Fitting" Subparagraph below for freeze-resistant drinking fountains. Locate supply fitting shutoff in heated portion of structure where temperature does not drop below 50 deg F (10 deg C).

          - Freeze-Resistant Supply Fittings: Through wall freeze-resistant shutoff and flow-control valve assembly.

Copy "Drinking Fountains - Semi-Recessed, Wall-Mounted, Stainless Steel" Paragraph below and re-edit for each type of drinking fountain required. Semi-recessed, wall-mounted drinking fountains may be used for interior/exterior applications. Projects requiring exterior fountains may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Semi-Recessed, Wall-Mounted, Stainless Steel: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain semi-recessed, wall-mounted, stainless steel drinking fountains from single source from single manufacturer.

          - Receptor Shape: Concave with projecting bowl.

          - Bubbler: One, with adjustable stream regulator, located on deck.

          - Maximum Water Flow: [0.15 gpm (0.0095 L/s)] [0.5 gpm (0.0316 L/s)] <Insert value>.

          - Control: [Push button] [Push bar] <Insert control>.

          - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

          - Support: Manufacturer-provided support frame for attaching to substrate.

          - Drinking Fountain Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1].

Copy "Drinking Fountains - Semi-Recessed, Wall-Mounted, Vitreous China" Paragraph below and re-edit for each type of drinking fountain required. Semi-recessed, wall-mounted drinking fountains may be used for interior/exterior applications. Projects requiring exterior fountains may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Semi-Recessed, Wall-Mounted, Vitreous China: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain semi-recessed, wall-mounted, vitreous-china drinking fountains from single source from single manufacturer.

          - Receptor Shape: Concave with projecting bowl.

          - Bubbler: One, with adjustable stream regulator, located on deck.

          - Maximum Water Flow: [0.15 gpm (0.0095 L/s)] [0.5 gpm (0.0316 L/s)] <Insert value>.

          - Control: [Push button] [Push bar] <Insert control>.

          - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

          - Support: Manufacturer-provided support frame for attaching to substrate.

          - Drinking Fountain Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1].

Copy "Drinking Fountains - Recessed, Wall-Mounted, Bronze" Paragraph below and re-edit for each type of drinking fountain required. Recessed, wall-mounted drinking fountains may be used for interior/exterior applications. Projects requiring exterior fountains may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Recessed, Wall-Mounted, Bronze: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain recessed, wall-mounted, bronze drinking fountains from single source from single manufacturer.

          - Receptor Shape: Concave with flush wall flange.

          - Bubbler: One, with adjustable stream regulator, located on deck.

          - Maximum Water Flow: [0.15 gpm (0.0095 L/s)] [0.5 gpm (0.0316 L/s)] <Insert value>.

          - Control: [Push button] [Push bar] <Insert control>.

          - Drain: Grid with NPS 1-1/4 (DN 32) minimum horizontal waste and trap, complying with ASME A112.18.2/CSA B125.2.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

          - Support: Provide manufacturer's support frame attached to substrate.

          - Drinking Fountain Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1].

Copy "Drinking Fountains - Recessed, Wall-Mounted, Stainless Steel" Paragraph below and re-edit for each type of drinking fountain required. Recessed, wall-mounted drinking fountains may be used for interior/exterior applications. Projects requiring exterior fountains may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Recessed, Wall-Mounted, Stainless Steel: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain recessed, wall-mounted, stainless steel drinking fountains from single source from single manufacturer.

          - Receptor Shape: Concave with flush wall flange.

          - Bubbler: One, with adjustable stream regulator, located on deck.

          - Maximum Water Flow: [0.15 gpm (0.0095 L/s)] [0.5 gpm (0.0316 L/s)] <Insert value>.

          - Control: [Push button] [Push bar] <Insert control>.

          - Drain: Grid with NPS 1-1/4 (DN 32) minimum horizontal waste and trap, complying with ASME A112.18.2/CSA B125.2.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

          - Support: Provide manufacturer's support frame attached to substrate.

          - Drinking Fountain Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1].

Copy "Drinking Fountains - Pedestal, Concrete" Paragraph below and re-edit for each type of drinking fountain required. Pedestal drinking fountains are used for exterior applications. Projects requiring pedestal fountains may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Pedestal, Concrete: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain pedestal, concrete drinking fountains rom single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Pedestal: [Rectangular] [Round] <Insert shape>.

          - Receptor(s):

            - Shape: [Rectangular] [Round] <Insert shape>.

            - Bubbler: One for each receptor, with adjustable stream regulator, located on deck.

            - Bottle Filler: Push-button activation.

            - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Maximum Water Flow: [0.15 gpm (0.0095 L/s)] [0.5 gpm (0.0316 L/s)] <Insert value>.

          - Controls: [Foot pedal] [Push bar] [Push button] <Insert control>.

          - Access to Internal Components: Panel in pedestal.

          - Supply: [NPS 3/8 (DN 10)] [NPS 1/2 (DN 15)] with shutoff valve.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters complying with NSF 42 and NSF 53 and with capacity sized for peak flow rate.

          - Drain Piping: [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)] minimum trap and waste.

Retain "High/low - standard/accessible in accordance with ICC A117.1" option in "Drinking Fountain Mounting Height" Subparagraph below for multiple receptor drinking fountains when one receptor will be installed at standard height and one receptor will be installed at accessible height.

          - Drinking Fountain Height: [Standard] [Child] [Accessible in accordance with ICC A117.1] [High/low - standard/accessible in accordance with ICC A117.1].

Retain "Freeze-Resistant Supply Fitting" and "Bury Depth, Grade to Valve Components" subparagraphs below for freeze-resistant drinking fountains.

          - Freeze-Resistant Supply Fittings: Underground freeze-resistant shutoff and flow-control valve assembly.

          - Bury Depth, Grade to Valve Components: [36 inches (915 mm)] [48 inches (1220 mm)] [60 inches (1525 mm)] <Insert dimension>.

Copy "Drinking Fountains - Pedestal, Powder-Coated Metal" Paragraph below and re-edit for each type of drinking fountain required. Pedestal drinking fountains are used for exterior applications. Projects requiring pedestal fountains may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Pedestal, Powder-Coated Metal: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain pedestal, powder-coated-metal drinking fountains from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Pedestal: [Rectangular] [Round] <Insert shape>.

          - Receptor(s):

            - Shape: [Rectangular] [Round] <Insert shape>.

            - Bubbler: One for each receptor, with adjustable stream regulator, located on deck.

            - Bottle Filler: Push-button activation.

            - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Maximum Water Flow: [0.15 gpm (0.0095 L/s)] [0.5 gpm (0.0316 L/s)] <Insert value>.

          - Controls: [Foot pedal] [Push bar] [Push button] <Insert control>.

          - Access to Internal Components: Panel in pedestal.

          - Supply: [NPS 3/8 (DN 10)] [NPS 1/2 (DN 15)] with shutoff valve.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters complying with NSF 42 and NSF 53 and with capacity sized for peak flow rate.

          - Drain Piping: [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)] minimum trap and waste.

Retain "High/low - standard/accessible in accordance with ICC A117.1" option in "Drinking Fountain Mounting Height" Subparagraph below for multiple receptor drinking fountains when one receptor will be installed at standard height and one receptor will be installed at accessible height.

          - Drinking Fountain Height: [Standard] [Child] [Accessible in accordance with ICC A117.1] [High/low - standard/accessible in accordance with ICC A117.1].

Retain "Freeze-Resistant Supply Fitting" and "Bury Depth, Grade to Valve Components" subparagraphs below for freeze-resistant drinking fountains.

          - Freeze-Resistant Supply Fittings: Underground freeze-resistant shutoff and flow-control valve assembly.

          - Bury Depth, Grade to Valve Components: [36 inches (915 mm)] [48 inches (1220 mm)] [60 inches (1525 mm)] <Insert dimension>.

Copy "Drinking Fountains - Pedestal, Stainless Steel" Paragraph below and re-edit for each type of drinking fountain required. Pedestal drinking fountains are used for exterior applications. Projects requiring pedestal fountains may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Drinking Fountains - Pedestal, Stainless Steel: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain pedestal, stainless steel drinking fountains from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Pedestal: [Rectangular] [Round] <Insert shape>.

          - Receptor(s):

            - Shape: [Rectangular] [Round] <Insert shape>.

            - Bubbler: One for each receptor, with adjustable stream regulator, located on deck.

            - Bottle Filler: Push-button activation.

            - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Maximum Water Flow: [0.15 gpm (0.0095 L/s)] [0.5 gpm (0.0316 L/s)] <Insert value>.

          - Controls: [Foot pedal] [Push bar] [Push button] <Insert control>.

          - Access to Internal Components: Panel in pedestal.

          - Supply: [NPS 3/8 (DN 10)] [NPS 1/2 (DN 15)] with shutoff valve.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters complying with NSF 42 and NSF 53 and with capacity sized for peak flow rate.

          - Drain Piping: [NPS 1-1/4 (DN 32)] [NPS 1-1/2 (DN 40)] minimum trap and waste.

Retain "High/low - standard/accessible in accordance with ICC A117.1" option in "Drinking Fountain Mounting Height" Subparagraph below for multiple receptor drinking fountains when one receptor will be installed at standard height and one receptor will be installed at accessible height.

          - Drinking Fountain Height: [Standard] [Child] [Accessible in accordance with ICC A117.1] [High/low - standard/accessible in accordance with ICC A117.1].

Retain "Freeze-Resistant Supply Fitting" and "Bury Depth, Grade to Valve Components" subparagraphs below for freeze-resistant drinking fountains.

          - Freeze-Resistant Supply Fittings: Underground freeze-resistant shutoff and flow-control valve assembly.

          - Bury Depth, Grade to Valve Components: [36 inches (915 mm)] [48 inches (1220 mm)] [60 inches (1525 mm)] <Insert dimension>.

      - BOTTLE FILLING STATIONS

Copy "Bottle Filling Station - Surface Wall-Mounted, ABS/Stainless Steel Combination" Paragraph below and re-edit for each type of bottle filling station required. Surface-mounted bottle filling stations may be used for interior/exterior applications. Projects requiring exterior filling stations may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each bottle filling station.

        - Bottle Filling Station - Surface Wall-Mounted, ABS/Stainless Steel Combination: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain surface wall-mounted, ABS/stainless steel combination, bottle filling stations from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Cabinet: ABS/stainless steel combination.

          - Bottle Filler: [Sensor] [Push-button] activation[, with] [20-second] <Insert value> [automatic shutoff timer]. Fill rate [0.5 to 1.5 gpm (0.03155 to 0.09464 L/s)] <Insert value>.

          - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters complying with NSF 42 and NSF 53 and with capacity sized for peak flow rate.

Coordinate "Support" Subparagraph below with "Supports" Article. There are no dedicated bottle filling station support carriers, so drinking fountain carriers are referenced below.

          - Support: Provide manufacturer's mounting plate [and] [drinking fountain carrier] <Insert carrier>.

          - Bottle Filling Station Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1].

Retain "Electrical Characteristics" Subparagraph below only if retaining "Sensor" option in "Bottle Filler" Subparagraph. Manual units do not have electrical requirements. Coordinate with electrical engineer to have receptacle placed below unit.

          - Electrical Characteristics:

            - Volts: 120 V ac.

            - Phase: Single.

            - Hertz: 60 Hz.

Copy "Bottle Filling Station - Surface Wall-Mounted, Powder-Coated Metal" Paragraph below and re-edit for each type of bottle filling station required. Surface wall-mounted bottle filling stations may be used for interior/exterior applications. Projects requiring exterior filling stations may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each bottle filling station.

        - Bottle Filling Station - Surface Wall-Mounted, Powder-Coated Metal: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain surface wall-mounted, powder-coated-metal, bottle filling stations from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Cabinet: Powder-coated metal.

          - Finish Color: <Insert color>.

          - Bottle Filler: [Sensor] [Push-button] activation[, with] [20-second] <Insert value> [automatic shutoff timer]. Fill rate [0.5 to 1.5 gpm (0.03155 to 0.09464 L/s)] <Insert value>.

          - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters complying with NSF 42 and NSF 53 and with capacity sized for peak flow rate.

Coordinate "Support" Subparagraph below with "Supports" Article.

          - Support: Provide manufacturer's mounting plate [and] [drinking fountain carrier] <Insert carrier>.

          - Bottle Filling Station Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1].

Retain "Electrical Characteristics" Subparagraph below only if retaining "Sensor" option in "Bottle Filler" Subparagraph. Manual units do not have electrical requirements. Coordinate with electrical engineer to have receptacle placed below unit.

          - Electrical Characteristics:

            - Volts: 120 V ac.

            - Phase: Single.

            - Hertz: 60 Hz.

Copy "Bottle Filling Station - Surface Wall-Mounted, Stainless Steel" Paragraph below and re-edit for each type of bottle filling station required. Surface wall-mounted bottle filling stations may be used for interior/exterior applications. Projects requiring exterior filling stations may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each bottle filling station.

        - Bottle Filling Station - Surface Wall-Mounted, Stainless Steel: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain surface wall-mounted, stainless steel, bottle filling stations from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Cabinet: Stainless steel.

          - Bottle Filler: [Sensor] [Push-button] activation[, with] [20-second] <Insert value> [automatic shutoff timer]. Fill rate [0.5 to 1.5 gpm (0.03155 to 0.09464 L/s)] <Insert value>.

          - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters complying with NSF 42 and NSF 53 and with capacity sized for peak flow rate.

Coordinate "Support" Subparagraph below with "Supports" Article.

          - Support: Provide manufacturer's mounting plate [and] [drinking fountain carrier] <Insert carrier>.

          - Bottle Filling Station Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1].

Retain "Electrical Characteristics" Subparagraph below only if retaining "Sensor" option in "Bottle Filler" Subparagraph. Manual units do not have electrical requirements. Coordinate with electrical engineer to have receptacle placed below unit.

          - Electrical Characteristics:

            - Volts: 120 V ac.

            - Phase: Single.

            - Hertz: 60 Hz.

Copy "Bottle Filling Station - Recessed, Wall-Mounted, ABS/Stainless Steel Combination" Paragraph below and re-edit for each type of bottle filling station required. Recessed, wall-mounted bottle filling stations may be used for interior/exterior applications. Projects requiring exterior filling stations may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each bottle filling station.

        - Bottle Filling Station - Recessed, Wall-Mounted, ABS/Stainless Steel Combination: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain recessed, wall-mounted, ABS/stainless steel combination, bottle filling stations from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Cabinet: ABS/stainless steel combination.

          - Bottle Filler: [Sensor] [Push-button] activation[, with] [20-second] <Insert value> [automatic shutoff timer]. Fill rate [0.5 to 1.5 gpm (0.03155 to 0.09464 L/s)] <Insert value>.

          - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters complying with NSF 42 and NSF 53 and with capacity sized for peak flow rate.

          - Support: Provide manufacturer's frame attached to substrate.

          - Bottle Filling Station Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1].

Retain "Electrical Characteristics" Subparagraph below only if retaining "Sensor" option in "Bottle Filler" Subparagraph. Manual units do not have electrical requirements. Coordinate with electrical engineer to have receptacle placed below unit.

          - Electrical Characteristics:

            - Volts: 120 V ac.

            - Phase: Single.

            - Hertz: 60 Hz.

Copy "Bottle Filling Station - Recessed, Wall-Mounted, Powder-Coated Metal" Paragraph below and re-edit for each type of bottle filling station required. Wall-mounted, recessed, bottle filling stations may be used for interior/exterior applications. Projects requiring exterior filling stations may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each bottle filling station.

        - Bottle Filling Station - Recessed, Wall-Mounted, Powder-Coated Metal: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain recessed, wall-mounted, powder-coated-metal, bottle filling stations from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Cabinet: Powder-coated metal.

          - Finish Color: <Insert color>.

          - Bottle Filler: [Sensor] [Push-button] activation[, with] [20-second] <Insert value> [automatic shutoff timer]. Fill rate [0.5 to 1.5 gpm (0.03155 to 0.09464 L/s)] <Insert value>.

          - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters complying with NSF 42 and NSF 53 and with capacity sized for peak flow rate.

          - Support: Provide manufacturer's frame attached to substrate.

          - Bottle Filling Station Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1].

Retain "Electrical Characteristics" Subparagraph below only if retaining "Sensor" option in "Bottle Filler" Subparagraph. Manual units do not have electrical requirements. Coordinate with electrical engineer to have receptacle placed below unit.

          - Electrical Characteristics:

            - Volts: 120 V ac.

            - Phase: Single.

            - Hertz: 60 Hz.

Copy "Bottle Filling Station - Recessed, Wall-Mounted, Stainless Steel" Paragraph below and re-edit for each type of bottle filling station required. Wall-mounted, recessed, bottle filling stations may be used for interior/exterior applications. Projects requiring exterior filling stations may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each bottle filling station.

        - Bottle Filling Station - Recessed, Wall-Mounted, Stainless Steel: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain recessed, wall-mounted, stainless steel, bottle filling stations from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Cabinet: Stainless steel.

          - Bottle Filler: [Sensor] [Push-button] activation[, with] [20-second] <Insert value> [automatic shutoff timer]. Fill rate [0.5 to 1.5 gpm (0.03155 to 0.09464 L/s)] <Insert value>.

          - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters complying with NSF 42 and NSF 53 and with capacity sized for peak flow rate.

          - Support: Provide manufacturer's frame attached to substrate.

          - Bottle Filling Station Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1].

Retain "Electrical Characteristics" Subparagraph below only if retaining "Sensor" option in "Bottle Filler" Subparagraph. Manual units do not have electrical requirements. Coordinate with electrical engineer to have receptacle placed below unit.

          - Electrical Characteristics:

            - Volts: 120 V ac.

            - Phase: Single.

            - Hertz: 60 Hz.

Copy "Bottle Filling Station - Pedestal, Powder-Coated Metal" Paragraph below and re-edit for each type of bottle filling station required. Pedestal bottle filling stations are used for exterior applications. Projects requiring pedestal filling stations may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Bottle Filling Station - Pedestal, Powder-Coated Metal: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain pedestal, powder-coated-metal, bottle filling stations from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Pedestal: [Rectangular] [Round] <Insert shape>.

          - Finish Color: <Insert color>

          - Bottle Filler: [Sensor] [Push-button] activation[, with] [20-second] <Insert value> [automatic shutoff timer]. Fill rate [0.5 to 1.5 gpm (0.03155 to 0.09464 L/s)] <Insert value>.

          - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Access to Internal Components: Panel in pedestal.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters complying with NSF 42 and NSF 53 and with capacity sized for peak flow rate.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

          - Bottle Filling Station Height: [Standard] [Child] [Accessible in accordance with ICC A117.1].

Retain "Freeze-Resistant Supply Fitting" and "Bury Depth, Grade to Valve Components" subparagraphs below for freeze-resistant bottle filling stations.

          - Freeze-Resistant Supply Fittings: Underground freeze-resistant shutoff and flow-control valve assembly.

          - Bury Depth, Grade to Valve Components: [36 inches (915 mm)] [48 inches (1220 mm)] [60 inches (1525 mm)] <Insert dimension>.

Retain "Electrical Characteristics" Subparagraph below only if retaining "Sensor" option in "Bottle Filler" Subparagraph. Manual units do not have electrical requirements. Coordinate with electrical engineer to have receptacle placed below unit.

          - Electrical Characteristics:

            - Volts: 120 V ac.

            - Phase: Single.

            - Hertz: 60 Hz.

Copy "Bottle Filling Station - Pedestal, Stainless Steel" Paragraph below and re-edit for each type of bottle filling station required. Pedestal bottle filling stations are used for exterior applications. Projects requiring pedestal filling stations may require the product to be freeze resistant.

Insert drawing designation. Use these designations on Drawings to identify each drinking fountain.

        - Bottle Filling Station - Pedestal, Stainless Steel: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain pedestal, stainless steel, bottle filling stations from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Pedestal: [Rectangular] [Round] <Insert shape>.

          - Bottle Filler: [Sensor] [Push-button] activation[, with] [20-second] <Insert value> [automatic shutoff timer]. Fill rate [0.5 to 1.5 gpm (0.03155 to 0.09464 L/s)] <Insert value>.

          - Drain: Grid type with NPS 1-1/4 (DN 32) tailpiece.

          - Access to Internal Components: Panel in pedestal.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters complying with NSF 42 and NSF 53 and with capacity sized for peak flow rate.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

          - Bottle Filling Station Height: [Standard] [Child] [Accessible in accordance with ICC A117.1].

Retain "Freeze-Resistant Supply Fitting" and "Bury Depth, Grade to Valve Components" subparagraphs below for freeze-resistant bottle filling stations.

          - Freeze-Resistant Supply Fittings: Underground freeze-resistant shutoff and flow-control valve assembly.

          - Bury Depth, Grade to Valve Components: [36 inches (915 mm)] [48 inches (1220 mm)] [60 inches (1525 mm)] <Insert dimension>.

Retain "Electrical Characteristics" Subparagraph below only if retaining "Sensor" option in "Bottle Filler" Subparagraph. Manual units do not have electrical requirements. Coordinate with electrical engineer to have receptacle placed below unit.

          - Electrical Characteristics:

            - Volts: 120 V ac.

            - Phase: Single.

            - Hertz: 60 Hz.

      - SUPPORTS

        - Drinking Fountain Carrier:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: ASME A112.6.1M.

- EXECUTION

      - EXAMINATION

        - Examine roughing-in for water-supply and sanitary drainage and vent piping systems to verify actual locations of piping connections before fixture installation.

        - Examine walls and floors for suitable conditions where fixtures will be installed.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - Install fixtures level and plumb according to roughing-in drawings. For fixtures indicated for children, install at height required by authorities having jurisdiction.

        - Set pedestal drinking fountains and bottle filling stations on flat surface in accordance with manufacturer's written installation instructions.

        - Install recessed, drinking fountains and bottle filling stations secured to wood blocking in wall construction.

        - Install off-the-floor carrier supports, affixed to building substrate, for wall-mounted fixtures.

        - Install water-supply piping with shutoff valve on supply to each fixture to be connected to domestic-water distribution piping. Use ball[ or gate] valve. Install valves in locations where they can be easily reached for operation. Valves are specified in Section 220523.12 "Ball Valves for Plumbing Piping"[ and Section 220523.15 "Gate Valves for Plumbing Piping."]

        - Install trap and waste piping on drain outlet of each fixture to be connected to sanitary drainage system.

        - Install wall flanges or escutcheons at piping wall penetrations in exposed, finished locations. Use deep-pattern escutcheons where required to conceal protruding fittings. Comply with escutcheon requirements specified in Section 220518 "Escutcheons for Plumbing Piping."

        - Seal joints between fixtures and walls using sanitary-type, one-part, mildew-resistant, silicone sealant. Match sealant color to fixture color. Comply with sealant requirements specified in Section 079200 "Joint Sealants."

      - PIPING CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Connect fixtures with water supplies, stops, and risers, and with traps, soil, waste, and vent piping. Use size fittings required to match fixtures.

        - Comply with water piping requirements specified in Section 221116 "Domestic Water Piping."

        - Install ball[ or gate] shutoff valve on water supply to each fixture.[ Install valve upstream from filter for drinking fountain.] Comply with valve requirements specified in Section 220523.12 "Ball Valves for Plumbing Piping"[ and Section 220523.15 "Gate Valves for Plumbing Piping."]

        - Comply with soil and waste piping requirements specified in Section 221316 "Sanitary Waste and Vent Piping."

      - ELECTRICAL CONNECTIONS

Retain this article if sensor/hands-free drinking fountains or bottle filling stations are required. Article is not required if sensor/hands-free feature is battery powered.

        - Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

        - Install electrical devices furnished by manufacturer, but not factory mounted, according to NFPA 70 and NECA 1.

        - Install nameplate for each electrical connection, indicating electrical equipment designation and circuit number feeding connection.

Retain one of two subparagraphs below. First subparagraph cross-references Section 260553 "Identification for Electrical Systems" and should be retained for consistent electrical identification. Second subparagraph is an abbreviated version of the product specified in Section 260553 "Identification for Electrical Systems."

          - Nameplates to be laminated acrylic or melamine plastic signs, as specified in Section 260553 "Identification for Electrical Systems."

          - Nameplates to be laminated acrylic or melamine plastic signs with a black background and engraved white letters at least 1/2 inch (13 mm) high.

      - ADJUSTING

        - Adjust fixture flow regulators for proper flow and stream height.

      - CLEANING

        - After installing fixtures, inspect unit. Remove paint splatters and other spots, dirt, and debris. Repair damaged finish to match original finish.

        - Clean fixtures, on completion of installation, according to manufacturer's written instructions.

        - Provide protective covering for installed fixtures.

        - Do not allow use of fixtures for temporary facilities unless approved in writing by Owner.

END OF SECTION 224713