Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 224716 - PRESSURE WATER COOLERS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Pressure water coolers.

          - Bottle filling stations.

          - Supports.

      - ACTION SUBMITTALS

        - Product Data: For each type of pressure water cooler and bottle filling station.

          - Include construction details, material descriptions, dimensions of individual components and profiles, and finishes.

          - Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

        - Sustainable Design Submittals:

          - <Double click to insert sustainable design text for plumbing fixtures.>

        - Shop Drawings:

          - Include diagrams for power wiring.

      - CLOSEOUT SUBMITTALS

        - Maintenance Data: For [pressure water coolers] [and] [bottle filling stations] to include in maintenance manuals.

      - MAINTENANCE MATERIAL SUBMITTALS

        - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Filter Cartridges: Equal to <Insert number> percent of quantity installed for each type and size indicated, but no fewer than <Insert number> of each.

- PRODUCTS

Manufacturers and products listed in SpecAgent and MasterWorks Paragraph Builder are neither recommended nor endorsed by the AIA or Deltek. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - PERFORMANCE REQUIREMENTS

        - Standards:

The U.S. Safe Drinking Water Act (SDWA) has required national compliance with less than or equal to 0.25 percent weighted average lead content at wetted surfaces for pipe, fittings, and devices intended to convey or dispense water for human consumption since January 2014. The IPC and UPC have the same requirements. Items in compliance with NSF 61 and NSF 372 also comply with this requirement. Some manufacturers choose to meet this requirement through independent testing and have "Certified Lead Free" products, which may or may not have NSF 61 or NSF 372 certifications.

          - Pressure water coolers and bottle filling stations intended to convey or dispense water for human consumption are to comply with the U.S. Safe Drinking Water Act (SDWA), requirements of the Authority Having Jurisdiction (AHJ), and with NSF 61 or NSF 372, or be certified in compliance with NSF 61 or NSF 372 by an ANSI-accredited third-party certification body, that the weighted average lead content at wetted surfaces is less than or equal to 0.25 percent.

          - Comply with ASHRAE 34 for water coolers. Provide HFC 134a (tetrafluoroethane) refrigerant unless otherwise indicated.

          - Comply with UL 399.

          - Comply with ASME A112.19.3/CSA B45.4.

          - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

          - Comply with NSF 42 and NSF 53 for water filters for water coolers and bottle filling stations.

          - Comply with ICC A117.1 for accessible water coolers and bottle filling stations.

      - PRESSURE WATER COOLERS

Copy "Pressure Water Coolers Freestanding, Floor-Mounted, Single-Station, Stainless Steel" Paragraph below and re-edit for each type of pressure water cooler required.

Insert drawing designation. Use these designations on Drawings to identify each pressure water cooler.

        - Pressure Water Coolers - Freestanding, Floor-Mounted, Single-Station, Stainless Steel: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain pressure water coolers - freestanding, floor-mounted, single-station stainless steel, from single source from single manufacturer.

          - Bubbler: One, with adjustable stream regulator, located on deck.

          - Control: [Push button] [Foot pedal] <Insert control>.

          - Drain: Grid with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

          - Cooling System: Electric, with[ precooler,] hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

Retain "Glass Filler" Subparagraph below only if required.

          - Glass filler.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

          - Capacities and Characteristics:

            - Cooled Water: [5 gph (0.0053 L/s)] [8 gph (0.0084 L/s)] [10 gph (0.0105 L/s)] [14 gph (0.0147 L/s)] <Insert value>.

            - Ambient-Air Temperature: 90 deg F (32 deg C).

            - Inlet-Water Temperature: 80 deg F (27 deg C).

            - Cooled-Water Temperature: 50 deg F (10 deg C).

            - Cooled-Water Storage: <Insert gal. (L)>.

            - Electrical Characteristics:

              - Motor Horsepower: [1/6] [1/5] [1/4] <Insert value>.

              - Volts: 120 V ac.

              - Phase: Single.

              - Hertz: 60 Hz.

              - Full-Load Amperes: <Insert value> A.

              - Minimum Circuit Ampacity: <Insert value> A.

              - Maximum Overcurrent Protection: <Insert value> A.

Copy "Pressure Water Coolers - Freestanding, Floor-Mounted, Single-Station, Powder-Coated Metal" Paragraph below and re-edit for each type of pressure water cooler required.

Insert drawing designation. Use these designations on Drawings to identify each pressure water cooler.

        - Pressure Water Coolers - Freestanding, Floor-Mounted, Single-Station, Powder-Coated Metal: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain freestanding, floor-mounted, single-station, powder-coated-metal pressure water coolers -from single source from single manufacturer.

          - Bubbler: One, with adjustable stream regulator, located on deck.

          - Control: [Push button] [Foot pedal] <Insert control>.

          - Drain: Grid with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

          - Cooling System: Electric, with[ precooler,] hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

Retain "Glass Filler" Subparagraph below only if required.

          - Glass filler.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

          - Capacities and Characteristics:

            - Cooled Water: [5 gph (0.0053 L/s)] [8 gph (0.0084 L/s)] [10 gph (0.0105 L/s)] [14 gph (0.0147 L/s)] <Insert value>.

            - Ambient-Air Temperature: 90 deg F (32 deg C).

            - Inlet-Water Temperature: 80 deg F (27 deg C).

            - Cooled-Water Temperature: 50 deg F (10 deg C).

            - Cooled-Water Storage: <Insert gal. (L)>.

            - Electrical Characteristics:

              - Motor Horsepower: [1/6] [1/5] [1/4] <Insert value>.

              - Volts: 120 V ac.

              - Phase: Single.

              - Hertz: 60 Hz.

              - Full-Load Amperes: <Insert value> A.

              - Minimum Circuit Ampacity: <Insert value> A.

              - Maximum Overcurrent Protection: <Insert value> A.

Copy "Pressure Water Coolers - Freestanding, Floor-Mounted, Single-Station, Vinyl-Covered Metal with Stainless Steel Top" Paragraph below and re-edit for each type of pressure water cooler required.

Insert drawing designation. Use these designations on Drawings to identify each pressure water cooler.

        - Pressure Water Coolers - Freestanding, Floor-Mounted, Single-Station, Vinyl-Covered Metal with Stainless Steel Top: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain freestanding, floor-mounted, single-station, vinyl-covered metal with stainless steel top, pressure water coolers from single source from single manufacturer.

          - Bubbler: One, with adjustable stream regulator, located on deck.

          - Control: [Push button] [Foot pedal] <Insert control>.

          - Drain: Grid with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

          - Cooling System: Electric, with[ precooler,] hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

Retain "Glass filler" Subparagraph below only if required.

          - Glass filler.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

          - Capacities and Characteristics:

            - Cooled Water: [5 gph (0.0053 L/s)] [8 gph (0.0084 L/s)] [10 gph (0.0105 L/s)] [14 gph (0.0147 L/s)] <Insert value>.

            - Ambient-Air Temperature: 90 deg F (32 deg C).

            - Inlet-Water Temperature: 80 deg F (27 deg C).

            - Cooled-Water Temperature: 50 deg F (10 deg C).

            - Cooled-Water Storage: <Insert gal. (L)>.

            - Electrical Characteristics:

              - Motor Horsepower: [1/6] [1/5] [1/4] <Insert value>.

              - Volts: 120 V ac.

              - Phase: Single.

              - Hertz: 60 Hz.

              - Full-Load Amperes: <Insert value> A.

              - Minimum Circuit Ampacity: <Insert value> A.

              - Maximum Overcurrent Protection: <Insert value> A.

Copy "Pressure Water Coolers - Surface Wall-Mounted, Stainless Steel" Paragraph below and re-edit for each type of pressure water cooler required.

Insert drawing designation. Use these designations on Drawings to identify each pressure water cooler.

        - Pressure Water Coolers - Surface Wall-Mounted, Stainless Steel: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain surface wall-mounted, stainless steel, pressure water coolers from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Bubbler: One, with adjustable stream regulator, located on each cabinet deck.

          - Control: [Push button] [Push bar] [Sensor] <Insert control>.

Retain "Glass filler" Subparagraph below only if required.

          - Glass filler.

Retain "Bottle Filler" Subparagraph below only if required.

          - Bottle Filler: [Sensor] [Push-button] activation[, with] [20-second] <Insert value> [automatic shutoff timer]: Fill rate [0.5 to 1.5 gpm (0.03155 to 0.09464 L/s)] <Insert value>.

          - Drain: Grid with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

          - Cooling System: Electric, with hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

Coordinate "Support" Subparagraph below with "Supports" Article.

          - Support: Water-cooler carrier.

          - Water-Cooler Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1] [High/low - standard/accessible in accordance with ICC A117.1].

          - Capacities and Characteristics:

            - Cooled Water: [5 gph (0.0053 L/s)] [8 gph (0.0084 L/s)] <Insert value>.

            - Ambient-Air Temperature: 90 deg F (32 deg C).

            - Inlet-Water Temperature: 80 deg F (27 deg C).

            - Cooled-Water Temperature: 50 deg F (10 deg C).

            - Cooled-Water Storage: <Insert value>.

            - Electrical Characteristics:

              - Motor Horsepower: [1/6] [1/5] [1/4] [1/3] <Insert value>.

              - Volts: 120 V ac.

              - Phase: Single.

              - Hertz: 60 Hz.

              - Full-Load Amperes: <Insert value> A.

              - Minimum Circuit Ampacity: <Insert value> A.

              - Maximum Overcurrent Protection: <Insert value> A.

Copy "Pressure Water Coolers - Surface Wall-Mounted, Powder-Coated Metal" Paragraph below and re-edit for each type of pressure water cooler required.

Insert drawing designation. Use these designations on Drawings to identify each pressure water cooler.

        - Pressure Water Coolers - Surface Wall-Mounted, Powder-Coated Metal: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain surface wall-mounted, powder-coated-metal, pressure water coolers from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Bubbler: One, with adjustable stream regulator, located on each cabinet deck.

          - Control: [Push button] [Push bar] [Sensor] <Insert control>.

Retain "Glass filler" Subparagraph below only if required.

          - Glass filler.

Retain "Bottle Filler" Subparagraph below only if required.

          - Bottle Filler: [Sensor] [Push-button] activation[, with] [20-second] <Insert value> [automatic shutoff timer]: Fill rate [0.5 to 1.5 gpm (0.03155 to 0.09464 L/s)] <Insert value>.

          - Drain: Grid with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

          - Cooling System: Electric, with hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

Coordinate "Support" Subparagraph below with "Supports" Article.

          - Support: Water-cooler carrier.

          - Water-Cooler Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1] [High/low - standard/accessible in accordance with ICC A117.1].

          - Capacities and Characteristics:

            - Cooled Water: [5 gph (0.0053 L/s)] [8 gph (0.0084 L/s)] <Insert value>.

            - Ambient-Air Temperature: 90 deg F (32 deg C).

            - Inlet-Water Temperature: 80 deg F (27 deg C).

            - Cooled-Water Temperature: 50 deg F (10 deg C).

            - Cooled-Water Storage: <Insert value>.

            - Electrical Characteristics:

              - Motor Horsepower: [1/6] [1/5] [1/4] [1/3] <Insert value>.

              - Volts: 120 V ac.

              - Phase: Single.

              - Hertz: 60 Hz.

              - Full-Load Amperes: <Insert value> A.

              - Minimum Circuit Ampacity: <Insert value> A.

              - Maximum Overcurrent Protection: <Insert value> A.

Copy "Pressure Water Coolers - Surface Wall-Mounted, Vinyl-Covered Metal with Stainless Steel Top" Paragraph below and re-edit for each type of pressure water cooler required.

Insert drawing designation. Use these designations on Drawings to identify each pressure water cooler.

        - Pressure Water Coolers - Surface Wall-Mounted, Vinyl-Covered Metal with Stainless Steel Top: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain surface wall-mounted, vinyl-covered metal with stainless steel top, pressure water coolers from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Bubbler: One, with adjustable stream regulator, located on each cabinet deck.

          - Control: [Push button] [Push bar] [Sensor] <Insert control>.

Retain "Glass filler" Subparagraph below only if required.

          - Glass filler.

Retain "Bottle Filler" Subparagraph below only if required.

          - Bottle Filler: [Sensor] [Push-button] activation[, with] [20-second] <Insert value> [automatic shutoff timer]: Fill rate [0.5 to 1.5 gpm (0.03155 to 0.09464 L/s)] <Insert value>.

          - Drain: Grid with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

          - Cooling System: Electric, with hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

Coordinate "Support" Subparagraph below with "Supports" Article.

          - Support: Water-cooler carrier.

          - Water-Cooler Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1] [High/low - standard/accessible in accordance with ICC A117.1].

          - Capacities and Characteristics:

            - Cooled Water: [5 gph (0.0053 L/s)] [8 gph (0.0084 L/s)] <Insert value>.

            - Ambient-Air Temperature: 90 deg F (32 deg C).

            - Inlet-Water Temperature: 80 deg F (27 deg C).

            - Cooled-Water Temperature: 50 deg F (10 deg C).

            - Cooled-Water Storage: <Insert value>.

            - Electrical Characteristics:

              - Motor Horsepower: [1/6] [1/5] [1/4] [1/3] <Insert value>.

              - Volts: 120 V ac.

              - Phase: Single.

              - Hertz: 60 Hz.

              - Full-Load Amperes: <Insert value> A.

              - Minimum Circuit Ampacity: <Insert value> A.

              - Maximum Overcurrent Protection: <Insert value> A.

Copy "Pressure Water Coolers - Inwall Frame/Plate, Wall-Mounted, Stainless Steel" Paragraph below and re-edit for each type of pressure water cooler required.

Insert drawing designation. Use these designations on Drawings to identify each pressure water cooler.

        - Pressure Water Coolers - Inwall Frame/Plate, Wall-Mounted, Stainless Steel: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain inwall frame/plate, wall-mounted, stainless steel, pressure water coolers from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Bubbler: One, with adjustable stream regulator, located on each cabinet deck.

          - Control: [Push button] [Push bar] [Sensor]<Insert control>.

Retain "Glass filler" Subparagraph below only if required.

          - Glass filler.

Retain "Bottle Filler" Subparagraph below only if required.

          - Bottle Filler: [Sensor] [Push-button] activation[, with] [20-second] <Insert value> [automatic shutoff timer]. Fill rate [0.5 to 1.5 gpm (0.03155 to 0.09464 L/s)] <Insert value>.

          - Drain: Grid with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

          - Cooling System: Electric, with hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

          - Support: Provide manufacturer's support frame for attachment to substrate.

          - Water-Cooler Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1] [High/low - standard/accessible in accordance with ICC A117.1].

          - Capacities and Characteristics:

            - Cooled Water: [5 gph (0.0053 L/s)] [8 gph (0.0084 L/s)] <Insert value>.

            - Ambient-Air Temperature: 90 deg F (32 deg C).

            - Inlet-Water Temperature: 80 deg F (27 deg C).

            - Cooled-Water Temperature: 50 deg F (10 deg C).

            - Cooled-Water Storage: <Insert value>.

            - Electrical Characteristics:

              - Motor Horsepower: [1/6] [1/5] [1/4] [1/3] <Insert value>.

              - Volts: 120 V ac.

              - Phase: Single.

              - Hertz: 60 Hz.

              - Full-Load Amperes: <Insert value> A.

              - Minimum Circuit Ampacity: <Insert value> A.

              - Maximum Overcurrent Protection: <Insert value> A.

Copy "Pressure Water Coolers - Inwall Frame/Plate, Wall-Mounted, Powder-Coated Metal" Paragraph below and re-edit for each type of pressure water cooler required.

Insert drawing designation. Use these designations on Drawings to identify each pressure water cooler.

        - Pressure Water Coolers - Inwall Frame/Plate, Wall-Mounted, Powder-Coated Metal: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain inwall frame/plate, wall-mounted, powder-coated-metal, pressure water coolers from single source from single manufacturer.

          - Type: [Vandal resistant] [and] [freeze resistant].

          - Bubbler: One, with adjustable stream regulator, located on each cabinet deck.

          - Control: [Push button] [Push bar] [Sensor]<Insert control>.

Retain "Glass filler" Subparagraph below only if required.

          - Glass filler.

Retain "Bottle Filler" Subparagraph below only if required.

          - Bottle Filler: [Sensor] [Push-button] activation[, with] [20-second] <Insert value> [automatic shutoff timer]. Fill rate [0.5 to 1.5 gpm (0.03155 to 0.09464 L/s)] <Insert value>.

          - Drain: Grid with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

          - Cooling System: Electric, with hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

          - Support: Provide manufacturer's support frame for attachment to substrate.

          - Water-Cooler Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1] [High/low - standard/accessible in accordance with ICC A117.1].

          - Capacities and Characteristics:

            - Cooled Water: [5 gph (0.0053 L/s)] [8 gph (0.0084 L/s)] <Insert value>.

            - Ambient-Air Temperature: 90 deg F (32 deg C).

            - Inlet-Water Temperature: 80 deg F (27 deg C).

            - Cooled-Water Temperature: 50 deg F (10 deg C).

            - Cooled-Water Storage: <Insert value>.

            - Electrical Characteristics:

              - Motor Horsepower: [1/6] [1/5] [1/4] [1/3] <Insert value>.

              - Volts: 120 V ac.

              - Phase: Single.

              - Hertz: 60 Hz.

              - Full-Load Amperes: <Insert value> A.

              - Minimum Circuit Ampacity: <Insert value> A.

              - Maximum Overcurrent Protection: <Insert value> A.

Copy "Pressure Water Coolers - Semi-Recessed, Wall-Mounted, Stainless Steel" Paragraph below and re-edit for each type of pressure water cooler required.

Insert drawing designation. Use these designations on Drawings to identify each pressure water cooler.

Semi-recessed pressure water coolers are unsuitable for accessible applications. Surface-mounted or fully recessed pressure water coolers should be selected if accessible application is required.

        - Pressure Water Coolers - Semi-Recessed, Wall-Mounted, Stainless Steel: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain semi-recessed, wall-mounted, stainless steel, pressure water coolers from single source from single manufacturer.

          - [Type: Vandal resistant.]

          - Bubbler: One, with adjustable stream regulator, located on deck.

          - Control: [Push button] [Push bar] <Insert control>.

          - Drain: Grid with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

          - Cooling System: Electric, with [precooler, ]hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

          - Support: Provide manufacturer's support frame attachment to substrate.

          - Water-Cooler Mounting Height: [Standard] [Child].

          - Capacities and Characteristics:

            - Cooled Water: [8 gph (0.0084 L/s)] [12 gph (0.0126 L/s)] <Insert value>.

            - Ambient-Air Temperature: 90 deg F (32 deg C).

            - Inlet-Water Temperature: 80 deg F (27 deg C).

            - Cooled-Water Temperature: 50 deg F (10 deg C).

            - Cooled-Water Storage: <Insert value>.

            - Electrical Characteristics:

              - Motor Horsepower: [1/6] [1/5] <Insert value>.

              - Volts: 120 V ac.

              - Phase: Single.

              - Hertz: 60 Hz.

              - Full-Load Amperes: <Insert value> A.

              - Minimum Circuit Ampacity: <Insert value> A.

              - Maximum Overcurrent Protection: <Insert value> A.

Copy "Pressure Water Coolers - Semi-Recessed, Wall-Mounted, Powder-Coated Metal" Paragraph below and re-edit for each type of pressure water cooler required.

Insert drawing designation. Use these designations on Drawings to identify each pressure water cooler.

        - Pressure Water Coolers - Semi-Recessed, Wall-Mounted, Powder-Coated Metal: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain semi-recessed, wall-mounted, powder-coated-metal, pressure water coolers from single source from single manufacturer.

          - [Type: Vandal resistant].

          - Bubbler: One, with adjustable stream regulator, located on deck.

          - Control: [Push button] [Push bar] <Insert control>.

          - Drain: Grid with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

          - Cooling System: Electric, with [precooler, ]hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

          - Support: Provide manufacturer's support frame attachment to substrate.

          - Water-Cooler Mounting Height: [Standard] [Child].

          - Capacities and Characteristics:

            - Cooled Water: [8 gph (0.0084 L/s)] [12 gph (0.0126 L/s)] <Insert value>.

            - Ambient-Air Temperature: 90 deg F (32 deg C).

            - Inlet-Water Temperature: 80 deg F (27 deg C).

            - Cooled-Water Temperature: 50 deg F (10 deg C).

            - Cooled-Water Storage: <Insert value>.

            - Electrical Characteristics:

              - Motor Horsepower: [1/6] [1/5] <Insert value>.

              - Volts: 120 V ac.

              - Phase: Single.

              - Hertz: 60 Hz.

              - Full-Load Amperes: <Insert value> A.

              - Minimum Circuit Ampacity: <Insert value> A.

              - Maximum Overcurrent Protection: <Insert value> A.

Copy "Pressure Water Coolers - Recessed, Wall-Mounted, Stainless Steel" Paragraph below and re-edit for each type of pressure water cooler required.

Insert drawing designation. Use these designations on Drawings to identify each pressure water cooler.

Recessed pressure water coolers intended for accessible applications have the chiller unit mounted above the receptor. If retaining "Accessible in accordance with ICC A117.1" option in "Water-Cooler Mounting Height" Subparagraph, verify that manufacturer has this product available.

        - Pressure Water Coolers - Recessed, Wall-Mounted, Stainless Steel: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain recessed, wall-mounted, stainless steel, pressure water coolers from single source from single manufacturer.

          - [Type: Vandal resistant.]

          - Bubbler: One, with adjustable stream regulator, located on deck.

          - Control: [Push button] [Push bar] <Insert control>.

Retain "Glass filler" Subparagraph below only if required.

          - Glass filler.

          - Drain: Grid with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

          - Cooling System: Electric, with [precooler, ]hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

          - Ventilation Grille: Stainless steel, located [above] [below] water cooler.

          - Support: Provide manufacturer's support frame attachment to substrate.

          - Water-Cooler Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1].

          - Capacities and Characteristics:

            - Cooled Water: [8 gph (0.0084 L/s)] [12 gph (0.0126 L/s)] <Insert value>.

            - Ambient-Air Temperature: 90 deg F (32 deg C).

            - Inlet-Water Temperature: 80 deg F (27 deg C.)

            - Cooled-Water Temperature: 50 deg F (10 deg C).

            - Cooled-Water Storage: <Insert value>.

            - Electrical Characteristics:

              - Motor Horsepower: [1/6] [1/5] <Insert value>.

              - Volts: 120 V ac.

              - Phase: Single.

              - Hertz: 60 Hz.

              - Full-Load Amperes: <Insert value> A.

              - Minimum Circuit Ampacity: <Insert value> A.

              - Maximum Overcurrent Protection: <Insert value> A.

      - BOTTLE FILLING STATION

Copy "Bottle Filling Station - Surface Wall-Mounted, Stainless Steel, Remote Chiller" Paragraph below and re-edit for each type of bottle filling station required.

Surface wall-mounted, bottle filling stations may be paired with other wall-mounted, surface pressure water coolers.

Insert drawing designation. Use these designations on Drawings to identify each bottle filling station.

        - Bottle Filling Station - Surface Wall-Mounted, Stainless Steel, Remote Chiller: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain surface wall-mounted, stainless steel, remote-chiller, bottle filling stations from single source from single manufacturer.

          - Bottle Filler: [Sensor] [Push button] activation[, with] [20-second] <Insert value> [automatic shutoff timer]. Fill rate [0.5 to 1.5 gpm (0.03155 to 0.09464 L/s)] <Insert value>.

          - Drain: Grid with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

Retain "Cooling System" Subparagraph below only if required. Manufacturers no longer offer self-contained cooling for wall-mounted bottle filling stations. Locate cooling system remote with interconnecting piping. If cooling is not required, see Section 224713 "Drinking Fountains" for selection.

          - Cooling System: For remote water chiller, see Section 224723 "Remote Water Coolers."

Coordinate "Support" Subparagraph below with "Supports" Article.

          - Support: Provide manufacturer's support frame attached to substrate.

          - Bottle Filling Station Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1].

Retain "Electrical Characteristics" Subparagraph below only if retaining "Sensor" option in "Bottle Filler" Subparagraph. Manual units do not have electrical requirements. Coordinate with electrical engineer to have receptacle placed below unit.

          - Electrical Characteristics:

            - Volts: 120 V ac.

            - Phase: Single.

            - Hertz: 60 Hz.

Copy "Bottle Filling Station - Recessed, Wall-Mounted, Stainless Steel" Paragraph below and re-edit for each type of bottle filling station required.

Recessed, wall-mounted, bottle filling stations may be paired with other recessed, wall-mounted, pressure water coolers.

Insert drawing designation. Use these designations on Drawings to identify each bottle filling station.

        - Bottle Filling Station - Recessed, Wall-Mounted, Stainless Steel: <Insert drawing designation>.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain recessed, wall-mounted, stainless steel, bottle filling stations from single source from single manufacturer.

          - Bottle Filler: [Sensor] [Push button] activation[, with] [20-second] <Insert value> [automatic shutoff timer]. Fill rate [0.5 to 1.5 gpm (0.03155 to 0.09464 L/s)] <Insert value>.

          - Drain: Grid with NPS 1-1/4 (DN 32) tailpiece.

          - Supply: NPS 3/8 (DN 10) with shutoff valve.

          - Waste Fitting: ASME A112.18.2/CSA B125.2, NPS 1-1/4 (DN 32) brass P-trap.

Retain "Filter" Subparagraph below only if required.

          - Filter: One or more water filters with capacity sized for unit peak flow rate.

If cooling is not required, see Section 224713 "Drinking Fountains" for selection.

          - Cooling System: Electric, with hermetically sealed compressor, cooling coil, air-cooled condensing unit, corrosion-resistant tubing, refrigerant, corrosion-resistant-metal storage tank, and adjustable thermostat.

            - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

          - Capacities and Characteristics:

            - Cooled Water: [5 gph (0.0053 L/s)] [8 gph (0.0084 L/s)] <Insert value>.

            - Ambient-Air Temperature: 90 deg F (32 deg C).

            - Inlet-Water Temperature: 80 deg F (27 deg C).

            - Cooled-Water Temperature: 50 deg F (10 deg C).

            - Cooled-Water Storage: <Insert value>.

            - Electrical Characteristics:

              - Motor Horsepower: [1/6] [1/5] [1/4] [1/3] <Insert value>.

              - Volts: 120 V ac.

              - Phase: Single.

              - Hertz: 60 Hz.

              - Full-Load Amperes: <Insert value> A.

              - Minimum Circuit Ampacity: <Insert value> A.

              - Maximum Overcurrent Protection: <Insert value> A.

            - Ventilation Grille: Stainless steel.

Coordinate "Support" Subparagraph below with "Supports" Article.

          - Support: Provide manufacturer's support frame attached to substrate.

          - Bottle Filling Station Mounting Height: [Standard] [Child] [Accessible in accordance with ICC A117.1].

      - SUPPORTS

        - Water-Cooler Carrier:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: ASME A112.6.1M.

- EXECUTION

      - EXAMINATION

        - Examine roughing-in for water-supply and sanitary drainage and vent piping systems to verify actual locations of piping connections before fixture installation.

        - Examine walls and floors for suitable conditions where fixtures will be installed.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - Install fixtures level and plumb according to roughing-in drawings. For fixtures indicated for children, install at height required by authorities having jurisdiction.

        - Set freestanding, pressure water coolers on floor.

        - Install off-the-floor carrier supports, affixed to building substrate, for wall-mounted fixtures.

        - Install mounting frames, affixed to building construction, and attach recessed, pressure water coolers, and bottle filling stations to mounting frames.

        - Install water-supply piping with shutoff valve on supply to each fixture to be connected to domestic-water distribution piping. Use ball[ or gate] valve. Install valves in locations where they can be easily reached for operation. Valves are specified in Section 220523.12 "Ball Valves for Plumbing Piping"[ and Section 220523.15 "Gate Valves for Plumbing Piping."]

        - Install trap and waste piping on drain outlet of each fixture to be connected to sanitary drainage system.

        - Install wall flanges or escutcheons at piping wall penetrations in exposed, finished locations. Use deep-pattern escutcheons where required to conceal protruding fittings. Comply with escutcheon requirements specified in Section 220518 "Escutcheons for Plumbing Piping."

        - Seal joints between fixtures and walls using sanitary-type, one-part, mildew-resistant, silicone sealant. Match sealant color to fixture color. Comply with sealant requirements specified in Section 079200 "Joint Sealants."

      - PIPING CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Connect fixtures with water supplies, stops, and risers, and with traps, soil, waste, and vent piping. Use size fittings required to match fixtures.

        - Comply with water piping requirements specified in Section 221116 "Domestic Water Piping."

        - Install ball[ or gate] shutoff valve on water supply to each fixture.[ Install valve upstream from filter for water cooler.] Comply with valve requirements specified in Section 220523.12 "Ball Valves for Plumbing Piping"[ and Section 220523.15 "Gate Valves for Plumbing Piping."]

        - Comply with soil and waste piping requirements specified in Section 221316 "Sanitary Waste and Vent Piping."

      - ELECTRICAL CONNECTIONS

        - Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

        - Install electrical devices furnished by manufacturer, but not factory mounted, according to NFPA 70 and NECA 1.

        - Install nameplate for each electrical connection, indicating electrical equipment designation and circuit number feeding connection.

Retain one of two subparagraphs below. First subparagraph cross-references Section 260553 "Identification for Electrical Systems" and should be retained for consistent electrical identification. Second subparagraph is an abbreviated version of the product specified in Section 260553 "Identification for Electrical Systems."

          - Nameplates to be laminated acrylic or melamine plastic signs, as specified in Section 260553 "Identification for Electrical Systems."

          - Nameplates to be laminated acrylic or melamine plastic signs with a black background and engraved white letters at least 1/2 inch (13 mm) high.

      - ADJUSTING

        - Adjust fixture flow regulators for proper flow and stream height.

        - Adjust pressure water-cooler temperature settings.

      - CLEANING

        - After installing fixture, inspect unit. Remove paint splatters and other spots, dirt, and debris. Repair damaged finish to match original finish.

        - Clean fixtures, on completion of installation, according to manufacturer's written instructions.

        - Provide protective covering for installed fixtures.

        - Do not allow use of fixtures for temporary facilities unless approved in writing by Owner.

END OF SECTION 224716