Copyright 2022 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 226119 - COMPRESSED-AIR EQUIPMENT FOR LABORATORY AND HEALTHCARE FACILITIES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Medical compressed-air packaged system.

          - Instrument compressed-air packaged system.

          - Air compressor packaged system - reciprocating, oil less.

          - Air compressor packaged system - liquid ring.

          - Air compressor packaged system - rotary screw.

          - Air compressor packaged system - scroll.

          - Air compressor packaged system - diaphragm.

          - Air filters - inlet type.

          - Compressed-air dryers - refrigerated.

          - Compressed-air dryers - desiccant.

          - Compressed-air purification systems.

          - Compressed-air filter assemblies.

          - Dental compressed-air packaged system.

          - Dental compressed-air system control panels.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - Actual Air: Air delivered at air compressor outlet. Flow rate is compressed air delivered and measured in acfm (actual L/s).

Equipment for laboratory air systems in "Laboratory Air Equipment" Paragraph below is not required to comply with NFPA 99.

        - Laboratory Air Equipment: Compressed-air equipment and accessories for laboratory facilities.

        - Medical Air Equipment: Compressed-air equipment and accessories for [medical] [dental] [and] [instrument] compressed air for healthcare facilities.

        - Standard Air: Free air at 68 deg F (20 deg C) and 1 atmosphere (29.92 in. Hg) before compression or expansion and measured in scfm (standard L/s).

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

          - Medical compressed-air packaged system.

          - Instrument compressed-air packaged system.

          - Air compressor packaged system - reciprocating, oil less.

          - Air compressor packaged system - liquid-ring.

          - Air compressor packaged system - rotary screw.

          - Air compressor packaged system - scroll.

          - Air compressor packaged system - diaphragm.

          - Air filters - inlet type.

          - Compressed-air dryers - refrigerated.

          - Compressed-air dryers - desiccant.

          - Compressed-air purification systems.

          - Compressed-air filter assemblies.

          - Dental compressed-air packaged system.

          - Dental compressed-air system control panels.

        - Product Data Submittals: For each product.

          - Construction details, material descriptions, dimensions of individual components and profiles.

          - Rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

        - Shop Drawings:

          - Plans, elevations, sections, and [mounting] [attachment] details.

          - Details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

          - Vibration Isolation Base Details: Detail fabrication including anchorages and attachments to structure and to supported equipment. Include adjustable motor bases, rails, and frames for equipment mounting.

          - Diagrams for power, signal, and control wiring.

Retain "Delegated Design Submittals" Paragraph below if design services has been delegated to Contractor. If seismic restraints are not applicable, signing and sealing by professional engineer may not be required. Verify with authorities having jurisdiction.

        - Delegated Design Submittals:

          - Detail fabrication and assembly of supports.

          - Include design calculations for selecting vibration isolators[ and seismic restraints] and for designing vibration isolation bases, indicated to comply with performance requirements and design criteria, including analysis data[ signed and sealed by the qualified professional engineer responsible for their preparation].

      - INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Retain "Seismic Qualification Data" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment." See ASCE/SEI 7 for certification requirements for equipment and components.

        - Seismic Qualification Data: Certificates for air compressors, accessories, and components from manufacturer.

          - Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculations.

          - Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

          - Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

Coordinate "Qualification Statements" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article. If inserting additional entities or specialist, add qualifications to "Quality Assurance" Article.

        - Qualification Statements: For [Installer] [and] [testing agency].

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For compressed-air equipment.

          - Indicate actual installed items by marking the submittals with an arrow or box.

      - MAINTENANCE MATERIAL SUBMITTALS

See Section 017700 "Closeout Procedures" for submission of maintenance material items.

        - Extra Stock Material: Furnish extra materials[, from the same production run,] to Owner that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Air Compressor, Inlet-Air Filter Elements: Equal to <Insert number> percent of quantity installed, but no fewer than <Insert number> units.

          - Belts: [One] [Two] <Insert number> for each belt-driven compressor.

      - FIELD CONDITIONS

Retain this article if interruption of existing compressed-air service is required.

        - Interruption of Existing Compressed-Air Service: Do not interrupt service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary service in accordance with the requirements indicated:

          - Notify [Architect] [Construction Manager] [Owner] no fewer than [seven] <Insert number> days in advance of proposed interruption of compressed-air service.

          - Do not proceed with interruption of compressed-air service without [Architect's] [Construction Manager's] [Owner's] written permission.

      - COORDINATION

        - Coordinate sizes and locations of concrete bases with actual equipment provided.

      - DELIVERY, STORAGE, AND HANDLING

        - Comply with manufacturer's written instructions for delivery, storage, and handling.

      - QUALITY ASSURANCE

        - Installer Qualifications:

Retain "Laboratory Air Equipment for Laboratory Facilities" Subparagraph below for equipment in laboratory facilities.

          - Laboratory Air Equipment for Laboratory Facilities: An employer of workers trained and approved by manufacturer.

Retain "Medical Air Equipment for Healthcare Facilities" Subparagraph below for equipment in healthcare facilities.

          - Medical Air Equipment for Healthcare Facilities: Qualify installers in accordance with ASSE 6010.

Retain "Testing Agency Qualifications" Paragraph below if Contractor selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control for Healthcare Facility Medical Compressed-Air Equipment" Article. Qualification requirements are in addition to those specified in Section 014000 "Quality Requirements," which also defines "NRTL" (nationally recognized testing laboratory).

Retain "Testing Agency Qualifications" Paragraph for medical air equipment.

        - Testing Agency Qualifications: An independent testing agency, with the experience and capability to conduct the compressed-air equipment testing indicated, that is[ a member of the Medical Gas Professional Healthcare Organization or is] an NRTL and that is acceptable to authorities having jurisdiction.

          - Qualify testing personnel in accordance with ASSE 6020 for inspectors and ASSE 6030 for verifiers.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

If Project has more than one type or configuration of air compressor assembly, copy appropriate article or paragraph and re-edit for each product. Alternatively, a schedule can be provided on Drawings or in the Specifications. See sample schedules in the Evaluations.

Where the term "simplex" is used in this Section, it means one of the indicated items; "duplex" means two.

      - PERFORMANCE REQUIREMENTS

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

        - Comply with NFPA 99, "Health Care Facilities Code," for compressed-air equipment and accessories for medical and dental compressed-air systems.

        - ASME Compliance: Fabricate and label receivers to comply with 2021 ASME Boiler and Pressure Vessel Code.

Retain "Delegated Design" Paragraph below if Contractor is required to assume responsibility for design.

        - Delegated Design: Engage a qualified professional engineer, as defined in Section 014000 "Quality Requirements," to design compressed-air equipment mounting.

Retain "Seismic Performance" Paragraph below with "Seismic Qualification Data" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Delete paragraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

        - Seismic Performance: Compressed-air equipment to withstand the effects of earthquake motions determined in accordance with [ASCE/SEI 7] <Insert requirement>.[ See Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment."]

Retain first subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

          - The term "withstand" means the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

For life-safety components required to function after an earthquake (such as medical air systems), the Component Importance Factor is 1.5. For other components, the Component Importance Factor is 1.0 unless the structure is in Seismic Use Group III and component is necessary for continued operation of facility or failure of component could impair continued operation of facility, in which case the Component Importance Factor is 1.5.

          - Component Importance Factor: [1.5] [1.0].

See ASCE/SEI 7, Coefficients for Architectural Component Table and Seismic Coefficients for Mechanical and Electrical Components Table for requirements to be inserted in subparagraph below.

          - <Insert requirements for Component Amplification Factor and Component Response Modification Factor>.

      - GENERAL REQUIREMENTS FOR COMPRESSED-AIR SYSTEMS

        - Description: Factory-assembled, -wired, -piped, and -tested; electric-motor-driven; air-cooled; continuous-duty air compressors and receivers that deliver air of quality equal to intake air.

        - Control Panels: Automatic control station with load control and protection functions. Comply with NEMA ICS 2 and UL 508.

          - Enclosure: NEMA ICS 6, Type 12 control panel unless otherwise indicated.

          - Motor Controllers: Full-voltage, combination-magnetic type with undervoltage release feature and motor-circuit-protector-type disconnecting means and short-circuit protective device.

          - Control Voltage: 120 V ac or less, using integral control power transformer.

          - Motor Overload Protection: Overload relay in each phase.

          - Starting Devices: Hand-off-automatic selector switch in cover of control panel, plus pilot device for automatic control.

Retain first subparagraph below for duplex and multiple air compressors.

          - Automatic control switches to [alternate lead-lag air compressors for duplex] [and] [sequence lead-lag air compressors for three or more] air compressors.

          - Instrumentation: Include discharge-air and receiver pressure gauges, air-filter maintenance indicator, hour meter, air compressor discharge-air and coolant temperature gauges, and control transformer.

          - Alarm Signal Device: For connection to alarm system to indicate when backup air compressor is operating.

          - Provide 65k AIC SCCR rating.

        - Receivers: Steel tank constructed in accordance with 2021 ASME Boiler and Pressure Vessel Code: Section VIII, Division 1.

          - Pressure Rating: At least as high as highest discharge pressure of connected air compressors and bearing appropriate code symbols.

          - Interior Finish: Corrosion-resistant coating.

          - Accessories: Include safety valve, pressure gauge, automatic drain, pressure regulator, and piped three-valve bypass with valves.

Retain "Mounting Frame" Paragraph below for projects in seismic areas.

        - Mounting Frame: Fabricate base and attachment to air compressor and components with reinforcement strong enough to resist movement during a seismic event when base is anchored to building structure.

In first article below, insert drawing designation. Use these designations on Drawings to identify each medical compressed-air packaged system.

      - MEDICAL COMPRESSED-AIR PACKAGED SYSTEM <Insert drawing designation>

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain medical compressed-air packaged system from single source from single manufacturer.

        - Description: Medical compressed-air packaged system, factory assembled on a common base, factory tested, fully compliant with NFPA 99 and featuring single-point connections for electrical power, intake air, discharge air, and condensate drains. Components are to include compressor(s), receiver, dryer(s), filter/pressure regulator system, all interconnecting piping, power, and control wiring, and UL-labeled control system.

Coordinate data specified in "Capacities and Characteristics" Paragraph below with piping systems in Section 226113 "Compressed-Air Piping for Laboratory and Healthcare Facilities" and with alarm systems in Section 220963 "Medical Gas Alarms."

        - Capacities and Characteristics:

          - Compressed-Air Service: Medical compressed air.

          - Air Compressor(s): Oil-less [duplex] <Insert number>, [scroll] [or] [reciprocating] <Insert type>.

Retain "Standard-Air Capacity of Each Air Compressor" or "Actual-Air Capacity of Each Air Compressor" Subparagraph below, or both.

          - Standard-Air Capacity of Each Air Compressor: <Insert scfm (standard L/s)> free air.

          - Actual-Air Capacity of Each Air Compressor: <Insert acfm (actual L/s)> delivered.

          - Discharge-Air Pressure: [80 psig (550 kPa)] [125 psig (860 kPa)] [175 psig (1200 kPa)] <Insert value>.

          - Intake-Air Temperature: <Insert deg F (deg C)>.

          - Discharge-Air Temperature: <Insert deg F (deg C)>.

          - Mounting: [Freestanding] [Tank mounted].

          - Motor (Each Air Compressor):

            - Horsepower: <Insert value>.

            - Speed: [1750] [3400] <Insert speed> rpm.

          - Electrical Characteristics:

            - Volts: <Insert value>.

            - Phase(s): [Single] [Three].

            - Hertz: [60] <Insert value>.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

          - Receiver:

            - Orientation: [Horizontal] [Vertical] arrangement.

            - Capacity: <Insert gal. (L)>.

            - Interior Finish: [Epoxy] [Epoxy or galvanized] [Galvanized] <Insert coating>.

            - Pressure Rating: [100 psig (690 kPa)] [125 psig (860 kPa)] [150 psig (1035 kPa)] [200 psig (1380 kPa)] <Insert value> minimum.

            - Pressure Regulator Setting: <Insert psig (kPa)>.

            - Pressure Relief Valve Setting: <Insert psig (kPa)>.

            - Drain: [Automatic] [Manual] valve.

          - Compressed-Air Dryer: [Desiccant] [Refrigerated].

            - Description:

Retain first subparagraph below if retaining "Desiccant" option in "Compressed-Air Dryer" Subparagraph above. Retain second subparagraph below if retaining "Refrigerated" option.

              - Twin-tower unit with purge system, mufflers, and capability to deliver [plus 10 deg F (minus 12 deg C)] <Insert temperature>, 100 psig (690 kPa) air at dew point. Include dew point controlled purge, step-down transformers, disconnect switches, inlet and outlet pressure gauges, thermometers, automatic controls, and filters.

              - Noncycling, air-cooled, electric-motor-driven unit with steel enclosure and capability to deliver 35 deg F (2 deg C), 100 psig (690 kPa) air at dew point. Include automatic ejection of condensate from airstream, step-down transformers, disconnect switches, inlet and outlet pressure gauges, thermometers, automatic controls, and filters.

            - Capacities and Characteristics:

              - Standard-Air Capacity of Each Compressed-Air Dryer: <Insert scfm (standard L/s)> free air.

              - Pressure: <Insert psig (kPa)>.

              - Entering-Air Temperature: <Insert deg F (deg C)>.

              - Leaving-Air Temperature: <Insert deg F (deg C)>.

              - Leaving-Air Pressure Dew Point: <Insert deg F (deg C)>.

              - Ambient-Air Temperature: <Insert deg F (deg C)>.

              - Maximum Air-Pressure Drop: <Insert psig (kPa)>.

              - Inlet Filter: [5] <Insert number> micrometers.

              - Outlet Filter: [1] <Insert number> micrometer(s).

              - Motor Horsepower: <Insert value>.

              - Electrical Characteristics:

                - Volts: <Insert value>.

                - Phase(s): [Single] [Three].

                - Hertz: [60] <Insert value>.

                - Full-Load Amperes: <Insert value>.

                - Minimum Circuit Ampacity: <Insert value>.

                - Maximum Overcurrent Protection: <Insert amperage>.

          - Compressed-air filter and purification system.

          - Control System:

            - Description: Duplex mounted and wired control system.

              - UL labeled.

              - NEMA ICS 6, Type 12 control panel enclosure.

              - Circuit-breaker disconnects for each motor with external operators.

              - Full voltage motor starters with overload protection.

              - 24 V control circuit.

              - 65k AIC SCCR rating.

              - Touchscreen controls.

              - Screen displays and functions (to include, but not limited to, the following):

                - Service alerts.

                - Runtime hours.

                - System status.

                - System pressure level.

                - Dew point level.

                - CO level.

                - Event logs.

                - <Insert type>.

              - Ethernet connectivity with embedded web page for remote monitoring.

              - Integral connectivity to the medical gas network via Ethernet.

              - Optional connectivity - BACnet communication with TCP/IP protocol.

In first article below, insert drawing designation. Use these designations on Drawings to identify each instrument compressed-air packaged system.

      - INSTRUMENT COMPRESSED-AIR PACKAGED SYSTEM <Insert drawing designation>

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain instrument compressed-air packaged system from single source from single manufacturer.

        - Description: Instrument compressed-air packaged system, factory assembled on a common base, factory tested, fully compliant with NFPA 99 and featuring single-point connections for electrical power, intake air, discharge air, and condensate drains. Components are to include compressor(s), receiver, dryer(s), filter/pressure regulator system, all interconnecting piping, power, and control wiring, and UL-labeled control system.

        - Capacities and Characteristics:

          - Compressed-Air Service: Instrument compressed air.

          - Air Compressor(s): [Duplex] <Insert number>, [reciprocating] <Insert type>.

Retain "Standard-Air Capacity of Each Air Compressor" or "Actual-Air Capacity of Each Air Compressor" Subparagraph below, or both.

          - Standard-Air Capacity of Each Air Compressor: <Insert scfm (standard L/s)> free air.

          - Actual-Air Capacity of Each Air Compressor: <Insert acfm (actual L/s)> delivered.

          - Discharge-Air Pressure: [125 psig (860 kPa)] [175 psig (1200 kPa)] <Insert value>.

          - Intake-Air Temperature: <Insert deg F (deg C)>.

          - Discharge-Air Temperature: <Insert deg F (deg C)>.

          - Mounting: [Freestanding] [Tank mounted].

          - Motor (Each Air Compressor):

            - Horsepower: <Insert value>.

            - Speed: [1750] [3400] <Insert speed> rpm.

          - Electrical Characteristics:

            - Volts: <Insert value>.

            - Phase(s): [Single] [Three].

            - Hertz: [60] <Insert value>.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

          - Receiver:

            - Orientation: [Horizontal] [Vertical] arrangement.

            - Capacity: <Insert gal. (L)>.

            - Interior Finish: [Epoxy] [Epoxy or galvanized] [Galvanized] <Insert coating>.

            - Pressure Rating: [250 psig (1725 kPa)] <Insert value> minimum.

            - Pressure Regulator Setting: <Insert psig (kPa)>.

            - Pressure Relief Valve Setting: <Insert psig (kPa)>.

            - Drain: [Automatic] [Manual] valve.

          - Compressed-Air Dryer: [Desiccant] <Insert type>.

            - Description: Twin-tower unit with purge system, mufflers, and capability to deliver [plus 10 deg F (minus 12 deg C)] <Insert temperature>, 100 psig (690 kPa) air at dew point. Include dew point controlled purge, step-down transformers, disconnect switches, inlet and outlet pressure gauges, thermometers, automatic controls, and filters.

            - Capacities and Characteristics:

              - Standard-Air Capacity of Each Compressed-Air Dryer: <Insert scfm (standard L/s)> free air.

              - Pressure: <Insert psig (kPa)>.

              - Entering-Air Temperature: <Insert deg F (deg C)>.

              - Leaving-Air Temperature: <Insert deg F (deg C)>.

              - Leaving-Air Pressure Dew Point: <Insert deg F (deg C)>.

              - Ambient-Air Temperature: <Insert deg F (deg C)>.

              - Maximum Air-Pressure Drop: <Insert psig (kPa)>.

              - Inlet Filter: [5] <Insert number> micrometers.

              - Outlet Filter: [1] <Insert number> micrometer(s).

              - Motor Horsepower: <Insert value>.

              - Electrical Characteristics:

                - Volts: <Insert value>.

                - Phase(s): [Single] [Three].

                - Hertz: [60] <Insert value>.

                - Full-Load Amperes: <Insert value>.

                - Minimum Circuit Ampacity: <Insert value>.

                - Maximum Overcurrent Protection: <Insert amperage>.

          - Compressed-air filter and purification system.

          - Control System:

            - Description: Duplex mounted and wired control system.

              - UL labeled.

              - NEMA ICS 6, Type 12 control panel enclosure.

              - Circuit-breaker disconnects for each motor with external operators.

              - Full voltage motor starters with overload protection.

              - 24 V control circuit.

              - 65k AIC SCCR rating.

              - Touchscreen controls.

              - Screen displays and functions (to include, but not limited to, the following):

                - Service alerts.

                - Runtime hours.

                - System status.

                - System pressure level.

                - Dew point level.

                - CO level.

                - Event logs.

                - <Insert type>.

              - Ethernet connectivity with embedded web page for remote monitoring.

              - Integral connectivity to the medical gas network via Ethernet.

              - Optional connectivity - BACnet communication with TCP/IP protocol.

In first article below, insert drawing designation. Use these designations on Drawings to identify each reciprocating, oil-less, air compressor packaged system.

      - AIR COMPRESSOR PACKAGED SYSTEM - RECIPROCATING, OIL LESS <Insert drawing designation>

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain reciprocating, oil-less, air compressors from single source from single manufacturer.

        - Description: Packaged system.

        - Compressor(s): [Single] [or] [two]-stage, oil-less (nonlubricated), reciprocating-piston type, with sealed oil-free bearings, that will deliver air of quality equal to intake air.

          - High discharge-air temperature switch.

          - Belt guard totally enclosing pulleys and belts.

          - Intercooler between stages of two-stage units.

        - Receiver and accessories.

        - Capacities and Characteristics:

          - Compressed-Air Service: [Dental] [Laboratory] <Insert service> air.

          - Air Compressor(s): [Simplex] [Duplex] <Insert number>.

Retain "Standard-Air Capacity of Each Air Compressor" or "Actual-Air Capacity of Each Air Compressor" Subparagraph below, or both.

          - Standard-Air Capacity of Each Air Compressor: <Insert scfm (standard L/s)> free air.

          - Actual-Air Capacity of Each Air Compressor: <Insert acfm (actual L/s)> delivered.

          - Discharge-Air Pressure: [80 psig (550 kPa)] [125 psig (860 kPa)] [175 psig (1200 kPa)] <Insert value>.

          - Intake-Air Temperature: <Insert deg F (deg C)>.

          - Discharge-Air Temperature: <Insert deg F (deg C)>.

          - Mounting: [Freestanding] [Tank mounted].

          - Motor (Each Air Compressor):

            - Horsepower: <Insert value>.

            - Speed: [1750] [3400] <Insert speed> rpm.

          - Electrical Characteristics:

            - Volts: <Insert value>.

            - Phase(s): [Single] [Three].

            - Hertz: [60] <Insert value>.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

          - Receiver:

            - Orientation: [Horizontal] [Vertical] arrangement.

            - Capacity: <Insert gal. (L)>.

            - Interior Finish: [Epoxy] [Epoxy or galvanized] [Galvanized] <Insert coating>.

            - Pressure Rating: [100 psig (690 kPa)] [125 psig (860 kPa)] [150 psig (1035 kPa)] [200 psig (1380 kPa)] <Insert value> minimum.

            - Pressure Regulator Setting: <Insert psig (kPa)>.

            - Pressure Relief Valve Setting: <Insert psig (kPa)>.

            - Drain: [Automatic] [Manual] valve.

In first article below, insert drawing designation. Use these designations on Drawings to identify each liquid-ring air compressor packaged system.

      - AIR COMPRESSOR PACKAGED SYSTEM - LIQUID RING <Insert drawing designation>

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain liquid-ring air compressors from single source from single manufacturer.

        - Description: Packaged system.

        - Compressor(s): Nonpulsating, rotary, liquid-ring type.

          - Construction: [Cast-iron body with bronze rotor] [Bronze body and rotor] [Cast-iron or bronze body and bronze rotor].

          - Coupling: Nonlubricated, flexible type.

Verify, with authorities having jurisdiction, that once through (non-circulated) potable water is acceptable. Verify that recirculated water is acceptable for the indicated application.

          - Sealing Fluid: Potable water.

        - Capacities and Characteristics:

          - Compressed-Air Service: [Laboratory] <Insert service> air.

          - Compressor(s): [Simplex] [Duplex] <Insert number>.

Retain "Standard-Air Capacity of Each Air Compressor" or "Actual-Air Capacity of Each Air Compressor" Subparagraph below, or both.

          - Standard-Air Capacity of Each Air Compressor: <Insert scfm (standard L/s)> free air.

          - Actual-Air Capacity of Each Air Compressor: <Insert acfm (actual L/s)> delivered.

          - Discharge-Air Pressure: [80 psig (550 kPa)] [100 psig (690 kPa)] <Insert value>.

          - Intake-Air Temperature: <Insert deg F (deg C)>.

          - Discharge-Air Temperature: <Insert deg F (deg C)>.

          - Mounting: [Freestanding] [Tank mounted].

          - Motor (Each Air Compressor):

            - Horsepower: <Insert value>.

            - Speed: [1750] [3400] <Insert speed> rpm.

          - Electrical Characteristics:

            - Volts: <Insert value>.

            - Phase(s): [Single] [Three].

            - Hertz: [60] <Insert value>.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

          - Receiver: ASME construction steel tank.

            - Orientation: [Horizontal] [Vertical] arrangement.

            - Capacity: <Insert gal. (L)>.

            - Interior Finish: [Epoxy] [Epoxy or galvanized] [Galvanized] <Insert coating>.

            - Pressure Rating: [100 psig (690 kPa)] [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert value> minimum.

            - Pressure Regulator Setting: <Insert psig (kPa)>.

            - Pressure Relief Valve Setting: <Insert psig (kPa)>.

            - Drain: [Automatic] [Manual] valve.

In first article below, insert drawing designation. Use these designations on Drawings to identify each rotary screw air compressor packaged system.

      - AIR COMPRESSOR PACKAGED SYSTEM - ROTARY SCREW <Insert drawing designation>

To prevent possible compressor malfunction and oil carryover into compressed-air system, use purification systems with this type of air compressor.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain rotary-screw air compressors from single source from single manufacturer.

        - Description: Packaged system.

        - Air Compressor(s): Single-stage, oil-free, rotary-screw type with nonlubricated helical screws and lubricated gearbox, and of construction that prohibits oil from entering compression chamber.

          - Cooling/Lubrication System: Unit-mounted, air-cooled exchanger package prepiped to unit; with air-pressure circulation system with coolant stop valve, full-flow coolant filter, and thermal-bypass valve.

          - Air Filter: Dry type, with maintenance indicator and cleanable replaceable filter element.

          - Air/Coolant Receiver and Separation System: 150 psig (1035 kPa) rated steel tank with ASME safety valve, coolant-level gauge, multistage air-coolant separator element, minimum pressure valve, blowdown valve, discharge check valve, coolant stop valve, full-flow coolant filter, and thermal-bypass valve.

          - Capacity Control: Capacity modulation between zero and 100 percent air delivery, with operating pressures between 50 and 100 psig (345 and 690 kPa). Include necessary control to hold constant pressure. When air demand is zero, unload compressor by using pressure switch and blowdown valve.

            - Mounting: Freestanding.

        - Sound-attenuation enclosure.

        - Capacities and Characteristics:

          - Compressed-Air Service: [Dental] [Laboratory] <Insert service> air.

          - Air Compressor(s): [Simplex] [Duplex] <Insert number>.

Retain "Standard-Air Capacity of Each Air Compressor" or "Actual-Air Capacity of Each Air Compressor" Subparagraph below, or both.

          - Standard-Air Capacity of Each Air Compressor: <Insert scfm (standard L/s)> free air.

          - Actual-Air Capacity of Each Air Compressor: <Insert acfm (actual L/s)> delivered.

          - Discharge-Air Pressure: [80 psig (550 kPa)] [110 psig (760 kPa)] <Insert value>.

          - Intake-Air Temperature: <Insert deg F (deg C)>.

          - Discharge-Air Temperature: <Insert deg F (deg C)>.

          - Motor (Each Air Compressor):

            - Horsepower: <Insert value>.

            - Speed: [1750] [3400] <Insert speed> rpm.

          - Electrical Characteristics:

            - Volts: <Insert value>.

            - Phase(s): [Single] [Three].

            - Hertz: [60] <Insert value>.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

          - Receiver: ASME construction steel tank.

            - Orientation: [Horizontal] [Vertical] arrangement.

            - Capacity: <Insert gal. (L)>.

            - Interior Finish: [Epoxy] [Epoxy or galvanized] [Galvanized] <Insert coating>.

            - Pressure Rating: [100 psig (690 kPa)] [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert value> minimum.

            - Pressure Regulator Setting: <Insert psig (kPa)>.

            - Pressure Relief Valve Setting: <Insert psig (kPa)>.

            - Drain: [Automatic] [Manual] valve.

In first article below, insert drawing designation. Use these designations on Drawings to identify each scroll air compressor packaged system.

      - AIR COMPRESSOR PACKAGED SYSTEM - SCROLL <Insert drawing designation>

To prevent possible compressor malfunction and oil carryover into compressed-air system, use purification systems with this type of air compressor.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain scroll air compressors from single source from single manufacturer.

        - Description: Packaged system.

        - Air Compressor(s): Single-stage, oil-free, rotary, oscillating-volute type of construction that prohibits oil from entering compression chamber.

          - Mounting: Freestanding.

        - Capacities and Characteristics:

          - Compressed-Air Service: [Dental] [Laboratory] <Insert service> air.

          - Air Compressor(s): [Simplex] [Duplex] <Insert number>.

Retain "Standard-Air Capacity of Each Air Compressor" or "Actual-Air Capacity of Each Air Compressor" Subparagraph below, or both.

          - Standard-Air Capacity of Each Air Compressor: <Insert scfm (standard L/s)> free air.

          - Actual-Air Capacity of Each Air Compressor: <Insert acfm (actual L/s)> delivered.

          - Discharge-Air Pressure: [80 psig (550 kPa)] [110 psig (760 kPa)] <Insert value>.

          - Intake-Air Temperature: <Insert deg F (deg C)>.

          - Discharge-Air Temperature: <Insert deg F (deg C)>.

          - Motor (Each Air Compressor):

            - Horsepower: <Insert value>.

            - Speed: [1750] [3400] <Insert speed> rpm.

          - Electrical Characteristics:

            - Volts: <Insert value>.

            - Phase(s): [Single] [Three].

            - Hertz: [60] <Insert value>.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

          - Receiver: ASME construction steel tank.

            - Orientation: [Horizontal] [Vertical] arrangement.

            - Capacity: <Insert gal. (L)>.

            - Interior Finish: [Epoxy] [Epoxy or galvanized] [Galvanized] <Insert coating>.

            - Pressure Rating: [100 psig (690 kPa)] [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert value> minimum.

            - Pressure Regulator Setting: <Insert psig (kPa)>.

            - Pressure Relief Valve Setting: <Insert psig (kPa)>.

            - Drain: [Automatic] [Manual] valve.

In first article below, insert drawing designation. Use these designations on Drawings to identify each diaphragm air compressor packaged system.

      - AIR COMPRESSOR PACKAGED SYSTEM - DIAPHRAGM <Insert drawing designation>

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Diaphragm air compressors typically have extremely low capacities and do not have a receiver.

        - Source Limitations: Obtain diaphragm air compressors from single source from single manufacturer.

        - Description: Simplex, single-stage, oil-free diaphragm air compressor with nonlubricated compression chamber and lubricated or dry crankcase, and of construction that prohibits oil from entering compression chamber.

Retain "Option" Subparagraph below if these types are acceptable.

          - Option: Construction may be articulating-piston, reciprocating-piston, or rotary-sliding-vane type.

        - Control: Adjustable pressure switch.

        - Mounting: Freestanding.

        - Capacities and Characteristics:

          - Compressed-Air Service: [Laboratory] <Insert service> air.

Retain "Standard-Air Capacity of Air Compressor" or "Actual-Air Capacity of Air Compressor" Subparagraph below, or both.

          - Standard-Air Capacity of Air Compressor: <Insert scfm (standard L/s)> free air.

          - Actual-Air Capacity of Air Compressor: <Insert acfm (actual L/s)> delivered.

          - Discharge-Air Pressure: [10 psig (69 kPa)] [15 psig (103 kPa)] <Insert value>.

Retain "Intake-Air Temperature" or "Discharge-Air Temperature" Subparagraph below if either is required, or both.

          - Intake-Air Temperature: <Insert deg F (deg C)>.

          - Discharge-Air Temperature: <Insert deg F (deg C)>.

          - Motor (Each Air Compressor):

            - Horsepower: <Insert value>.

            - Speed: [1750] [3400] <Insert speed> rpm.

          - Electrical Characteristics:

            - Volts: <Insert value>.

            - Phase(s): [Single] [Three].

            - Hertz: [60] <Insert value>.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

      - AIR FILTERS - INLET TYPE

        - Air Filters - Inlet Type:

          - Source Limitations: Obtain inlet-type air filters from single source from single manufacturer.

Retain one of two subparagraphs below.

          - Combination inlet-air filter-silencer, suitable for remote installation, for each air compressor:

Revise "Construction" Subparagraph below if filter is in-line type and installed in an interior space. Install gooseneck with screen on exterior air inlet.

            - Construction: Weatherproof housing for replaceable, dry-type filter element, with silencer tubes or other method of sound reduction.

            - Capacity: Match capacity of air compressor, with collection efficiency of 99 percent retention of particles larger than 10 micrometers.

          - Combination inlet-air filter-silencer, suitable for remote installation, for multiple air compressors:

Revise "Construction" Subparagraph below if filter is in-line type and installed in an interior space. Install gooseneck with screen on exterior air inlet.

            - Construction: Weatherproof housing for replaceable, dry-type filter element, with silencer tubes or other method of sound reduction.

            - Capacity: Match total capacity of connected air compressors, with collection efficiency of 99 percent retention of particles larger than 10 micrometers.

In first article below, insert drawing designation. Use these designations on Drawings to identify each refrigerant compressed-air dryer.

      - COMPRESSED-AIR DRYERS - REFRIGERATED <Insert drawing designation>

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain refrigerated compressed-air dryers from single source from single manufacturer.

        - Description: Noncycling, air-cooled, electric-motor-driven unit with steel enclosure and capability to deliver 35 deg F (2 deg C), 100 psig (690 kPa) air at dew point. Include automatic ejection of condensate from airstream, step-down transformers, disconnect switches, inlet and outlet pressure gauges, thermometers, automatic controls, and filters.

        - Capacities and Characteristics:

          - Standard-Air Capacity of Each Compressed-Air Dryer: <Insert scfm (standard L/s)> free air.

          - Pressure: <Insert psig (kPa)>.

          - Entering-Air Temperature: <Insert deg F (deg C)>.

          - Leaving-Air Temperature: <Insert deg F (deg C)>.

          - Leaving-Air Pressure Dew Point: <Insert deg F (deg C)>.

          - Ambient-Air Temperature: <Insert deg F (deg C)>.

          - Maximum Air-Pressure Drop: <Insert psig (kPa)>.

          - Inlet Filter: [5] <Insert number> micrometers.

          - Outlet Filter: [1] <Insert number> micrometer(s).

          - Motor Horsepower: <Insert value>.

          - Electrical Characteristics:

            - Volts: <Insert value>.

            - Phase(s): [Single] [Three].

            - Hertz: [60] <Insert value>.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

In first article below, insert drawing designation. Use these designations on Drawings to identify each desiccant compressed-air dryer.

      - COMPRESSED-AIR DRYERS - DESICCANT <Insert drawing designation>

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain desiccant compressed-air dryers from single source from single manufacturer.

        - Description: Twin-tower unit with purge system, mufflers, and capability to deliver [plus 10 deg F (minus 12 deg C)] <Insert temperature>, 100 psig (690 kPa) air at dew point. Include dew point controlled purge, step-down transformers, disconnect switches, inlet and outlet pressure gauges, thermometers, automatic controls, and filters.

        - Capacities and Characteristics:

          - Standard-Air Capacity of Each Compressed-Air Dryer: <Insert scfm (standard L/s)> free air.

          - Pressure: <Insert psig (kPa)>.

          - Entering-Air Temperature: <Insert deg F (deg C)>.

          - Leaving-Air Temperature: <Insert deg F (deg C)>.

          - Leaving-Air Pressure Dew Point: <Insert deg F (deg C)>.

          - Ambient-Air Temperature: <Insert deg F (deg C)>.

          - Maximum Air-Pressure Drop: <Insert psig (kPa)>.

          - Inlet Filter: [5] <Insert number> micrometers.

          - Outlet Filter: [1] <Insert number> micrometer(s).

          - Motor Horsepower: <Insert value>.

          - Electrical Characteristics:

            - Volts: <Insert value>.

            - Phase(s): [Single] [Three].

            - Hertz: [60] <Insert value>.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

In first article below, insert drawing designation. Use these designations on Drawings to identify each compressed-air purification system.

      - COMPRESSED-AIR PURIFICATION SYSTEMS <Insert drawing designation>

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain compressed-air purification systems from single source from single manufacturer.

        - Description: Compressed-air purification system sized for maximum connected equipment capacity with coalescing, particulate, and activated-charcoal filters; compressed-air dryer; catalytic converter; gauges and thermometers; and controls.

        - Include the following capabilities:

          - Removal of excessive moisture, solid particulates, oil and oil mist, carbon monoxide, and hydrocarbon vapors.

          - Automatic ejection of condensate from airstream.

          - Production of air complying with USP - NF for medical air.

          - Capacity and dew point indicated, but not higher than [35 deg F (2 deg C) at 100 psig (690 kPa)] <Insert temperature and value>.

        - Filters: Parallel duplex filters, each sized for maximum system demand, with valved bypass for filter servicing.

          - Inlet Filters: [5] <Insert number> micrometers.

          - Outlet Filters: [1] <Insert number> micrometer(s).

        - Accessories: Inlet and outlet pressure gauges, thermometers, safety valves, and shutoff valves; and automatic ejection of condensate from airstream.

        - Differential Pressure Switch: Adjustable, diaphragm type, with electrical connections for alarm system, to indicate when air-pressure drop through filters rises to more than 2 psig (13.8 kPa) greater than when new and clean.

          - Inlet Connection: From inlet to particulate filter.

          - Outlet Connection: To outlet from final activated-charcoal filter.

        - Compressed-Air Dryer: [Twin-tower desiccant type with automatic controls, purge system, and mufflers] [Noncycling refrigerant type].

        - Capacities and Characteristics:

          - Standard-Air Capacity of Each Compressed-Air Purification System: <Insert scfm (standard L/s)> free air.

          - Entering-Air Pressure: <Insert psig (kPa)>.

          - Entering-Air Temperature: <Insert deg F (deg C)>.

          - Leaving-Air Temperature: <Insert deg F (deg C)>.

          - Leaving-Air Pressure Dew Point: <Insert deg F (deg C)>.

          - Ambient-Air Temperature: <Insert deg F (deg C)>.

          - Maximum Compressed-Air Pressure Drop: <Insert psig (kPa)>.

          - Electrical Characteristics:

            - Volts: <Insert value>.

            - Phase(s): [Single] [Three].

            - Hertz: [60] <Insert value>.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

In first article below, insert drawing designation. Use these designations on Drawings to identify each compressed-air filter assembly.

      - COMPRESSED-AIR FILTER ASSEMBLIES <Insert drawing designation>

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain compressed-air filter assemblies from single source from single manufacturer.

        - Description: Filter assemblies suitable for compressed air, in parallel duplex arrangement. Size each assembly for maximum capacity of connected equipment and operating pressure of compressed-air system. Include automatic ejection of condensate from airstream, inlet and outlet pressure gauges, and shutoff valves.

          - Option: Factory-fabricated filter system consisting of three air filters equivalent to those specified, pipe, fittings, valves, differential pressure switch, and enclosure; and with additional automatic drain traps and gauges.

        - Size filter assemblies for [5 psig (34.5 kPa)] <Insert value> maximum air-pressure drop when filters are new and clean, at system rated capacity, and at 100 psig (690 kPa) pressure.

        - Differential Pressure Switch: Adjustable, diaphragm type, with electrical connections for alarm system, to indicate when air-pressure drop through filters rises to more than 2 psig (13.8 kPa) greater than when new and clean.

        - Particulate Filters: Collection efficiency of 98 percent retention of particles 1 micrometer and larger.

        - Odor and Taste Filters: Vapor-absorbing, activated charcoal.

        - Coalescing Filters: Collection efficiency of 99.9 percent retention of particles 0.3 micrometer and smaller.

        - Include automatic drain trap for each filter.

In first article below, insert drawing designation. Use these designations on Drawings to identify each dental compressed-air packaged system.

      - DENTAL COMPRESSED-AIR PACKAGED SYSTEM <Insert drawing designation>

Retain "General Requirements for Compressed-Air Systems" Article if specifying a diaphragm air compressor.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain dental compressed-air systems from single source from single manufacturer.

        - Description: Factory-assembled, -tested, and -packaged; automatic, dental compressed-air system that will deliver air of quality at least equal to intake air; suitable for dental applications and capable of producing air at [80 psig (550 kPa)] <Insert value>.

        - Air Compressor(s): Oil-less reciprocating type.

Retain "Option" Subparagraph below if these types are acceptable.

          - Option: Construction may be oil-free, sliding-vane or scroll type.

        - Compressor Controls: Adjustable, tank-mounted, pressure [switches and alternator for duplex air compressors] [switch for simplex air compressor].

        - Check Valves: In discharge piping of each air compressor.

        - Air Filter: Integral with air compressor or separate unit for field installation in compressed-air piping.

        - Dryer:

Retain one of two subparagraphs below.

          - Desiccant type, integral with air compressor or separate unit for field installation in compressed-air piping.

          - Refrigerated [35 deg F (2 deg C)] <Insert temperature> dew point, in cabinet with automatic controls, for remote installation. Include on-off switch, on light, inlet and outlet temperature indicators, high-temperature alarm, and rubber isolators on feet.

        - Receiver: Steel tank rated for at least 100 psig (690 kPa) with rubber isolators on feet.

          - Pressure Regulator: Adjustable.

          - Safety Valve: ASME relief valve with setting of 100 psig (690 kPa) or less.

          - Drain: [Automatic] [Manual] valve.

Retain "Cabinet" Subparagraph below if cabinet is required.

        - Cabinet: Enameled steel, with control panel with manual on-off switch, on light, and pressure gauge.[ Refrigeration-type dryer may be separate with integral cabinet.]

        - Capacities and Characteristics:

          - Air Compressor(s): [Simplex] [Duplex] <Insert number>.

Retain "Standard-Air Capacity of Each Air Compressor" or "Actual-Air Capacity of Each Air Compressor" Subparagraph below, or both.

          - Standard-Air Capacity of Each Air Compressor: <Insert scfm (standard L/s)> free air.

          - Actual-Air Capacity of Each Air Compressor: <Insert acfm (actual L/s)> delivered.

          - Discharge-Air Pressure: [80 psig (550 kPa)] <Insert value>.

          - Arrangement: [Duplex, mounted on horizontal] [Simplex, mounted on horizontal] [Simplex, mounted on vertical] receiver.

          - Motor (Each Air Compressor):

            - Horsepower: <Insert value>.

            - Speed: [1750] [3400] <Insert speed> rpm.

          - Electrical Characteristics:

            - Volts: <Insert value>.

            - Phase(s): [Single] [Three].

            - Hertz: [60] <Insert value>.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

In first article below, insert drawing designation. Use these designations on Drawings to identify each dental compressed-air system control panel.

      - DENTAL COMPRESSED-AIR SYSTEM CONTROL PANELS <Insert drawing designation>

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain dental compressed-air system control panels from single source from single manufacturer.

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

        - Description: Wall-mounted type with visual indicators to indicate equipment in operation and to perform the following:

          - Shut off dental air equipment.

          - Shut off water supply to dental air equipment. Include solenoid-operated valve for installation in water piping.

        - Control panels may be combined with dental vacuum pump control panels in single dental equipment control panels.

      - MOTORS

Default motor characteristics are specified in Section 220513 "Common Motor Requirements for Plumbing Equipment."

        - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 220513 "Common Motor Requirements for Plumbing Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" paragraphs or subparagraphs.

          - Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from equipment manufacturers and are different from default requirements specified in Section 220513 "Common Motor Requirements for Plumbing Equipment." Consider each subparagraph and retain only those that vary from default requirements.

          - Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

          - Motor Bearings: <Insert requirements>.

          - Unusual Service Conditions:

            - Ambient Temperature: <Insert deg C>.

            - Altitude: <Insert feet (meter)> above sea level.

            - High humidity.

            - <Insert conditions>.

          - Efficiency: Premium efficient.

          - NEMA Design: <Insert designation>.

          - Service Factor: <Insert value>.

Retain "Electrical Characteristics" Subparagraph below if characteristics are not indicated on Drawings or in "Capacities and Characteristics" paragraphs or subparagraphs.

          - Electrical Characteristics:

            - Horsepower: <Insert horsepower>.

            - Volts: [120] [208] [230] [460] <Insert value>.

            - Phase: [Single] [Poly].

            - Hertz: [60] <Insert value>.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

- EXECUTION

      - PREPARATION

        - Compressed-air equipment, accessories, and components are to be factory cleaned for oxygen service and sealed and furnished suitable for [laboratory air] [and] [medical/instrument air] applications, in accordance with CGA G-4.1, "Cleaning of Equipment for Oxygen Service."

        - Compressed-air equipment, accessories, and components that have not been cleaned for oxygen service, or have been cleaned but become contaminated and unsuitable for [laboratory air] [and] [medical/instrument air] applications, are not to be used.

      - INSTALLATION OF COMPRESSED-AIR EQUIPMENT

        - General Requirements for Compressed-Air Equipment Installation:

          - Install compressed-air equipment to allow maximum headroom unless specific mounting heights are indicated.

          - Install equipment level and plumb, parallel and perpendicular to other building systems and components in exposed interior spaces unless otherwise indicated.

          - Install equipment to facilitate service, maintenance, and repair or replacement of components. Connect equipment for ease of disconnecting, with minimum interference to other installations. Extend grease fittings to accessible locations.

          - Install equipment to allow right of way for piping installed at required slope.

          - Install the following devices on compressed-air equipment:

            - Thermometer, Pressure Gauge, and Safety Valve: Install on each compressed-air receiver.

            - Pressure Regulators: Install downstream from air compressors, dryers, purification units, and filter assemblies.

            - Drain Valves: Install on aftercoolers, receivers, and dryers. Discharge condensate over nearest floor drain.

Retain "Laboratory Compressed-Air Equipment Installation" Paragraph below for compressed-air equipment in laboratory facilities.

        - Laboratory Compressed-Air Equipment Installation:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

          - Install compressed-air equipment, except wall-mounted equipment[ and diaphragm air compressors], on cast-in-place concrete equipment bases. Comply with requirements for equipment bases and foundations specified in Section 033000 "Cast-in-Place Concrete."

Retain one of first two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic control device type and minimum deflection in supported equipment schedule on Drawings.

          - Comply with requirements for vibration isolation and seismic control devices specified in Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment."

          - Comply with requirements for vibration isolation devices specified in Section 220548.13 "Vibration Controls for Plumbing Piping and Equipment."

          - Install diaphragm air compressors on [floor] [counter] <Insert location>.

            - Anchor air compressors to surface in accordance with manufacturer's written instructions[ and seismic criteria applicable to Project].

Retain "Medical Compressed-Air Equipment Installation" Paragraph below for medical compressed-air equipment in healthcare facilities.

        - Medical Compressed-Air Equipment Installation:

          - Install in accordance with ASSE 6010 and NFPA 99.

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

          - Install compressed-air equipment, except wall-mounted equipment, on cast-in-place concrete equipment bases. Comply with requirements for equipment bases and foundations specified in Section 033000 "Cast-in-Place Concrete."

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic control device type and minimum deflection in supported equipment schedule on Drawings.

          - Comply with requirements for vibration isolation and seismic control devices specified in Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment."

          - Comply with requirements for vibration isolation devices specified in Section 220548.13 "Vibration Controls for Plumbing Piping and Equipment."

Retain "Dental Air System Equipment Installation" Paragraph below for dental air system equipment in a small dental office.

        - Dental Air System Equipment Installation:

          - Install in accordance with ASSE 6010 and NFPA 99.

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

          - Install dental air system units on cast-in-place concrete equipment bases. Comply with requirements for equipment bases and foundations specified in Section 033000 "Cast-in-Place Concrete."

Retain one of first two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic control device type and minimum deflection in supported equipment schedule on Drawings.

          - Comply with requirements for vibration isolation and seismic control devices specified in Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment."

          - Comply with requirements for vibration isolation devices specified in Section 220548.13 "Vibration Controls for Plumbing Piping and Equipment."

          - Maintain manufacturer's recommended clearances for service and maintenance.

          - Install control panels for dental compressed-air equipment on wall near [equipment] [office entrance] <Insert location>.

      - PIPING CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Comply with requirements for water-supply piping specified in Section 221116 "Domestic Water Piping." Drawings indicate general arrangement of piping, fittings, and specialties.

        - Comply with requirements for drain piping specified in Section 221316 "Sanitary Waste and Vent Piping." Drawings indicate general arrangement of piping, fittings, and specialties.

        - Comply with requirements for compressed-air piping specified in Section 226113 "Compressed-Air Piping for Laboratory and Healthcare Facilities." Drawings indicate general arrangement of piping, fittings, and specialties.

        - Where installing piping adjacent to equipment, allow space for service and maintenance.

        - Connect compressed-air piping to compressed-air equipment, accessories, and specialties with shutoff valve and union or flanged connection.

        - Connect water supply to compressed-air equipment that requires water. Include backflow preventer. Backflow preventers are specified in Section 221119 "Domestic Water Piping Specialties."

      - ELECTRICAL CONNECTIONS

        - Connect wiring in accordance with Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

        - Ground equipment in accordance with Section 260526 "Grounding and Bonding for Electrical Systems."

        - Install electrical devices furnished by manufacturer, but not factory mounted, in accordance with NFPA 70 and NECA 1.

        - Install nameplate for each electrical connection, indicating electrical equipment designation and circuit number feeding connection.

Retain one of two subparagraphs below. First subparagraph cross-references Section 260553 "Identification for Electrical Systems" and should be retained for consistent electrical identification. Second subparagraph is an abbreviated version of the product specified in Section 260553 "Identification for Electrical Systems."

          - Nameplate to be laminated acrylic or melamine plastic signs, as specified in Section 260553 "Identification for Electrical Systems."

          - Nameplate to be laminated acrylic or melamine plastic signs with a black background and engraved white letters at least 1/2 inch (13 mm) high.

      - CONTROL CONNECTIONS

        - Install control and electrical power wiring to field-mounted control devices.

        - Connect control wiring in accordance with Section 260523 "Control-Voltage Electrical Power Cables."

      - IDENTIFICATION

        - Identify laboratory compressed-air equipment system components. Comply with requirements for identification specified in Section 220553 "Identification for Plumbing Piping and Equipment."

        - Identify medical compressed-air equipment system components. Comply with requirements for identification specified in Section 220553 "Identification for Plumbing Piping and Equipment" and with NFPA 99.

      - STARTUP SERVICE

        - [Engage a factory-authorized service representative to perform] [Perform] startup service.

          - Complete installation and startup checks in accordance with manufacturer's written instructions.

          - Check for lubricating oil in lubricated-type equipment.

          - Check belt drives for proper tension.

          - Verify that air compressor inlet filters and piping are clear.

          - Check for equipment vibration-control supports and flexible pipe connectors, and verify that equipment is properly attached to substrate.

          - Check safety valves for correct settings. Ensure that settings are higher than air compressor discharge pressure, but not higher than rating of system components.

Retain first subparagraph below if seismic restraints are required.

          - Check for proper seismic restraints.

          - Drain receiver tank(s).

          - Operational Test: After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

          - Test and adjust controls and safeties.

        - Prepare written report documenting testing procedures and results.

      - ADJUSTING

        - Adjust equipment to function smoothly, and lubricate as recommended by manufacturer.

        - Adjust control set points.

      - FIELD QUALITY CONTROL FOR HEALTHCARE FACILITY MEDICAL COMPRESSED-AIR EQUIPMENT

Retain first option in "Testing Agency" Paragraph below if Owner hires an independent testing agency.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

        - Tests and Inspections:

          - Medical Compressed-Air Equipment Testing Coordination: Perform tests, inspections, verifications, and certification of medical compressed-air equipment concurrently with tests, inspections, and certification of [medical vacuum equipment] [medical vacuum piping] [medical compressed-air piping] [and] [medical gas piping] systems.

Tests in "Preparation" Subparagraph below are required by Installer before verification by testing agency.

          - Preparation: Perform medical compressed-air equipment tests in accordance with requirements in NFPA 99 for the following:

            - Air-quality purity test.

            - System operation test.

          - Equipment Verification: Comply with requirements in ASSE 6020, ASSE 6030, and NFPA 99 for verification of medical compressed-air equipment.

          - Replace damaged and malfunctioning controls and equipment.

Revise "Testing Certification" Subparagraph below for exact certification material required.

          - Testing Certification: Certify that specified tests, inspections, and procedures have been performed and certify report results. Include the following:

            - Inspections performed.

            - Procedures, materials, and gases used.

            - Test methods used.

            - Results of tests.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

          - Components will be considered defective if they do not pass tests and inspections and is to be replaced with new components.

        - Prepare test and inspection reports.

      - DEMONSTRATION

        - [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain air compressors[, compressed-air dryers] [compressed-air purification units] [and] [compressed-air filter assemblies].

END OF SECTION 226119