Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 230523.12 - BALL VALVES FOR HVAC PIPING

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Access Manufacturer-Provided, AIA MasterSpec-Based Sections:

<Double click here for this Section based on specific manufacturer’s products set as Basis-of-Design at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provision for LEED 2009, LEED v4, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using the hypertext links.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Brass ball valves.

          - Bronze ball valves.

          - Steel ball valves.

          - Iron ball valves.

          - Stainless steel ball valves.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

        - CWP: Cold working pressure.

        - RPTFE: Reinforced polytetrafluoroethylene.

        - SWP: Steam working pressure.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data: For each type of valve.

      - DELIVERY, STORAGE, AND HANDLING

Information in this article is paraphrased from MSS publications.

        - Prepare valves for shipping as follows:

          - Protect internal parts against rust and corrosion.

          - Protect threads, flange faces, and weld ends.

          - Set ball valves open to minimize exposure of functional surfaces.

        - Use the following precautions during storage:

          - Maintain valve end protection.

          - Store valves indoors and maintain at higher-than-ambient-dew-point temperature. If outdoor storage is necessary, store valves off the ground in watertight enclosures.

        - Use sling to handle large valves; rig sling to avoid damage to exposed parts. Do not use operating handles or stems as lifting or rigging points.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - SOURCE LIMITATIONS

        - Obtain each type of valve from single source from single manufacturer.

      - PERFORMANCE REQUIREMENTS

        - ASME Compliance:

          - ASME B1.20.1 for threads for threaded-end valves.

          - ASME B16.1 for flanges on iron valves.

          - ASME B16.5 for flanges on steel valves.

          - ASME B16.10 and ASME B16.34 for ferrous valve dimensions and design criteria.

Caution: Soldering and brazing methods used to achieve required pressure-temperature ratings may damage internal valve parts. Installers must follow manufacturer's written installation instructions and avoid heating above recommended maximum permitted temperature when soldering.

          - ASME B16.18 for cast copper solder-joint connections.

          - ASME B16.22 for wrought copper and copper alloy solder-joint connections.

          - ASME B16.34 for flanged and threaded end connections.

          - ASME B31.1 for power piping valves.

          - ASME B31.9 for building services piping valves.

        - Provide bronze valves made with dezincification-resistant materials. Bronze valves made with copper alloy (brass) containing more than 15 percent zinc are not permitted.

        - Valve Pressure-Temperature Ratings: Not less than indicated and as required for system pressures and temperatures.

        - Valve Sizes: Same as upstream piping unless otherwise indicated.

        - Valve Actuator Types:

          - Gear Actuator: For quarter-turn valves [NPS 4 (DN 100)] <Insert pipe size> and larger.

          - Hand Lever: For quarter-turn valves smaller than [NPS 4 (DN 100)] <Insert pipe size>.

        - Valves in Insulated Piping:

          - Provide 2-inch (50-mm) extended neck stems.

          - Extended operating handles with nonthermal-conductive covering material, and protective sleeves that allow operation of valves without breaking vapor seals or disturbing insulation.

          - Memory stops that are fully adjustable after insulation is applied.

        - Valve Bypass and Drain Connections: MSS SP-45.

      - BRASS BALL VALVES

Retain one or more paragraphs in this article if brass ball valves are required. MSS SP-110 covers both brass and bronze, copper-alloy ball valves from NPS 1/4 to NPS 4 (DN 8 to DN 100). See the Evaluations and manufacturers' catalogs before selecting brass or bronze ball valves, or both.

Caution: Two-piece ball valves with a full or regular port are recommended for most services. One-piece ball valves have a reduced port and one fewer leak path. Three-piece ball valves are recommended if disassembly without removing valve from piping is required.

Where pressure drop is a concern, use full-port ball valves. For corrosive or high-temperature applications, use ball valves with stainless steel trim.

        - Brass Ball Valves, One Piece:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110.

          - CWP Rating: 400 psig (2760 kPa).

          - Body Design: One piece.

          - Body Material: Forged brass.

          - Ends: Threaded.

          - Seats: PTFE.

          - Stem: Brass.

          - Ball: Chrome-plated brass.

          - Port: Reduced.

        - Brass Ball Valves, Two Piece with Full Port and Brass Trim, Threaded or Soldered Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110.

          - SWP Rating: 150 psig (1035 kPa).

          - CWP Rating: 600 psig (4140 kPa).

          - Body Design: Two piece.

          - Body Material: Forged brass.

          - Ends: Threaded or soldered.

          - Seats: PTFE.

          - Stem: Brass.

          - Ball: Chrome-plated brass.

          - Port: Full.

        - Brass Ball Valves, Two Piece with Full Port and Brass Trim, Press Ends:

Press-end connections are unsuitable for steam or flammable gas service.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110; IAPMO/ANSI Z1157.

          - CWP Rating: 600 psig (4140 kPa).

          - Body Design: Two piece.

          - Body Material: Forged brass.

          - Ends: Press.

          - Seats: PTFE or RPTFE.

          - Stem: Brass.

          - Ball: Chrome-plated brass.

          - Port: Full.

          - O-Ring Seal: Buna-N or EPDM.

        - Brass Ball Valves, Two Piece with Full Port and Stainless Steel Trim, Threaded Ends or Soldered Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110.

          - SWP Rating: 150 psig (1035 kPa).

          - CWP Rating: 600 psig (4140 kPa).

          - Body Design: Two piece.

          - Body Material: Forged brass.

          - Ends: Threaded or soldered.

          - Seats: PTFE.

          - Stem: Stainless steel.

          - Ball: Stainless steel, vented.

          - Port: Full.

        - Brass Ball Valves, Two Piece with Full Port and Stainless Steel Trim, Press Ends:

Press-end connections are unsuitable for steam or flammable gas service.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110; IAPMO/ANSI Z1157.

          - CWP Rating: Minimum 200 psig (1380 kPa).

          - Body Design: Two piece.

          - Body Material: Forged brass.

          - Ends: Press.

          - Press-End Connections Rating: Minimum 200 psig (1380 kPa).

          - Seats: PTFE or RPTFE.

          - Stem: Stainless steel.

          - Ball: Stainless steel, vented.

          - Port: Full.

          - O-Ring Seal: Buna-N or EPDM.

        - Brass Ball Valves, Two Piece with Regular Port and Brass Trim, Threaded or Soldered Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110.

          - SWP Rating: 150 psig (1035 kPa).

          - CWP Rating: 600 psig (4140 kPa).

          - Body Design: Two piece.

          - Body Material: Forged brass.

          - Ends: Threaded or soldered.

          - Seats: PTFE.

          - Stem: Brass.

          - Ball: Chrome-plated brass.

          - Port: Regular.

        - Brass Ball Valves, Two Piece with Regular Port and Stainless Steel Trim, Threaded or Soldered Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110.

          - SWP Rating: 150 psig (1035 kPa).

          - CWP Rating: 600 psig (4140 kPa).

          - Body Design: Two piece.

          - Body Material: Brass or bronze.

          - Ends: Threaded or soldered.

          - Seats: PTFE.

          - Stem: Stainless steel.

          - Ball: Stainless steel, vented.

          - Port: Regular.

        - Brass Ball Valves, Three Piece with Full Port and Brass Trim, Threaded or Soldered Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110.

          - SWP Rating: 150 psig (1035 kPa).

          - CWP Rating: 600 psig (4140 kPa).

          - Body Design: Three piece.

          - Body Material: Forged brass.

          - Ends: Threaded or soldered ends.

          - Seats: PTFE.

          - Stem: Brass.

          - Ball: Chrome-plated brass.

          - Port: Full.

        - Brass Ball Valves, Three Piece with Full Port and Stainless Steel Trim, Threaded or Soldered Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110.

          - SWP Rating: 150 psig (1035 kPa).

          - CWP Rating: 600 psig (4140 kPa).

          - Body Design: Three piece.

          - Body Material: Forged brass.

          - Ends: Threaded or soldered.

          - Seats: PTFE.

          - Stem: Stainless steel.

          - Ball: Stainless steel, vented.

          - Port: Full.

      - BRONZE BALL VALVES

Retain one or more of paragraphs in this article if bronze ball valves are required. MSS SP-110 covers both brass and bronze, copper-alloy ball valves from NPS 1/4 to NPS 4 (DN 8 to DN 100). See the Evaluations and manufacturers' catalogs before selecting brass or bronze ball valves, or both.

Caution: Two-piece ball valves with a full or regular port are recommended for most services. One-piece ball valves have a reduced port and one fewer leak path. Three-piece ball valves are recommended if disassembly without removing valve from piping is required.

Where pressure drop is a concern, use full-port ball valves. For corrosive or high-temperature applications, use ball valves with stainless steel trim.

        - Bronze Ball Valves, One Piece with Bronze Trim, Threaded Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110.

          - CWP Rating: 400 psig (2760 kPa).

          - Body Design: One piece.

          - Body Material: Bronze.

          - Ends: Threaded.

          - Seats: PTFE.

          - Stem: Bronze.

          - Ball: Chrome-plated brass.

          - Port: Reduced.

        - Bronze Ball Valves, One Piece with Stainless Steel Trim, Threaded Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110.

          - CWP Rating: 600 psig (4140 kPa).

          - Body Design: One piece.

          - Body Material: Bronze.

          - Ends: Threaded.

          - Seats: PTFE.

          - Stem: Stainless steel.

          - Ball: Stainless steel, vented.

          - Port: Reduced.

        - Bronze Ball Valves, Two Piece with Full Port and Bronze or Brass Trim, Threaded or Soldered Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110.

          - SWP Rating: 150 psig (1035 kPa).

          - CWP Rating: 600 psig (4140 kPa).

          - Body Design: Two piece.

          - Body Material: Bronze.

          - Ends: Threaded or soldered.

          - Seats: PTFE.

          - Stem: Bronze.

          - Ball: Chrome-plated brass.

          - Port: Full.

        - Bronze Ball Valves, Two Piece with Full Port, and Bronze or Brass Trim, Press Ends:

Press-end connections are unsuitable for flammable gas service.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110; IAPMO/ANSI Z1157.

          - CWP Rating: Minimum 200 psig (1380 kPa).

          - Body Design: Two piece.

          - Body Material: Bronze.

          - Ends: Press.

          - Press-End Connections Rating: Minimum 200 psig (1380 kPa).

          - Seats: PTFE or RTPFE.

          - Stem: Bronze or brass.

          - Ball: Chrome-plated brass.

          - Port: Full.

          - O-Ring Seal: EPDM or Buna-N.

        - Bronze Ball Valves, Two Piece with Full Port and Stainless Steel Trim, Threaded or Soldered Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110.

          - SWP Rating: 150 psig (1035 kPa).

          - CWP Rating: 600 psig (4140 kPa).

          - Body Design: Two piece.

          - Body Material: Bronze.

          - Ends: Threaded or soldered.

          - Seats: PTFE.

          - Stem: Stainless steel.

          - Ball: Stainless steel, vented.

          - Port: Full.

        - Bronze Ball Valves, Two Piece with Regular Port and Bronze or Brass Trim, Threaded Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110.

          - SWP Rating: 150 psig (1035 kPa).

          - CWP Rating: 600 psig (4140 kPa).

          - Body Design: Two piece.

          - Body Material: Bronze.

          - Ends: Threaded.

          - Seats: PTFE.

          - Stem: Bronze.

          - Ball: Chrome-plated brass.

          - Port: Regular.

        - Bronze Ball Valves, Two Piece with Regular Port and Stainless Steel Trim, Threaded Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110.

          - SWP Rating: 150 psig (1035 kPa).

          - CWP Rating: 600 psig (4140 kPa).

          - Body Design: Two piece.

          - Body Material: Bronze.

          - Ends: Threaded.

          - Seats: PTFE.

          - Stem: Stainless steel.

          - Ball: Stainless steel, vented.

          - Port: Regular.

        - Bronze Ball Valves, Three Piece with Full Port and Bronze or Brass Trim, Threaded Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110.

          - SWP Rating: 150 psig (1035 kPa).

          - CWP Rating: 600 psig (4140 kPa).

          - Body Design: Three piece.

          - Body Material: Bronze.

          - Ends: Threaded.

          - Seats: PTFE.

          - Stem: Bronze.

          - Ball: Chrome-plated brass.

          - Port: Full.

        - Bronze Ball Valves, Three Piece with Full Port Stainless Steel Trim, Threaded Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110.

          - SWP Rating: 150 psig (1035 kPa).

          - CWP Rating: 600 psig (4140 kPa).

          - Body Design: Three piece.

          - Body Material: Bronze.

          - Ends: Threaded.

          - Seats: PTFE.

          - Stem: Stainless steel.

          - Ball: Stainless steel, vented.

          - Port: Full.

        - Bronze Ball Valves, Three Piece with Regular Port and Bronze or Brass Trim, Threaded or Soldered Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110; MSS SP-145.

          - CWP Rating: 600 psig (4140 kPa).

          - Body Design: Three piece.

          - Body Material: Bronze.

          - Ends: Threaded.

          - Seats: PTFE.

          - Stem: Bronze.

          - Ball: Chrome-plated brass.

          - Port: Regular.

        - Bronze Ball Valves, Three Piece with Regular Port, and Stainless Steel Trim, Threaded or Soldered Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110.

          - SWP Rating: 150 psig (1035 kPa).

          - CWP Rating: 600 psig (4140 kPa).

          - Body Design: Three piece.

          - Body Material: Bronze.

          - Ends: Threaded or soldered.

          - Seats: PTFE.

          - Stem: Stainless steel.

          - Ball: Stainless steel, vented.

          - Port: Regular.

      - STEEL BALL VALVES

Retain this article if steel ball valves are required. MSS SP-72 covers steel ball valves from NPS 1/2 to NPS 36 (DN 15 to DN 900).

        - Steel Ball Valves with Full Port and Stainless Steel Trim, Class 150:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-72.

          - CWP Rating: 285 psig (1964 kPa).

          - Body Design: Split body.

          - Body Material: Carbon steel, ASTM A216/A216M, Type WCB.

          - Ends: Flanged.

          - Seats: PTFE.

          - Stem: Stainless steel.

          - Ball: Stainless steel, vented.

          - Port: Full.

        - Steel Ball Valves with Full Port and Stainless Steel Trim, Class 300:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-72.

          - CWP Rating: 720 psig (4960 kPa).

          - Body Design: Split body.

          - Body Material: Carbon steel, ASTM A216/A216M, Type WCB.

          - Ends: Flanged.

          - Seats: PTFE.

          - Stem: Stainless steel.

          - Ball: Stainless steel, vented.

          - Port: Full.

      - IRON BALL VALVES

        - Iron Ball Valves, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-72.

          - CWP Rating: 200 psig (1380 kPa).

          - Body Design: Split body.

          - Body Material: ASTM A126, gray iron.

          - Ends: Flanged.

          - Seats: PTFE.

          - Stem: Stainless steel.

          - Ball: Stainless steel.

          - Port: Full.

      - STAINLESS STEEL BALL VALVES

        - Stainless Steel Ball Valves, Two Piece with Full Port, Threaded or Flanged Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Standard: MSS SP-110.

          - CWP Rating: 200 psig (1380 kPa).

          - Body Design: Split body.

          - Body Material: Type 316 stainless steel.

          - Ends: Threaded or flanged.

          - Seats: PTFE.

          - Stem: Type 316 stainless steel.

          - Ball: Type 316 stainless steel.

          - Port: Full.

- EXECUTION

      - EXAMINATION

        - Examine valve interior for cleanliness, freedom from foreign matter, and corrosion. Remove special packing materials, such as blocks, used to prevent disc movement during shipping and handling.

        - Operate valves in positions from fully open to fully closed. Examine guides and seats made accessible by such operations.

        - Examine threads on valve and mating pipe for form and cleanliness.

        - Examine mating flange faces for conditions that might cause leakage. Check bolting for proper size, length, and material. Verify that gasket is of proper size, that its material composition is suitable for service, and that it is free from defects and damage.

        - Do not attempt to repair defective valves; replace with new valves. Remove defective valves from site.

      - INSTALLATION OF VALVES

        - Install valves with unions or flanges at each piece of equipment arranged to allow space for service, maintenance, and equipment removal without system shutdown.

        - Provide support of piping adjacent to valves such that no force is imposed upon valves.

        - Locate valves for easy access.

        - Install valves in horizontal piping with stem at or above center of pipe.

        - Install valves in position to allow full valve actuation movement.

        - Valve Tags: Comply with requirements in Section 230553 "Identification for HVAC Piping and Equipment" for valve tags and schedules.

        - Adhere to manufacturer's written installation instructions. When soldering or brazing valves, do not heat valves above maximum permitted temperature. Do not use solder with melting point temperature above valve manufacturer's recommended maximum.

      - ADJUSTING

        - Adjust or replace valve packing after piping systems have been tested and put into service, but before final adjusting and balancing. Replace valves exhibiting leakage.

      - GENERAL REQUIREMENTS FOR VALVE APPLICATIONS

The Section Text is arranged to provide bronze or brass valves in NPS 2 (DN 50) and smaller and iron valves from NPS 2-1/2 to NPS 12 (DN 65 to DN 300).

Caution: Verify that valve classes and pressure-temperature ratings are adequate for system fluid. Repeat each category listing if necessary and insert required pressure range for each listing. Indicate location of each different pressure system on Drawings.

Retain and revise valve applications in this article and in schedules below. Coordinate with valves specified in Part 2.

        - If valves with specified SWP classes or CWP ratings are unavailable, provide the same types of valves with higher SWP classes or CWP ratings.

        - Select valves with the following end connections:

Press-end connections are not for use with steam or flammable gases. Press-end connections are limited to 200 psig (1380 kPa).

          - For Copper Tubing, NPS 2 (DN 50) and Smaller: Threaded ends except where solder-joint valve-end option or press-end option is indicated in valve schedules below.

          - For Copper Tubing, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Flanged ends except where threaded valve-end option is indicated in valve schedules below.

          - For Copper Tubing, NPS 5 (DN 125) and Larger: Flanged ends.

          - For Steel Piping, NPS 2 (DN 50) and Smaller: Threaded ends.

          - For Steel Piping, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Flanged ends except where threaded valve-end option is indicated in valve schedules below.

          - For Steel Piping, NPS 5 (DN 125) and Larger: Flanged ends.

          - For Stainless Steel Piping, NPS 2 (DN 50) and Smaller: Threaded ends.

          - For Stainless Steel Piping,NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Flanged ends.

      - CHILLED-WATER VALVE SCHEDULE

Caution: No one-piece, reduced-port, brass ball valves with stainless steel trim; three-piece, regular-port, brass ball valves with brass trim; or bronze ball valves with bronze trim are included in the Section Text. Retain brass or stainless steel trim with brass ball valves, or bronze or stainless steel trim with bronze ball valves. Press-end connections are typically only available for two-piece, full-port, ball valves. Revise first paragraph below accordingly.

        - Pipe NPS 2 (DN 50) and Smaller: [Brass] [or] [bronze] ball valves, [one] [two] [three] piece, with [brass] [bronze] [stainless steel] trim, [full] [regular] [reduced] port, and [threaded] [solder] [or] [press-connection]-joint ends.

Retain subparagraph below if solder-joint valve ends are permitted for this application.

          - Valves may be provided with solder-joint ends instead of threaded ends.

        - Pipe NPS 2-1/2 (DN 65) and Larger:

Retain one of two subparagraphs below.

          - Iron ball valves, Class 125.

Retain first subparagraph below if threaded valve ends are permitted for this application.

            - Iron Valves, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): May be provided with threaded ends instead of flanged ends.

          - Steel ball valves, Class 150.

      - CONDENSER-WATER VALVE SCHEDULE

Caution: No one-piece, reduced-port, brass ball valves with stainless steel trim; three-piece, regular-port, brass ball valves with brass trim; or bronze ball valves with bronze trim are included in the Section Text. Retain brass or stainless steel trim with brass ball valves, or bronze or stainless steel trim with bronze ball valves. Press-end connections are typically only available for two-piece, full-port, ball valves. Revise first paragraph below accordingly.

        - Pipe NPS 2 (DN 50) and Smaller: [Brass] [or] [bronze] ball valves, [one] [two] [three] piece with [brass] [bronze] [stainless steel] trim, [full] [regular] [reduced] port, and [threaded] [solder] [or] [press-connection]-joint ends.

Retain subparagraph below if solder-joint valve ends are permitted for this application.

          - Valves may be provided with solder-joint ends instead of threaded ends.

        - Pipe NPS 2-1/2 (DN 65) and Larger:

Retain one of two subparagraphs below.

          - Iron ball valves, Class 125.

Retain first subparagraph below if threaded valve ends are permitted for this application.

            - Iron Valves, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): May be provided with threaded ends instead of flanged ends.

          - Steel ball valves, Class 150.

      - HEATING-WATER VALVE SCHEDULE

Caution: No one-piece, reduced-port, brass ball valves with stainless steel trim; three-piece, regular-port, brass ball valves with brass trim; or bronze ball valves with bronze trim are included in the Section Text. Retain brass or stainless steel trim with brass ball valves, or bronze or stainless steel trim with bronze ball valves. Press-end connections are typically only available for two-piece, full-port, ball valves. Revise first paragraph below accordingly.

        - Pipe NPS 2 (DN 50) and Smaller: [Brass] [or] [bronze] ball valves, [one] [two] [three] piece with [brass] [bronze] [stainless steel] trim, [full] [regular] [reduced] port, and [threaded] [solder] [or] [press-connection]-joint ends.

        - Pipe NPS 2-1/2 (DN 65) and Larger:

Retain one of two subparagraphs below.

          - Iron ball valves, Class 125.

Retain first subparagraph below if threaded valve ends are permitted for this application.

            - Iron Valves, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): May be provided with threaded ends instead of flanged ends.

          - Steel ball valves, Class 150.

      - LOW-PRESSURE STEAM VALVE SCHEDULE - 15 PSIG (104 kPa) OR LESS

Caution: No one-piece, reduced-port, brass ball valves with stainless steel trim; three-piece, regular-port, brass ball valves with brass trim; or bronze ball valves with bronze trim are included in the Section Text. Retain brass or stainless steel trim with brass ball valves, or bronze or stainless steel trim with bronze ball valves.

        - Pipe NPS 2 (DN 50) and Smaller: [Brass] [or] [bronze] ball valves, [one] [two] [three] piece, with [brass] [bronze] [stainless steel] trim, [full] [regular] [reduced] port, and threaded connection.

        - Pipe NPS 2-1/2 (DN 65) and Larger:

Retain one of two subparagraphs below.

          - Iron ball valves, Class 125.

Retain first subparagraph below if threaded valve ends are permitted for this application.

            - Iron Valves, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): May be provided with threaded ends instead of flanged ends.

          - Steel ball valves, Class 150.

      - LOW-PRESSURE CLEAN STEAM VALVE SCHEDULE - 15 PSIG (104 kPa) OR LESS

        - Pipe NPS 2 (DN 50) and Smaller: Stainless steel ball valves, two piece with full port, and threaded ends.

        - Pipe NPS 2-1/2 (DN 65) and Larger: Stainless steel ball valves, two piece with full port, and flanged ends.

      - HIGH-PRESSURE STEAM VALVE SCHEDULE - MORE THAN 15 PSIG (104 kPa)

Caution: No one-piece, reduced-port, brass ball valves with stainless steel trim; three-piece, regular-port, brass ball valves with brass trim; or bronze ball valves with bronze trim are included in the Section Text. Retain brass or stainless steel trim with brass ball valves, or bronze or stainless steel trim with bronze ball valves.

        - Pipe NPS 2 (DN 50) and Smaller: [Brass] [or] [bronze] ball valves, [one] [two] [three] piece with [brass] [bronze] [stainless steel] trim, [full] [regular] [reduced] port, and threaded connection.

        - Pipe NPS 2-1/2 (DN 65) and Larger:

Retain one of two subparagraphs below.

          - Iron ball valves, Class 125.

Retain first subparagraph below if threaded valve ends are permitted for this application.

            - Iron Valves, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): May be provided with threaded ends instead of flanged ends.

          - Steel ball valves, Class 300.

      - HIGH-PRESSURE CLEAN STEAM VALVE SCHEDULE - MORE THAN 15 PSIG (104 kPa)

        - Pipe NPS 2 (DN 50) and Smaller: Stainless steel ball valves, two piece with full port, and threaded ends.

        - Pipe NPS 2-1/2 (DN 65) and Larger: Stainless steel ball valves, two piece with full port, and flanged ends.

      - STEAM-CONDENSATE VALVE SCHEDULE

Caution: No one-piece, reduced-port, brass ball valves with stainless steel trim; three-piece, regular-port, brass ball valves with brass trim; or bronze ball valves with bronze trim are included in the Section Text. Retain brass or stainless steel trim with brass ball valves, or bronze or stainless steel trim with bronze ball valves.

        - Pipe NPS 2 (DN 50) and Smaller: [Brass] [or] [bronze] ball valves, [one] [two] [three] piece with [brass] [bronze] [stainless steel] trim, [full] [regular] [reduced] port, and threaded connection.

        - Pipe NPS 2-1/2 (DN 65) and Larger:

Retain one of two subparagraphs below.

          - Iron ball valves, Class 125.

Retain first subparagraph below if threaded valve ends are permitted for this application.

            - Iron Valves, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): May be provided with threaded ends instead of flanged ends.

          - Steel ball valves, Class 300.

      - CLEAN STEAM-CONDENSATE VALVE SCHEDULE

        - Pipe NPS 2 (DN 50) and Smaller: Stainless steel ball valves, two piece with full port, and threaded ends.

        - Pipe NPS 2-1/2 (DN 65) and Larger: Stainless steel ball valves, two piece with full port, and flanged ends.

END OF SECTION 230523.12