Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 230523.14 - CHECK VALVES FOR HVAC PIPING

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Access Manufacturer-Provided, AIA MasterSpec-Based Sections:

<Double click here for this Section based on specific manufacturer’s products set as Basis-of-Design at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Bronze lift check valves.

          - Bronze swing check valves.

          - Iron swing check valves.

          - Iron swing check valves with closure control.

          - Iron, grooved-end swing check valves.

          - Iron, center-guided check valves.

          - Iron, plate-type check valves.

          - Plastic check valves.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - CWP: Cold working pressure.

        - EPDM: Ethylene-propylene-diene monomer.

        - NBR: Nitrile butadiene rubber (also known as "Buna-N").

        - SWP: Steam working pressure.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data: For each type of valve.

      - DELIVERY, STORAGE, AND HANDLING

Information in this article is paraphrased from MSS.

        - Prepare valves for shipping as follows:

          - Protect internal parts against rust and corrosion.

          - Protect threads, flange faces, grooves, press connections, and weld ends.

          - Block check valves in either closed or open position.

        - Use the following precautions during storage:

          - Maintain valve end protection.

          - Store valves indoors and maintain at higher than ambient dew point temperature. If outdoor storage is necessary, store valves off the ground in watertight enclosures.

        - Use sling to handle large valves; rig sling to avoid damage to exposed parts. Do not use stems or other components as lifting or rigging points unless specifically indicated for this purpose in manufacturer's written instructions.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - SOURCE LIMITATIONS

        - Obtain each type of valve from single source from single manufacturer.

      - PERFORMANCE REQUIREMENTS

        - ASME Compliance:

          - ASME B1.20.1 for threads for threaded-end valves.

          - ASME B16.1 for flanges on iron valves.

          - ASME B16.5 for flanges for metric standard piping.

          - ASME B16.10 and ASME B16.34 for ferrous valve dimensions and design criteria.

Valve solder-joint connections are common in smaller sizes of HVAC piping. Soldering and brazing methods used to achieve required pressure and temperature ratings may damage internal valve parts. Special installation requirements for soldered valves may make threaded valves more cost-effective.

          - ASME B16.18 for cast copper solder joint.

          - ASME B16.22 for wrought copper solder joint.

          - ASME B16.51 for press joint.

          - ASME B31.1 for power piping valves.

          - ASME B31.9 for building services piping valves.

        - AWWA Compliance: Comply with AWWA C606 for grooved-end connections.

        - Provide bronze valves made with dezincification-resistant materials. Bronze valves made with copper alloy (brass) containing more than 15 percent zinc are unacceptable.

Caution: Revise pressure ratings and insert temperature ratings in valve articles if valves with higher ratings are required. Valves larger than NPS 12 (DN 300) typically have a lower pressure rating than smaller valves. Verify pressure requirements for large valves.

        - Valve Pressure-Temperature Ratings: Not less than indicated and as required for system pressures and temperatures.

        - Valve Sizes: Same as upstream piping unless otherwise indicated.

        - Valve Bypass and Drain Connections: MSS SP-45.

      - BRONZE LIFT CHECK VALVES

Retain "Bronze Lift Check Valves with Bronze Disc, Class 125" or "Bronze Lift Check Valves with Nonmetallic Disc, Class 125" Paragraph below, or both, if bronze lift check valves are required. MSS SP-80 covers bronze lift check valves from NPS 1/4 to NPS 3 (DN 8 to DN 80).

        - Bronze Lift Check Valves with Bronze Disc, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-80, Type 1.

            - CWP Rating: 200 psig (1380 kPa).

            - Body Design: Vertical flow.

            - Body Material: ASTM B61 or ASTM B62, bronze.

            - Ends: Threaded.

            - Disc: Bronze.

        - Bronze Lift Check Valves with Nonmetallic Disc, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-80, Type 2.

            - CWP Rating: 200 psig (1380 kPa).

            - Body Design: Vertical flow.

            - Body Material: ASTM B61 or ASTM B62, bronze.

            - Ends: Threaded.

            - Disc: NBR or PTFE.

      - BRONZE SWING CHECK VALVES

Retain one or more of five paragraphs in this article if bronze swing check valves are required. MSS SP-80 covers bronze swing check valves from NPS 1/4 to NPS 3 (DN 8 to DN 80).

        - Bronze Swing Check Valves with Bronze Disc, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-80, Type 3.

            - CWP Rating: 200 psig (1380 kPa).

            - Body Design: Horizontal flow.

            - Body Material: ASTM B62, bronze.

            - Ends: Threaded.

            - Disc: Bronze.

        - Bronze Swing Check Valves with Nonmetallic Disc, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-80, Type 4.

            - CWP Rating: 200 psig (1380 kPa).

            - Body Design: Horizontal flow.

            - Body Material: ASTM B62, bronze.

            - Ends: Threaded.

            - Disc: PTFE.

        - Bronze Swing Check Valves with Bronze Disc, Class 150:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-80, Type 3.

            - CWP Rating: 300 psig (2070 kPa).

            - Body Design: Horizontal flow.

            - Body Material: ASTM B62, bronze.

            - Ends: Threaded.

            - Disc: Bronze.

        - Bronze Swing Check Valves with Nonmetallic Disc, Class 150:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-80, Type 4.

            - CWP Rating: 300 psig (2070 kPa).

            - Body Design: Horizontal flow.

            - Body Material: ASTM B62, bronze.

            - Ends: Threaded.

            - Disc: PTFE.

        - Bronze Swing Check Valves, Press Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-80.

            - CWP Rating: Minimum 200 psig (1380 kPa).

            - Body Design: Horizontal flow.

            - Body Material: ASTM B584, bronze.

            - Ends: Press.

            - Press Ends Connection Rating: Minimum 200 psig (1380 kPa).

            - Disc: Brass or bronze.

      - IRON SWING CHECK VALVES

Retain one or more of three paragraphs in this article if iron swing check valves are required. MSS SP-71 covers iron swing check valves of NPS 2 to NPS 24 (DN 50 to DN 600).

        - Iron Swing Check Valves with Metal Seats, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-71, Type I.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 200 psig (1380 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 150 psig (1035 kPa).

            - Body Design: Clear or full waterway.

            - Body Material: ASTM A126, gray iron with bolted bonnet.

            - Ends: Flanged.

            - Trim: Bronze.

            - Gasket: Asbestos free.

        - Iron Swing Check Valves with Nonmetallic-to-Metal Seats, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-71, Type I.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 200 psig (1380 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 150 psig (1035 kPa).

            - Body Design: Clear or full waterway.

            - Body Material: ASTM A126, gray iron with bolted bonnet.

            - Ends: Flanged.

            - Trim: Composition.

            - Seat Ring: Bronze.

            - Disc Holder: Bronze.

            - Disc: PTFE.

            - Gasket: Asbestos free.

        - Iron Swing Check Valves with Metal Seats, Class 250:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-71, Type I.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 500 psig (3450 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 300 psig (2070 kPa).

            - Body Design: Clear or full waterway.

            - Body Material: ASTM A126, gray iron with bolted bonnet.

            - Ends: Flanged.

            - Trim: Bronze.

            - Gasket: Asbestos free.

      - IRON SWING CHECK VALVES WITH CLOSURE CONTROL

Retain "Iron Swing Check Valves with Lever- and Spring-Closure Control, Class 125" or "Iron Swing Check Valves with Lever and Weight-Closure Control, Class 125" Paragraph below, or both, if iron swing check valves are required. MSS SP-71 covers iron swing check valves from NPS 2 to NPS 24 (DN 50 to DN 600).

        - Iron Swing Check Valves with Lever- and Spring-Closure Control, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-71, Type I.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 200 psig (1380 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 150 psig (1035 kPa).

            - Body Design: Clear or full waterway.

            - Body Material: ASTM A126, gray iron with bolted bonnet.

            - Ends: Flanged.

            - Trim: Bronze.

            - Gasket: Asbestos free.

            - Closure Control: Factory-installed, exterior lever and spring.

        - Iron Swing Check Valves with Lever and Weight-Closure Control, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-71, Type I.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 200 psig (1380 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 150 psig (1035 kPa).

            - Body Design: Clear or full waterway.

            - Body Material: ASTM A126, gray iron with bolted bonnet.

            - Ends: Flanged.

            - Trim: Bronze.

            - Gasket: Asbestos free.

            - Closure Control: Factory-installed, exterior lever and weight.

      - IRON, GROOVED-END SWING CHECK VALVES

Retain this article if iron, grooved-end swing check valves are required. No standard for these valves was located. They are available in NPS 2 to NPS 12 (DN 50 to DN 300).

        - Iron, Grooved-End Swing Check Valves, 300 CWP:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - CWP Rating: 300 psig (2070 kPa).

            - Body Material: ASTM A536, ductile iron.

            - Seal: EPDM.

            - Disc: Spring-operated, ductile iron or stainless steel.

      - IRON, CENTER-GUIDED CHECK VALVES

Retain one or more of 16 paragraphs in this article if iron, center-guided check valves are required. MSS SP-125 covers iron, center-guided check valves of NPS 2 to NPS 42 (DN 50 to DN 1050).

        - Iron, Compact-Wafer, Center-Guided Check Valves with Metal Seat, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-125.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 200 psig (1380 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 150 psig (1035 kPa).

            - Body Material: ASTM A126, gray iron.

            - Style: Compact wafer.

            - Seat: Bronze.

        - Iron, Globe, Center-Guided Check Valves with Metal Seat, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-125.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 200 psig (1380 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 150 psig (1035 kPa).

            - Body Material: ASTM A126, gray iron.

            - Style: Globe, spring loaded.

            - Ends: Flanged.

            - Seat: Bronze.

        - Iron, Compact-Wafer, Center-Guided Check Valves with Metal Seat, Class 150:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-125.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 300 psig (2070 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 250 psig (1725 kPa).

            - Body Material: ASTM A395/A395M or ASTM A536, ductile iron.

            - Style: Compact wafer.

            - Seat: Bronze.

        - Iron, Globe, Center-Guided Check Valves with Metal Seat, Class 150:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-125.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 300 psig (2070 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 250 psig (1725 kPa).

            - Body Material: ASTM A395/A395M or ASTM A536, ductile iron.

            - Style: Globe, spring loaded.

            - Ends: Flanged.

            - Seat: Bronze.

        - Iron, Compact-Wafer, Center-Guided Check Valves with Metal Seat, Class 250:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-125.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 400 psig (2760 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 300 psig (2070 kPa).

            - Body Material: ASTM A126, gray iron.

            - Style: Compact wafer, spring loaded.

            - Seat: Bronze.

        - Iron, Globe, Center-Guided Check Valves with Metal Seat, Class 250:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-125.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 400 psig (2760 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 300 psig (2070 kPa).

            - Body Material: ASTM A126, gray iron.

            - Style: Globe, spring loaded.

            - Ends: Flanged.

            - Seat: Bronze.

        - Iron, Compact-Wafer, Center-Guided Check Valves with Metal Seat, Class 300:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-125.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 500 psig (3450 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 400 psig (2760 kPa).

            - Body Material: ASTM A395/A395M or ASTM A536, ductile iron.

            - Style: Compact wafer, spring loaded.

            - Seat: Bronze.

        - Iron, Globe, Center-Guided Check Valves with Metal Seat, Class 300:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-125.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 500 psig (3450 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 400 psig (2760 kPa).

            - Body Material: ASTM A395/A395M or ASTM A536, ductile iron.

            - Style: Globe, spring loaded.

            - Ends: Flanged.

            - Seat: Bronze.

        - Iron, Compact-Wafer, Center-Guided Check Valves with Resilient Seat, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-125.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 200 psig (1380 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 150 psig (1035 kPa).

            - Body Material: ASTM A126, gray iron.

            - Style: Compact wafer.

            - Seat: [EPDM] [or] [NBR] <Insert material>.

        - Iron, Globe, Center-Guided Check Valves with Resilient Seat, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-125.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 200 psig (1380 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 150 psig (1035 kPa).

            - Body Material: ASTM A126, gray iron.

            - Style: Globe, spring loaded.

            - Ends: Flanged.

            - Seat: [EPDM] [or] [NBR] <Insert material>.

        - Iron, Compact-Wafer, Center-Guided Check Valves with Resilient Seat, Class 150:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-125.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 300 psig (2070 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 250 psig (1725 kPa).

            - Body Material: ASTM A395/A395M or ASTM A536, ductile iron.

            - Style: Compact wafer.

            - Seat: [EPDM] [or] [NBR] <Insert material>.

        - Iron, Globe, Center-Guided Check Valves with Resilient Seat, Class 150:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-125.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 300 psig (2070 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 250 psig (1725 kPa).

            - Body Material: ASTM A395/A395M or ASTM A536, ductile iron.

            - Style: Globe, spring loaded.

            - Ends: Flanged.

            - Seat: [EPDM] [or] [NBR] <Insert material>.

        - Iron, Compact-Wafer, Center-Guided Check Valves with Resilient Seat, Class 250:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-125.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 400 psig (2760 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 300 psig (2070 kPa).

            - Body Material: ASTM A126, gray iron.

            - Style: Compact wafer, spring loaded.

            - Seat: [EPDM] [or] [NBR] <Insert material>.

        - Iron, Globe, Center-Guided Check Valves with Resilient Seat, Class 250:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-125.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 400 psig (2760 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 300 psig (2070 kPa).

            - Body Material: ASTM A126, gray iron.

            - Style: Globe, spring loaded.

            - Ends: Flanged.

            - Seat: [EPDM] [or] [NBR] <Insert material>.

        - Iron, Compact-Wafer, Center-Guided Check Valves with Resilient Seat, Class 300:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-125.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 500 psig (3450 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 400 psig (2760 kPa).

            - Body Material: ASTM A395/A395M or ASTM A536, ductile iron.

            - Style: Compact wafer, spring loaded.

            - Seat: [EPDM] [or] [NBR] <Insert material>.

        - Iron, Globe, Center-Guided Check Valves with Resilient Seat, Class 300:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-125.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 500 psig (3450 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 400 psig (2760 kPa).

            - Body Material: ASTM A395/A395M or ASTM A536, ductile iron.

            - Style: Globe, spring loaded.

            - Ends: Flanged.

            - Seat: [EPDM] [or] [NBR] <Insert material>.

      - IRON, PLATE-TYPE CHECK VALVES

Retain one or more of 10 paragraphs in this article if iron, plate-type check valves are required. API 594 covers iron, plate-type check valves of NPS 2 to NPS 60 (DN 50 to DN 1500).

        - Iron, Dual-Plate Check Valves with Metal Seat, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: API 594.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 200 psig (1380 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 150 psig (1035 kPa).

            - Body Design: Wafer, spring-loaded plates.

            - Body Material: ASTM A126, gray iron.

            - Seat: Bronze.

        - Iron, Dual-Plate Check Valves with Metal Seat, Class 150:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: API 594.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 300 psig (2070 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 250 psig (1725 kPa).

            - Body Design: Wafer, spring-loaded plates.

            - Body Material: ASTM A395/A395M or ASTM A536, ductile iron.

            - Seat: Bronze.

        - Iron, Dual-Plate Check Valves with Metal Seat, Class 250:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: API 594.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 400 psig (2760 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 300 psig (2070 kPa).

            - Body Design: Wafer, spring-loaded plates.

            - Body Material: ASTM A126, gray iron.

            - Seat: Bronze.

        - Iron, Dual-Plate Check Valves with Metal Seat, Class 300:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: API 594.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 500 psig (3450 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 400 psig (2760 kPa).

            - Body Design: Wafer, spring-loaded plates.

            - Body Material: ASTM A395/A395M or ASTM A536, ductile iron.

            - Seat: Bronze.

        - Iron, Single-Plate Check Valves with Resilient Seat, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: API 594.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 200 psig (1380 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 150 psig (1035 kPa).

            - Body Design: Wafer, spring-loaded plate.

            - Body Material: ASTM A126, gray iron.

            - Seat: [EPDM] [or] [NBR] <Insert material>.

        - Iron, Dual-Plate Check Valves with Resilient Seat, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: API 594.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 200 psig (1380 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 150 psig (1035 kPa).

            - Body Design: Wafer, spring-loaded plates.

            - Body Material: ASTM A126, gray iron.

            - Seat: [EPDM] [or] [NBR] <Insert material>.

        - Iron, Dual-Plate Check Valves with Resilient Seat, Class 150:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: API 594.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 300 psig (2070 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 250 psig (1725 kPa).

            - Body Design: Wafer, spring-loaded plates.

            - Body Material: ASTM A395/A395M or ASTM A536, ductile iron.

            - Seat: [EPDM] [or] [NBR] <Insert material>.

        - Iron, Wafer, Single-Plate Check Valves with Resilient Seat, Class 250:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: API 594.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 400 psig (2760 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 300 psig (2070 kPa).

            - Body Design: Wafer, spring-loaded plate.

            - Body Material: ASTM A126, gray iron.

            - Seat: [EPDM] [or] [NBR] <Insert material>.

        - Iron, Dual-Plate Check Valves with Resilient Seat, Class 250:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: API 594.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 400 psig (2760 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 300 psig (2070 kPa).

            - Body Design: Wafer, spring-loaded plates.

            - Body Material: ASTM A126, gray iron.

            - Seat: [EPDM] [or] [NBR] <Insert material>.

        - Iron, Dual-Plate Check Valves with Resilient Seat, Class 300:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: API 594.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 500 psig (3450 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 400 psig (2760 kPa).

            - Body Design: Wafer, spring-loaded plates.

            - Body Material: ASTM A395/A395M or ASTM A536, ductile iron.

            - Seat: [EPDM] [or] [NBR] <Insert material>.

      - PLASTIC CHECK VALVES

        - CPVC Ball Check Valves:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Pressure Rating and Temperature: [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert value> at [73 deg F (23 deg C)] <Insert temperature>.

            - Body Material: CPVC.

            - Body Design: Union-type ball check.

            - End Connections for Valves NPS 2 (DN 50) and Smaller: Detachable, [socket] [or] [threaded].

            - End Connections for Valves NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Detachable, [socket] [socket or threaded] [threaded] [flange].

            - Ball: CPVC.

            - Seals: EPDM- or FKM-rubber O-rings.

        - PVC Ball Check Valves:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Pressure Rating and Temperature: [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert value> at [73 deg F (23 deg C)] <Insert temperature>.

            - Body Material: PVC.

            - Body Design: Union-type ball check.

            - End Connections for Valves NPS 2 (DN 50) and Smaller: Detachable, [socket] [or] [threaded].

            - End Connections for Valves NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Detachable, [socket] [socket or threaded] [threaded] [flange].

            - Ball: PVC.

            - Seals: EPDM- or FKM-rubber O-rings.

- EXECUTION

      - EXAMINATION

        - Examine valve interior for cleanliness, freedom from foreign matter, and corrosion. Remove special packing materials, such as blocks, used to prevent disc movement during shipping and handling.

        - Operate valves in positions from fully open to fully closed. Examine guides and seats made accessible by such operations.

        - Examine threads on valve and mating pipe for form and cleanliness.

        - Examine mating flange faces for conditions that might cause leakage. Check bolting for proper size, length, and material. Verify that gasket is of proper size, that its material composition is suitable for service, and that it is free from defects and damage.

        - Examine press fittings to verify they have been properly pressed.

        - Do not attempt to repair defective valves; replace with new valves.

      - INSTALLATION OF VALVES

        - Install valves with unions or flanges at each piece of equipment arranged to allow service, maintenance, and equipment removal without system shutdown.

        - Provide support of piping adjacent to valves such that no force is imposed upon valves.

        - Locate valves for easy access and where not blocked by equipment, other piping, or building components.

        - Install valves with stem at or above center of pipe.

        - Install valves in position that does not project into aisles or block access to other equipment.

        - Install valves in position to allow full stem and manual operator movement.

        - Verify that joints of each valve have been properly installed and sealed to ensure that there is no leakage or damage.

        - Install check valves for proper direction of flow and as follows:

Revise check valve installation requirements to suit Project; delete those not required.

          - Swing Check Valves: In horizontal position with hinge pin level.

          - [Center-Guided] [and] [Plate-Type] Check Valves: In horizontal or vertical position, between flanges.

          - Lift Check Valves: With stem upright and plumb.

        - Install valve tags. Comply with requirements for valve tags and schedules in Section 230553 "Identification for HVAC Piping and Equipment."

        - Adhere to manufacturer's written installation instructions. When soldering or brazing valves, do not heat valves above maximum permitted temperature. Do not use solder with melting point temperature above valve of manufacturer's recommended maximum.

      - ADJUSTING

        - Adjust or replace valve packing after piping systems have been tested and put into service, but before final adjusting and balancing. Replace valves if persistent leaking occurs.

      - GENERAL REQUIREMENTS FOR VALVE APPLICATIONS

The Section Text is arranged to provide bronze or brass valves in NPS 2 (DN 50) and smaller and iron valves in NPS 2-1/2 to NPS 24 (DN 65 to DN 600).

Caution: Verify that valve classes and pressure and temperature ratings are adequate for system fluid. Repeat each category listing if necessary and indicate each required pressure-temperature range and its location on Drawings.

Retain and revise valve applications in this article. Coordinate with valves specified in Part 2.

        - If valve applications are not indicated, use the following:

          - Pump-Discharge Check Valves:

            - NPS 2 (DN 50) and Smaller: Bronze swing check valves with [bronze] [or] [nonmetallic] disc.

            - NPS 2-1/2 (DN 65) and Larger: Iron swing check valves with lever and weight or with spring or iron, center-guided, [metal] [or] [resilient]-seat check valves.

        - If valves with specified SWP classes or CWP ratings are unavailable, the same types of valves with higher SWP classes or CWP ratings may be substituted.

        - End Connections:

          - For Copper Tubing, NPS 2 (DN 50) and Smaller: Threaded ends, except where solder-joint or press valve-end option is indicated in valve schedules.

          - For Copper Tubing, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Flanged ends, except where threaded valve-end option is indicated in valve schedules.

          - For Copper Tubing, NPS 5 (DN 125) and Larger: Flanged ends.

          - For Steel Piping, NPS 2 (DN 50) and Smaller: Threaded ends.

          - For Steel Piping, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Flanged ends, except where threaded valve-end option is indicated in valve schedules.

          - For Steel Piping, NPS 5 (DN 125) and Larger: Flanged ends.

          - For Grooved-End [Copper Tubing] [and] [Steel Piping], except Steam and Steam Condensate Piping: Valve ends may be grooved.

          - Wafer-Type Valves: Flanged connections.

      - CHILLED-WATER VALVE SCHEDULE

        - Pipe NPS 2 (DN 50) and Smaller:

Retain "Bronze Valves" Subparagraph below if solder-joint valve ends are permitted for this application.

          - Bronze Valves: May be provided with solder-joint [or press ]ends instead of threaded ends.

          - Bronze swing check valves with [bronze] [nonmetallic] disc, [Class 125] [Class 150].

        - Pipe NPS 2-1/2 (DN 65) and Larger:

Retain first subparagraph below if threaded valve ends are permitted for this application.

          - NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Iron valves may be provided with threaded ends instead of flanged ends.

Retain one or more of seven subparagraphs below and indicate location of each type on Drawings.

          - NPS 2-1/2 to NPS 12 (DN 65 to DN 300): Iron swing check valves with lever and [spring] [weight]-closure control, Class 125.

          - NPS 3 to NPS 12 (DN 80 to DN 300): Iron, grooved-end swing check valves, 300 CWP.

          - Iron swing check valves with [metal] [nonmetallic-to-metal] seats, [Class 125] [Class 250].

          - Iron, [compact-wafer] [globe], center-guided check valves [metal] [resilient] seat, [Class 125] [Class 150] [Class 250] [Class 300].

          - Iron, single-plate check valves with resilient seat, Class 125.

          - Iron, dual-plate check valves with metal seat, [Class 125] [Class 150] [Class 250] [Class 300].

          - Iron, dual-plate check valves with resilient seat, [Class 125] [Class 150] [Class 250] [Class 300].

Retain first or second paragraph below if CPVC and/or PVC pipe are specified for any piping applications in Section 232113 "Hydronic Piping."

        - CPVC Pipe [NPS 2 (DN 50)] [NPS 4 (DN 100)] and Smaller: CPVC ball check valve.

        - PVC Pipe [NPS 2 (DN 50)] [NPS 4 (DN 100)] and Smaller: PVC ball check valve.

      - CONDENSER-WATER VALVE SCHEDULE

        - Pipe NPS 2 (DN 50) and Smaller:

Retain "Bronze Valves" Subparagraph below if solder-joint valve ends are permitted for this application.

          - Bronze Valves: May be provided with solder-joint [or press ]ends instead of threaded ends.

          - Bronze swing check valves with [bronze] [nonmetallic] disc, [Class 125] [Class 150].

        - Pipe NPS 2-1/2 (DN 65) and Larger:

Retain first subparagraph below if threaded valve ends are permitted for this application.

          - NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Iron valves may be provided with threaded ends instead of flanged ends.

Retain one or more of seven subparagraphs below and indicate location of each type on Drawings.

          - NPS 2-1/2 to NPS 12 (DN 65 to DN 300): Iron swing check valves with lever and [spring] [weight]-closure control, Class 125.

          - NPS 3 to NPS 12 (DN 80 to DN 300): Iron, grooved-end swing check valves, 300 CWP.

          - NPS 2-1/2 to NPS 24 (DN 65 to DN 600): Iron, [compact-wafer] [globe], center-guided check valves with [metal] [resilient] seat, [Class 125] [Class 150] [Class 250] [Class 300].

          - Iron swing check valves with [metal] [nonmetallic-to-metal] seats, [Class 125] [Class 250].

          - Iron, single plate-check valves with resilient seat, [Class 125] [Class 250].

          - Iron, dual-plate-check valves with metal seat, [Class 125] [Class 150] [Class 250] [Class 300].

          - Iron, dual plate check valves with resilient seat, [Class 125] [Class 150] [Class 250] [Class 300].

Retain first or second paragraph below if CPVC and/or PVC pipe are specified for any piping applications in Section 232113 "Hydronic Piping."

        - CPVC Pipe [NPS 2 (DN 50)] [NPS 4 (DN 100)] and Smaller: CPVC ball check valve.

        - PVC Pipe [NPS 2 (DN 50)] [NPS 4 (DN 100)] and Smaller: PVC ball check valve.

      - HEATING-WATER VALVE SCHEDULE

        - Pipe NPS 2 (DN 50) and Smaller:

Retain "Bronze Valves" Subparagraph below if solder-joint valve ends are permitted for this application.

          - Bronze Valves: May be provided with solder-joint [or press ]ends instead of threaded ends.

          - Bronze swing check valves with [bronze] [nonmetallic] disc, [Class 125] [Class 150].

        - Pipe NPS 2-1/2 (DN 65) and Larger:

Retain first subparagraph below if threaded valve ends are permitted for this application.

          - NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Iron valves may be provided with threaded ends instead of flanged ends.

Retain one or more of seven subparagraphs below and indicate location of each type on Drawings.

          - NPS 2-1/2 to NPS 12 (DN 65 to DN 300): Iron swing check valves with lever and [spring] [weight]-closure control, Class 125.

          - NPS 3 to NPS 12 (DN 80 to DN 300): Iron, grooved-end check valves, 300 CWP.

          - Iron swing check valves with [metal] [nonmetallic-to-metal] seats, [Class 125] [Class 250].

          - Iron, [compact-wafer] [globe], center-guided check valves with [metal] [resilient] seat, [Class 125] [Class 150] [Class 250] [Class 300].

          - Iron, single-plate check valves with resilient seat, [Class 125] [Class 250].

          - Iron, dual-plate check valves with metal seat, [Class 125] [Class 150] [Class 250] [Class 300].

          - Iron, dual-plate check valves with resilient seat, [Class 125] [Class 150] [Class 250] [Class 300].

Retain first or second paragraph below if CPVC and/or PVC pipe are specified for any piping applications in Section 232113 "Hydronic Piping."

        - CPVC Pipe [NPS 2 (DN 50)] [NPS 4 (DN 100)] and Smaller: CPVC ball check valve.

        - PVC Pipe [NPS 2 (DN 50)] [NPS 4 (DN 100)] and Smaller: PVC ball check valve.

      - LOW-PRESSURE STEAM VALVE SCHEDULE - 15 PSIG (104 kPa) OR LESS

        - Pipe NPS 2 (DN 50) and Smaller:

          - Bronze swing check valves with [bronze] [nonmetallic] disc, [Class 125] [Class 150].

        - Pipe NPS 2-1/2 (DN 65) and Larger:

Retain first subparagraph below if threaded valve ends are permitted for this application.

          - NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Iron valves may be provided with threaded ends instead of flanged ends.

Retain one or both subparagraphs below and indicate location of each type on Drawings.

          - Iron swing check valves with [metal] [nonmetallic-to-metal] seats; [Class 125] [Class 250].

          - NPS 2-1/2 to NPS 12 (DN 65 to DN 300): Iron swing check valves with lever and [spring] [weight]-closure control, Class 125.

      - HIGH-PRESSURE STEAM VALVE SCHEDULE - MORE THAN 15 PSIG (104 kPa)

        - Pipe NPS 2 (DN 50) and Smaller:

          - Bronze swing check valves with [bronze] [nonmetallic] disc, [Class 125] [Class 150].

        - Pipe NPS 2-1/2 (DN 65) and Larger:

Retain first subparagraph below if threaded valve ends are permitted for this application.

          - Iron Valves, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): May be provided with threaded ends instead of flanged ends.

Retain one or both subparagraphs below and indicate location of each type on Drawings.

          - Iron swing check valves with [metal] [nonmetallic-to-metal] seats, [Class 125] [Class 250].

          - NPS 2-1/2 to NPS 12 (DN 65 to DN 300): Iron swing check valves with lever and [spring] [weight]-closure control, Class 125.

      - STEAM-CONDENSATE VALVE SCHEDULE

        - Pipe NPS 2 (DN 50) and Smaller:

          - Bronze swing check valves with [bronze] [nonmetallic] disc, [Class 125] [Class 150].

        - Pipe NPS 2-1/2 (DN 65) and Larger:

Retain first subparagraph below if threaded valve ends are permitted for this application.

          - NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Iron valves may be provided with threaded ends instead of flanged ends.

Retain one or both subparagraphs below and indicate location of each type on Drawings.

          - Iron swing check valves with [metal] [nonmetallic-to-metal] seats, [Class 125] [Class 250].

          - Iron swing check valves with lever and [spring] [weight]-closure control, Class 125.

END OF SECTION 230523.14