Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 230523.15 - GATE VALVES FOR HVAC PIPING

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Access Manufacturer-Provided, AIA MasterSpec-Based Sections:

<Double click here for this Section based on specific manufacturer’s products set as Basis-of-Design at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Bronze gate valves.

          - Iron gate valves.

          - Plastic gate valves.

          - Chainwheels.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - CWP: Cold working pressure.

        - NRS: Nonrising stem.

        - OS&Y: Outside screw and yoke.

        - RS: Rising stem.

        - SWP: Steam working pressure.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data: For each type of valve.

      - DELIVERY, STORAGE, AND HANDLING

Information in this article is paraphrased from MSS publications.

        - Prepare valves for shipping as follows:

          - Protect internal parts against rust and corrosion.

          - Protect threads, flange faces, grooves, press connections, and weld ends.

          - Set gate valves closed to prevent rattling.

        - Use the following precautions during storage:

          - Maintain valve end protection.

          - Store valves indoors and maintain at higher-than-ambient-dew-point temperature. If outdoor storage is necessary, store valves off the ground in watertight enclosures.

        - Use sling to handle large valves; rig sling to avoid damage to exposed parts. Do not use handwheels, stems, or other components as lifting or rigging points unless specifically indicated for this purpose in manufacturer's written instructions.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - SOURCE LIMITATIONS

        - Obtain each type of valve from single source from single manufacturer.

      - PERFORMANCE REQUIREMENTS

        - ASME Compliance:

          - ASME B1.20.1 for threads for threaded-end valves.

          - ASME B16.1 for flanges on iron valves.

          - ASME B16.5 for flanges on metric standard piping.

          - ASME B16.10 and ASME B16.34 for ferrous valve dimensions and design criteria.

Valve solder-joint connections are common in smaller sizes of HVAC piping. Soldering and brazing methods used to achieve required pressure and temperature ratings may damage internal valve parts. Special installation requirements for soldered valves may make threaded valves more cost-effective.

          - ASME B16.18 for cast copper solder joint.

          - ASME B16.22 for wrought copper solder joint.

          - ASME B16.34 for flanged, threaded, and welding ends.

          - ASME B16.51 for press joint.

          - ASME B31.1 for power piping valves.

          - ASME B31.9 for building services piping valves.

        - AWWA Compliance: Comply with AWWA C606 for grooved-end connections.

        - Provide bronze valves made with dezincification-resistant materials. Bronze valves made with copper alloy (brass) containing more than 15 percent zinc are unacceptable.

Caution: Revise pressure ratings and insert temperature ratings in valve articles if valves with higher ratings are required. Valves larger than NPS 12 (DN 300) typically have a lower pressure rating than smaller valves. Verify pressure requirements for large valves.

        - Valve Pressure-Temperature Ratings: Not less than indicated and as required for system pressures and temperatures.

        - Valve Sizes: Same as upstream piping unless otherwise indicated.

        - RS Valves in Insulated Piping: With 2-inch (50-mm) stem extensions.

        - Valve Bypass and Drain Connections: MSS SP-45.

      - BRONZE GATE VALVES

Retain one or more of five paragraphs in this article if bronze gate valves are required. MSS SP-80 covers bronze gate valves from NPS 1/4 to NPS 3 (DN 8 to DN 80).

        - Bronze Gate Valves, NRS, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-80, Type 1.

            - CWP Rating: 200 psig (1380 kPa).

            - Body Material: ASTM B62, bronze with integral seat and screw-in bonnet.

            - Ends: Threaded[ or solder joint].

            - Stem: Bronze.

            - Disc: Solid wedge; bronze.

            - Packing: Asbestos free.

            - Handwheel: Malleable iron[, bronze, or aluminum].

        - Bronze Gate Valves, RS, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-80, Type 2.

            - CWP Rating: 200 psig (1380 kPa).

            - Body Material: ASTM B62, bronze with integral seat and screw-in bonnet.

            - Ends: Threaded[ or solder joint].

            - Stem: Bronze.

            - Disc: Solid wedge; bronze.

            - Packing: Asbestos free.

            - Handwheel: Malleable iron, bronze, or aluminum.

        - Bronze Gate Valves, NRS, Class 150:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-80, Type 1.

            - CWP Rating: 300 psig (2070 kPa).

            - Body Material: ASTM B62, bronze with integral seat and union-ring bonnet.

            - Ends: Threaded.

            - Stem: Bronze.

            - Disc: Solid wedge; bronze.

            - Packing: Asbestos free.

            - Handwheel: Malleable iron, bronze, or aluminum.

        - Bronze Gate Valves, RS, Class 150:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-80, Type 2.

            - CWP Rating: 300 psig (2070 kPa).

            - Body Material: ASTM B62, bronze with integral seat and union-ring bonnet.

            - Ends: Threaded.

            - Stem: Bronze.

            - Disc: Solid wedge; bronze.

            - Packing: Asbestos free.

            - Handwheel: Malleable iron[, bronze, or aluminum].

        - Bronze Gate Valves, Press Ends:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-80.

            - CWP Rating: Minimum 200 psig (1380 kPa).

            - Body Material: Bronze with integral seat and union-ring bonnet.

            - Ends: Press.

            - Press Ends Connection Rating: Minimum 200 psig (1380 kPa).

            - Stem: Brass or bronze [RS] [NRS].

            - Disc: Solid wedge; bronze.

            - Packing: Graphite.

            - Port: Full.

            - Handwheel: Malleable iron, bronze, or aluminum.

      - IRON GATE VALVES

Retain one or more of four paragraphs in this article if iron gate valves are required. MSS SP-70 covers iron gate valves from NPS 2 to NPS 48 (DN 50 to DN 1200).

        - Iron Gate Valves, NRS, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-70, Type I.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 200 psig (1380 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 150 psig (1035 kPa).

            - Body Material: ASTM A126, gray iron with bolted bonnet.

            - Ends: Flanged.

            - Trim: Bronze.

            - Disc: Solid wedge.

            - Packing and Gasket: Asbestos free.

        - Iron Gate Valves, OS&Y, Class 125:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-70, Type I.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 200 psig (1380 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 150 psig (1035 kPa).

            - Body Material: ASTM A126, gray iron with bolted bonnet.

            - Ends: Flanged.

            - Trim: Bronze.

            - Disc: Solid wedge.

            - Packing and Gasket: Asbestos free.

        - Iron Gate Valves, NRS, Class 250:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-70, Type I.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 500 psig (3450 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 300 psig (2070 kPa).

            - Body Material: ASTM A126, gray iron with bolted bonnet.

            - Ends: Flanged.

            - Trim: Bronze.

            - Disc: Solid wedge.

            - Packing and Gasket: Asbestos free.

        - Iron Gate Valves, OS&Y, Class 250:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Standard: MSS SP-70, Type I.

            - NPS 2-1/2 to NPS 12 (DN 65 to DN 300), CWP Rating: 500 psig (3450 kPa).

            - NPS 14 to NPS 24 (DN 350 to DN 600), CWP Rating: 300 psig (2070 kPa).

            - Body Material: ASTM A126, gray iron with bolted bonnet.

            - Ends: Flanged.

            - Trim: Bronze.

            - Disc: Solid wedge.

            - Packing and Gasket: Asbestos free.

      - PLASTIC GATE VALVES

        - CPVC Gate Valves:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Pressure Rating and Temperature: [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert value> at [73 deg F (23 deg C)] <Insert temperature>.

            - Body Material: CPVC.

            - Body Design: Nonrising stem.

            - End Connections for Valves NPS 2 (DN 50) and Smaller: [Socket] [or] [threaded].

            - End Connections for Valves NPS 2-1/2 to NPS 4 (DN 65 to DN 100): [Socket] [Socket or threaded] [Threaded] [Flanged].

            - Gate and Stem: Plastic.

            - Seals: EPDM rubber.

            - Handle: Wheel.

        - PVC Gate Valves:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - Pressure Rating and Temperature: [125 psig (860 kPa)] [150 psig (1035 kPa)] <Insert value> at [73 deg F (23 deg C)] <Insert temperature>.

            - Body Material: PVC.

            - Body Design: Nonrising stem.

            - End Connections for Valves NPS 2 (DN 50) and Smaller: [Socket] [or] [threaded].

            - End Connections for Valves NPS 2-1/2 to NPS 4 (DN 65 to DN 100): [Socket] [Socket or threaded] [Threaded] [Flanged].

            - Gate and Stem: Plastic.

            - Seals: EPDM rubber.

            - Handle: Wheel.

      - CHAINWHEELS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain option in "Description" Paragraph below if chainwheel does not mount directly to the valve stem or gearbox shaft.

        - Description: Valve actuation assembly with sprocket rim, chain guides, chain[, and attachment brackets for mounting chainwheels directly to handwheels].

In "Sprocket Rim with Chain Guides" Subparagraph below, consider specifying aluminum or the zinc or epoxy coatings for corrosive operating conditions. Bronze should be specified for severe operating conditions. See the Evaluations.

          - Sprocket Rim with Chain Guides: [Ductile iron] [Ductile or cast iron] [Cast iron] [Aluminum] [Bronze], of type and size required for valve.[ Include zinc or epoxy coating.]

In "Chain" Subparagraph below, retain chain material appropriate for chosen sprocket rim material.

          - Chain: [Hot-dip galvanized steel] [Brass] [Stainless steel], of size required to fit sprocket rim.

- EXECUTION

      - EXAMINATION

        - Examine valve interior for cleanliness, freedom from foreign matter, and corrosion. Remove special packing materials, such as blocks, used to prevent disc movement during shipping and handling.

        - Operate valves in positions from fully open to fully closed. Examine guides and seats made accessible by such operations.

        - Examine threads on valve and mating pipe for form and cleanliness.

        - Examine mating flange faces for conditions that might cause leakage. Check bolting for proper size, length, and material. Verify that gasket is of proper size, that its material composition is suitable for service, and that it is free from defects and damage.

        - Examine press joint surfaces. Verify that they are clean and free from dents and burrs and that O-ring seals are in place and undamaged.

        - Do not attempt to repair defective valves; replace with new valves.

      - INSTALLATION OF VALVES

        - Install valves with unions or flanges at each piece of equipment arranged to allow service, maintenance, and equipment removal without system shutdown.

        - Provide support of piping adjacent to valves such that no force is imposed upon valves.

        - Locate valves for easy access and where not blocked by equipment, other piping, or building components.

        - Install valves so that stems are horizontal or slope upward from centerline of pipe.

        - Install valves in position that does not project into aisles or block access to other equipment.

        - Install valves in position to allow full stem and manual operator movement.

        - Verify that joints of each valve have been properly installed and sealed to ensure that there is no leakage or damage.

        - Install chainwheels on manual operators for gate valves [NPS 4 (DN 100)] <Insert pipe size> and larger and more than [96 inches (2400 mm)] <Insert dimension> above floor. Extend chains to [60 inches (1520 mm)] <Insert dimension> above finished floor.

        - Install valve tags. Comply with requirements in Section 230553 "Identification for HVAC Piping and Equipment" for valve tags and schedules.

        - Adhere to manufacturer's written installation instructions. When soldering or brazing valves, do not heat valves above maximum permitted temperature. Do not use solder with melting point temperature above valve of manufacturer's recommended maximum.

      - ADJUSTING

        - Adjust or replace valve packing after piping systems have been tested and put into service, but before final adjusting and balancing. Replace valves if persistent leaking occurs.

      - GENERAL REQUIREMENTS FOR VALVE APPLICATIONS

The Section Text is arranged to provide bronze or brass valves in NPS 2 (DN 50) and smaller and iron valves from NPS 2-1/2 to NPS 24 (DN 65 to DN 600).

Caution: Verify that valve classes and pressure and temperature ratings are adequate for system fluid. Repeat each category listing if necessary and indicate each required pressure-temperature range and its location on Drawings.

Retain and revise valve applications in this article. Coordinate with valves specified in Part 2.

        - If valve applications are not indicated, use the following:

          - Shutoff Service: Gate valves.

        - If valves with specified SWP classes or CWP ratings are unavailable, the same types of valves with higher SWP classes or CWP ratings may be substituted.

        - Select valves, except wafer types, with the following end connections:

          - For Copper Tubing, NPS 2 (DN 50) and Smaller: Threaded ends, except where solder-joint or press valve-end option is indicated in valve schedules.

          - For Copper Tubing, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Flanged ends, except where threaded valve-end option is indicated in valve schedules.

          - For Copper Tubing, NPS 5 (DN 125) and Larger: Flanged ends.

          - For Steel Piping, NPS 2 (DN 50) and Smaller: Threaded ends.

          - For Steel Piping, NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Flanged ends, except where threaded valve-end option is indicated in valve schedules.

          - For Steel Piping, NPS 5 (DN 125) and Larger: Flanged ends.

          - For Grooved-End [Copper Tubing] [and] [Steel Piping], except for Steam and Steam Condensate Piping: Valve ends may be grooved.

      - CHILLED-WATER VALVE SCHEDULE

        - Pipe NPS 2 (DN 50) and Smaller: Bronze valves, [NRS] [RS], [Class 125] [Class 150], with [soldered] [threaded] [press] ends.

        - Pipe NPS 2-1/2 (DN 65) and Larger: Iron gate valves, [NRS] [OS&Y], [Class 125] [Class 250].

Retain first or second paragraph below if CPVC and/or PVC pipe is specified for any piping applications in Section 232113 "Hydronic Piping."

        - CPVC Pipe [NPS 2 (DN 50)] [NPS 4 (DN 100)] and Smaller: CPVC gate valve.

        - PVC Pipe [NPS 2 (DN 50)] [NPS 4 (DN 100)] and Smaller: PVC gate valve.

      - CONDENSER-WATER VALVE SCHEDULE

        - Pipe NPS 2 (DN 50) and Smaller: Bronze valves, [NRS] [RS], [Class 125] [Class 150], with [soldered] [threaded] [press] ends.

        - Pipe NPS 2-1/2 (DN 65) and Larger: Iron gate valves, [NRS] [OS&Y], [Class 125] [Class 250].

Retain first or second paragraph below if CPVC and/or PVC pipe is specified for any piping applications in Section 232113 "Hydronic Piping."

        - CPVC Pipe [NPS 2 (DN 50)] [NPS 4 (DN 100)] and Smaller: CPVC gate valve.

        - PVC Pipe [NPS 2 (DN 50)] [NPS 4 (DN 100)] and Smaller: PVC gate valve.

      - HEATING-WATER VALVE SCHEDULE

        - Pipe NPS 2 (DN 50) and Smaller: Bronze valves, [NRS] [RS], [Class 125] [Class 150] with [soldered] [threaded] [press] ends.

        - Pipe NPS 2-1/2 (DN 65) and Larger: Iron gate valves, [NRS] [OS&Y], [Class 125] [Class 250].

Retain first or second paragraph below if CPVC and/or PVC pipe is specified for any piping applications in Section 232113 "Hydronic Piping."

        - CPVC Pipe [NPS 2 (DN 50)] [NPS 4 (DN 100)] and Smaller: CPVC gate valve.

        - PVC Pipe [NPS 2 (DN 50)] [NPS 4 (DN 100)] and Smaller: PVC gate valve.

      - LOW-PRESSURE STEAM VALVE SCHEDULE - 15 PSIG (104 kPa) OR LESS

        - Pipe NPS 2 (DN 50) and Smaller: Bronze gate valves, [NRS] [RS], [Class 125] [Class 150].

        - Pipe NPS 2-1/2 (DN 65) and Larger: Iron gate valves, [NRS] [OS&Y], [Class 125] [Class 250].

      - HIGH-PRESSURE STEAM VALVE SCHEDULE - MORE THAN 15 PSIG (104 kPa)

        - Pipe NPS 2 (DN 50) and Smaller: Bronze gate valves, [NRS] [RS], [Class 125] [Class 150].

        - Pipe NPS 2-1/2 (DN 65) and Larger: Iron gate valves, [NRS] [OS&Y], [Class 125] [Class 250].

      - STEAM-CONDENSATE VALVE SCHEDULE

        - Pipe NPS 2 (DN 50) and Smaller: Bronze gate valves, [NRS] [RS], [Class 125] [Class 150].

        - Pipe NPS 2-1/2 (DN 65) and Larger: Iron gate valves, [NRS] [OS&Y], [Class 125] [Class 250].

END OF SECTION 230523.15