Copyright 2019 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 230800 - COMMISSIONING OF HVAC

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

See "Sustainable Design Considerations" Article in the Evaluations for a discussion of sustainable design requirements that may impact editing of this Section.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and other Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section includes Cx process requirements for the following HVAC systems, assemblies, and equipment:

Retain or add systems below that are to be commissioned. Coordinate subparagraphs below with retained "Construction Checklists" Article under Part 3.

          - Energy supply systems.

          - Heat generation systems.

          - Cooling generation systems.

          - Central-station air-handling systems.

          - Air, steam, and hydronic distribution systems.

          - Heating and cooling terminal and unitary equipment.

          - HVAC controls.

          - TAB verification.

          - <Insert additional systems>.

        - Related Requirements:

Retain first subparagraph below because it contains the general Cx process requirements that apply to Cx of HVAC systems. If the work covered under Section 019113 "General Commissioning Requirements" is not to be performed by an independent contractor, it must be included under this or other sections of the Specification. Modify the Specifications where necessary.

          - Section 019113 "General Commissioning Requirements" for general Cx process requirements and CxA responsibilities.

          - For construction checklists, comply with requirements in various Division 23 Sections specifying HVAC systems, system components, equipment, and products.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

        - BAS: Building automation system.

        - Cx: Commissioning, as defined in Section 019113 "General Commissioning Requirements."

        - CxA: Commissioning Authority, as defined in Section 019113 "General Commissioning Requirements."

        - IgCC: International Green Construction Code.

        - "Systems," "Assemblies," "Subsystems," "Equipment," and "Components": Where these terms are used together or separately, they mean "as-built" systems, assemblies, subsystems, equipment, and components.

        - TAB: Testing, adjusting, and balancing.

      - INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Data: For [BAS] [and] [HVAC] testing technician.

        - Construction Checklists:

Retain one of two subparagraphs below. Retain first subparagraph for projects in which an independent CxA creates construction checklists. Retain second subparagraph for projects in which Contractor creates and submits construction checklists. Note that in order to conform to IgCC requirements, checklists must be prepared by the CxA who must be designated by the Owner to manage the Cx process. CxA must have the necessary training, experience, and equipment and be independent from the design team and the Contractor.

          - Draft Cx plan, including draft construction checklists to be prepared by CxA under Section 019113 "General Commissioning Requirements." Div. 23 Subcontractor is to review Construction Checklist in accordance with requirements in Section 019113 "General Commissioning Requirements" and ASHRAE 202 and to resolve any issues with the CxA.

          - Cx plan, including material, installation, and performance construction checklists for systems, assemblies, subsystems, equipment, and components relating to [BAS] [and] [HVAC] to be part of the Cx process and in accordance with requirements in Section 019113 "General Commissioning Requirements and ASHRAE 202."

Retain "Test Equipment and Instruments" Paragraph below if contractor is to provide test equipment.

        - Test Equipment and Instruments: For all test equipment and instruments to be used in conducting Cx tests by Div. 23 Subcontractor, provide the following:

          - Equipment/instrument identification number.

          - Planned Cx application or use.

          - Manufacturer, make, model, and serial number.

          - Calibration history, including certificates from agencies that calibrate the equipment and instrumentation.

          - Equipment manufacturers' proprietary instrumentation and tools. For each instrument or tool, identify the following:

            - Instrument or tool identification number.

            - Equipment schedule designation of equipment for which the instrument or tool is required.

            - Manufacturer, make, model, and serial number.

            - Calibration history, including certificates from agencies that calibrate the instrument or tool, where appropriate.

      - QUALITY ASSURANCE

        - BAS Testing Technician Qualifications: Technicians performing BAS Construction Checklist verification tests, Construction Checklist verification test demonstrations, Cx tests, and Cx test demonstrations are to have the following minimum qualifications:

          - Journey level or equivalent skill level with knowledge of BAS, HVAC, electrical concepts, and building operations.

          - Minimum [three years'] <Insert time> experience installing, servicing, and operating systems manufactured by approved manufacturer.

          - International Society of Automation (ISA)-Certified Control Systems Technician (CCST) Level I.

        - HVAC Testing Technician Qualifications: Technicians to perform HVAC Construction Checklist verification tests, Construction Checklist verification test demonstrations, Cx tests, and Cx test demonstrations shall have the following minimum qualifications:

          - Journey level or equivalent skill level; vocational school four-year-program graduate or an Associate's degree in mechanical systems, air conditioning, or similar field. Degree may be offset by three years' experience in servicing mechanical systems in the HVAC industry. Generally, required knowledge includes HVAC systems, electrical concepts, building operations, and application and use of tools and instrumentation to measure performance of HVAC equipment, assemblies, and systems.

          - Minimum [three years'] <Insert time> experience that is to include installing, servicing, and operating systems manufactured by approved manufacturer.

        - Testing Equipment and Instrumentation Quality and Calibration:

          - Capable of testing and measuring performance within the specified acceptance criteria.

          - Be calibrated at manufacturer's recommended intervals with current calibration tags permanently affixed to the instrument being used.

          - Be maintained in good repair and operating condition throughout duration of use on Project.

          - Be recalibrated/repaired if dropped or damaged in any way since last calibrated.

        - Proprietary Test Instrumentation and Tools:

          - Equipment Manufacturer's Proprietary Instrumentation and Tools: For installed equipment included in the Cx process, test instrumentation and tools manufactured or prescribed by equipment manufacturer to service, calibrate, adjust, repair, or otherwise work on its equipment or required as a condition of equipment warranty, shall comply with the following:

            - Be calibrated by manufacturer with current calibration tags permanently affixed.

            - Include a separate list of proprietary test instrumentation and tools in operation and maintenance manuals.

          - HVAC proprietary test instrumentation and tools become property of Owner at the time of Substantial Completion.

- PRODUCTS (Not Used)

- EXECUTION

      - Cx PROCESS:

        - Perform Cx process in accordance with Section 019113 "General Commissioning Requirements" for [BAS] [and] [HVAC] and in accordance with the following:

Retain first subparagraph below if IgCC applies to Project. IgCC requires compliance with ASHRAE 202.

          - [IgCC, which requires compliance with ASHRAE 202].

          - [ASHRAE 202].

          - [Commissioning standards acceptable to the authority having jurisdiction].

          - <Insert standard>.

      - CONSTRUCTION CHECKLISTS

Retain first paragraph below if construction checklists are to be prepared under Section 019113 "General Commissioning Requirements." Coordinate with "Construction Checklists" Paragraph in Informational Submittals Article.

        - Preliminary detailed construction checklists are to be prepared under Section 019113 "General Commissioning Requirements" for each [BAS] [and] [HVAC] system, assembly, subsystem, equipment, and component required to be commissioned, as detailed in [IgCC and] ASHRAE 202. Contractor performs the following:

          - Review [BAS] [and] [HVAC] preliminary construction checklists and provide written comments on checklist items where appropriate.

          - Return preliminary Construction Checklist with review comments within [10] <Insert number> days of receipt.

          - When review comments have been resolved, the CxA will provide final construction checklists marked "Approved for Use, (date)."

          - Use only construction checklists marked "Approved for Use, (date)" When performing tests. Mark construction checklists in the appropriate place as indicated Project events are completed, and provide pertinent details and other information.

Retain first paragraph below if construction checklists are to be prepared by the Contractor. Coordinate with "Construction Checklists" Paragraph in "Informational Submittals" Article.

        - Prepare preliminary detailed construction checklists for each [BAS] [and] [HVAC] system, assembly, subsystem, equipment, and component required to be commissioned, as detailed in [IgCC and ASHRAE 202] [ASHRAE 202].

          - Submit preliminary construction checklists to CxA and Designer for review.

          - When review comments have been resolved, the CxA will provide final construction checklists marked "Approved for Use, (date)."

          - Use only construction checklists, marked "Approved for Use, (date)" when performing tests. Mark construction checklists in the appropriate place, as indicated Project events are completed and provide pertinent details and other information.

On projects subject to IgCC, the following BAS and HVAC systems must be commissioned as a minimum. Delete systems not applicable to Project. Add system as required for the Project. On projects not subject to IgCC, paragraphs below may be modified as required to suit Project.

        - Systems required to be commissioned under IgCC:

          - Heating, ventilating, air-conditioning, and refrigeration systems (mechanical and/or passive) and associated controls.

          - Air-curtain systems.

          - Water-pumping and -mixing systems over 5 hp (4 kW) and purification systems.

          - Renewable energy systems and energy storage systems.

          - Energy and building management and demand-control systems.

        - Additional systems required to be commissioned:

Additional systems may be commissioned as required. Revise subparagraphs below to indicate Cx requirements on this Project.

          - Energy supply systems, including the following:

            - Fuel-oil supply.

            - Fuel gas supply.

            - Central-plant steam supply.

            - Central-plant hot-water supply.

            - Solar-energy supply.

            - Renewable energy systems.

            - Energy storage systems.

            - Demand-control systems.

            - <Insert supply sources>.

          - Heat generation systems, including the following:

            - Boilers.

            - Furnaces.

            - Fuel-fired unit heaters.

            - Auxiliary equipment.

            - <Insert equipment>.

          - Cooling generation systems, including the following:

            - Water chillers.

            - Cooling towers.

            - Direct-expansion refrigeration systems.

            - <Insert systems>.

          - Air-handling systems, including the following:

            - Supply, return, and exhaust air fans, motors, and drives.

            - Automatic and gravity dampers.

            - Heating and cooling devices.

            - Humidification and dehumidification devices.

            - Air filters.

            - Hangers and supports.

            - Interlock between air-handling system and fire/smoke alarm system.

            - <Insert components>.

          - Air duct systems, including the following:

            - Duct systems.

            - Air-duct accessories, including volume dampers, fire and smoke dampers, turning vanes, sound attenuators, and flexible connectors.

            - Duct-mounted access doors and panels.

            - Hangers and supports.

            - <Insert components>.

          - Air curtain systems.

            - Supply air fans and motors.

            - Heating and cooling devices.

            - <Insert components>.

          - Steam and hydronic distribution systems, including the following:

            - Steam distribution piping systems.

            - Condensate piping systems, including condensate pumps and all accessories.

            - Hydronic piping systems and all accessories.

            - Pumps and all accessories.

            - Sleeves and sleeve seals.

            - Meters and gauges.

            - General-duty and specialty valves.

            - Hangers and supports

            - Heat tracing.

            - <Insert systems>.

          - Refrigerant piping, including the following:

            - Refrigerant piping, fittings, and specialties.

            - Refrigerant charge.

            - Sleeves and sleeve seals.

            - Meters and gauges.

            - General-duty and specialty valves.

            - Hangers and supports.

            - <Insert components>.

          - Smoke-control systems, including the following:

            - Exhaust and makeup fans, motors, and drives.

            - Exhaust and makeup air distribution systems.

            - Smoke dampers.

            - Smoke detectors.

            - Fire and smoke alarm system interface.

            - <Insert system>.

          - Heating and cooling terminal and unitary equipment, including the following:

            - Unit ventilators.

            - Unit heaters.

            - Fan-coil units.

            - Finned-tube radiation.

            - Electric heating.

            - Unitary heating and cooling equipment.

            - <Insert units>.

          - Vibration isolation systems.

          - Controls and instrumentation, including the following:

            - Energy monitoring and recording system.

            - Controllers and sensors.

            - Automatic control valves, dampers, and actuators.

            - Control interface with fans, pumps, dampers, and other equipment and systems.

            - Demand-control systems.

            - <Insert systems>.

          - TAB Verification:

            - Airflow.

            - Water flow.

            - Space pressurization.

          - Documentation:

            - Mechanical systems manuals.

            - Documentation of required commissioning.

          - Mechanical insulation, including the following:

            - Duct and plenum insulation.

            - HVAC piping insulation.

          - <Insert additional systems>.

      - Cx TESTING PREPARATION

        - Certify that HVAC systems, subsystems, and equipment have been installed, calibrated, and started and that they are operating in accordance with the Contract Documents and approved submittals.

        - Certify that HVAC instrumentation and control systems have been completed and calibrated, point-to-point checkout has been successfully completed, and systems are operating in accordance with their design sequence of operation, Contract Documents, and approved submittals. Certify that all sensors are operating within specified accuracy and all systems are set to and maintaining set points as required by the design documents.

        - Certify that TAB procedures have been completed and that TAB reports have been submitted, discrepancies corrected, and corrective work approved.

        - Set systems, subsystems, and equipment into operating mode to be tested in accordance with approved test procedures (e.g., normal shutdown, normal auto position, normal manual position, unoccupied cycle, emergency power, and alarm conditions).

      - Cx TEST CONDITIONS

        - Perform tests using design conditions, whenever possible.

          - Simulated conditions may, with approval of Architect, be imposed using an artificial load when it is impractical to test under design conditions. Before simulating conditions, calibrate testing instruments. Provide equipment to simulate loads. Set simulated conditions as directed by CxA, and document simulated conditions and methods of simulation. After tests, return configurations and settings to normal operating conditions.

          - Cx test procedures may direct that set points be altered when simulating conditions is impractical.

          - Cx test procedures may direct that sensor values be altered with a signal generator when design or simulating conditions and altering set points are impractical.

        - If tests cannot be completed because of a deficiency outside the scope of the HVAC system, document the deficiency and report it to Architect. After deficiencies are resolved, reschedule tests.

        - If seasonal testing is specified, complete appropriate initial performance tests and documentation, and schedule seasonal tests.

      - Cx TESTS COMMON TO HVAC SYSTEMS

        - Measure capacities and effectiveness of systems, assemblies, subsystems, equipment, and components, including operational and control functions, to verify compliance with acceptance criteria.

        - Test systems, assemblies, subsystems, equipment, and components for operating modes, interlocks, control responses, responses to abnormal or emergency conditions, and response in accordance with acceptance criteria.

        - Coordinate schedule with, and perform Cx activities at the direction of, CxA.

        - Comply with Construction Checklist requirements, including material verification, installation checks, startup, and performance test requirements specified in Division 23 Sections specifying HVAC systems and equipment.

        - Provide technicians, instrumentation, tools, and equipment to perform and document the following:

          - Cx Construction Checklist verification tests.

          - Cx Construction Checklist verification test demonstrations.

      - CONSTRUCTION CHECKLIST EXAMPLES

Specific test procedures are to be developed by the CxA or Contractor. The paragraphs below represent a potential outline of procedures for certain typical systems and are provided as examples. Revise as required.

        - Vibration Isolation in HVAC Systems:

          - Prerequisites: Acceptance of results of construction checklists for vibration[ and seismic] control devices specified in [Section 230548 "Vibration and Seismic Controls for HVAC Piping and Equipment"] [Section 230548.13 "Vibration Controls for HVAC Piping and Equipment"].

          - Components to Be Tested:

            - Vibration isolation control devices in HVAC systems.

            - Support systems.

          - Test Purpose: Evaluate effectiveness of vibration isolation control devices.

Retain one of first two subparagraphs below. Retain first subparagraph if isolated equipment operates at constant speed; retain second if equipment operates at variable speed.

          - Test Conditions, Constant Speed Equipment: Measure vibration of the facility structure at [three] <Insert number> locations designated by Owner's witness while the isolated equipment operates.

          - Test Conditions, Variable Speed Equipment: Measure vibration of the facility structure at [three] <Insert number> locations designated by Owner's witness at the following operating conditions:

            - Maximum speed.

            - Minimum speed.

            - Critical speed.

          - Acceptance Criteria: Structure-borne vibration not to exceed specified performance.

        - Heat Tracing in HVAC Systems:

          - Prerequisites: Acceptance of results of construction checklists for heat tracing specified in HVAC systems. Comply with requirements listed in Section 230533 "Heat Tracing for HVAC Piping."

          - Equipment and Systems to Be Tested:

            - Self-regulating, parallel-resistance heating cables.

            - Heat tracing circuit controller.

          - Test Purpose:

            - Evaluate response to ambient temperature below freeze-protection set point.

            - Evaluate heating cable fault alarm.

          - Test Conditions:

            - Subject temperature sensor to temperature approximately [3 deg F (2 deg C)] <Insert value> above freeze-protection set point (initial set point [41 deg F (5 deg C)] <Insert value>). Monitor sensed temperature with a calibration-grade thermometer. Gradually change set point or sensed temperature until freeze-protection circuit is energized.

            - Subject temperature sensor to temperature approximately [3 deg F (2 deg C)] <Insert value> below freeze-protection set point (initial set point [41 deg F (5 deg C)] <Insert value>). Monitor sensed temperature with a calibration-grade thermometer. Gradually change set point or sensed temperature until freeze-protection circuit is de-energized.

            - Simulate an electrical fault on the heating cable.

          - Acceptance Criteria:

            - Freeze-protection circuit is energized at set-point temperature of minus 2 deg F (1 deg C).

            - Freeze-protection circuit is de-energized at set-point temperature of plus 2 deg F (1 deg C).

            - Heater trace circuit controller initiates an alarm of cable fault. Alarm is correctly reported at the alarm panel.

      - TAB VERIFICATION

        - Prerequisites: Completion of "Examination" Article requirements and correction of deficiencies, as specified in Section 230593 "Testing, Adjusting, and Balancing for HVAC."

        - Completion of "Preparation" Article requirements for preparation of a TAB plan that includes strategies and step-by-step procedures, and system-readiness checks and reports, as specified in Section 230593 "Testing, Adjusting, and Balancing for HVAC."

        - Scope: HVAC air systems and hydronic piping systems.

Final inspection requirements are detailed in "Inspections" Article in Section 230593 "Testing, Adjusting, and Balancing for HVAC." Coordinate "Purpose" Paragraph below with requirements in Section 230593 "Testing, Adjusting, and Balancing for HVAC."

        - Purpose: Differential flow relationships intended to maintain air and water pressurization differentials between the various areas of Project.

        - Conditions of the Test:

          - Cx Test Demonstration Sampling Rate: As specified in "Inspections" Article in Section 230593 "Testing, Adjusting, and Balancing for HVAC."

          - Systems operating in full heating mode[ with minimum outside-air volume].

          - Systems operating in full cooling mode[ with minimum outside-air volume].

          - For measurements at air-handling units with economizer controls; systems operating in economizer mode with 100 percent outside air.

        - Acceptance Criteria:

          - Under all conditions, rechecked measurements comply with "Inspections" Article in Section 230593 "Testing, Adjusting, and Balancing for HVAC."

          - Additionally, no rechecked measurement shall differ from measurements documented in the final report by more than the tolerances allowed.

          - Under all conditions, where the Contract Documents indicate a differential in airflow between supply and exhaust and/or return in a space, the differential relationship shall be maintained.

      - HEATING CONTROL SYSTEM Cx TESTS

        - Heating-Water Supply Temperature Control:

          - Prerequisites: Installation verification of the following:

            - Startup of [boiler] <Insert boiler designation> [steam to hot-water converter] <Insert converter designation> <Insert prime heating-water equipment>.

            - Startup of heating-water pump(s) <Insert pump designation(s)>.

            - TAB of heating-water flow and pressure.

            - Input Device: Heating-water supply temperature; [thermostat] [thermistor temperature sensor] [resistance temperature sensor] <Insert device designation>.

            - Output Device: Control valve <Insert device designation>.

            - Display the following at the operator's workstation:

              - Heating-water supply temperature.

              - Heating-water supply temperature set point.

              - Control-valve position.

          - Scope: Heating-water system.

          - Purpose: Control of heating-water supply temperature at input device <Insert device designation>.

          - Conditions of the Test:

            - Minimum heating-water flow.

            - Midrange Heating-Water Flow: [50 to 60] <Insert number(s)> percent of maximum.

            - Maximum heating-water flow.

          - Acceptance Criteria: Under all conditions, heating-water supply temperature is within plus or minus [2.0 deg F (1.1 deg C)] <Insert temperature> of set point.

        - Heating-Water Supply Temperature Reset:

          - Prerequisites: Installation verification of the following:

            - Startup of [boiler] <Insert boiler designation> [steam to hot-water converter] <Insert converter designation> <Insert prime heating-water equipment>.

            - Startup of heating-water pump(s) <Insert pump designation(s)>.

            - TAB of heating-water flow and pressure.

            - Input Device: Heating-water supply temperature; [thermostat] [thermistor temperature sensor] [resistance temperature sensor] <Insert device designation>.

            - Input Device: Outdoor-air temperature; [electric, outdoor-air-reset controller] [outdoor-air sensor].

            - Output Device: Control valve <Insert device designation>.

            - Display the following at the operator's workstation:

              - Outdoor-air temperature.

              - Heating-water supply temperature.

              - Heating-water supply temperature set point.

              - Control-valve position.

          - Scope: Heating-water system.

          - Purpose: Control of heating-water supply temperature at heating-water supply temperature input device <Insert device designation> in response to variable outdoor-air temperature input; [electric, outdoor-air-reset controller] [outdoor-air sensor] <Insert device designation>.

          - Conditions of the Test: Outdoor-air temperature input value may be overridden for this test.

            - Low Temperature: Outdoor-air temperature between [minus 30 and 0 deg F (minus 34 and minus 18 deg C)] <Insert temperature range>.

            - Midrange Temperature: Outdoor-air temperature between [30 and 45 deg F (minus 1 and plus 7 deg C)] <Insert temperature range>.

            - High Temperature: Outdoor-air temperature above [65 deg F (18 deg C)] <Insert temperature>.

          - Acceptance Criteria: Heating-water supply temperature resets in straight-line relationship with outdoor-air temperature for the following reset schedule. Under all conditions, heating-water supply temperature is within [2.0 deg F (1.1 deg C)] <Insert temperature> of set point.

            - [195 deg F (90 deg C)] <Insert temperature> heating water when outdoor-air temperature is [minus 30 deg F (minus 34 deg C)] <Insert temperature>.

            - [130 deg F (54 deg C)] <Insert temperature> heating water when outdoor-air temperature is [65 deg F (18 deg C)] <Insert temperature>.

            - Under all conditions, heating-water supply temperature is within plus or minus [2.0 deg F (1.1 deg C)] <Insert temperature> of set point.

        - Control Primary Circulating Pump(s):

          - Prerequisites: Installation verification of the following:

            - Startup of heating-water pump(s) <Insert pump designation(s)>.

            - Input Device: Outdoor-air temperature; [electric, outdoor-air-reset controller] [outdoor-air sensor] <Insert device designation>.

            - Output Device: Heating-water pump; [starter] [DDC system command to starter] <Insert device designation> relay.

            - Display the following at the operator's workstation:

              - Outdoor-air temperature.

              - Operating status of primary circulating pump(s).

          - Scope: Heating-water pump(s) <Insert pump designation(s)> and associated controls.

          - Purpose: On-off control of heating-water pump(s) in response to variable outdoor-air temperature input; [electric, outdoor-air-reset controller] [outdoor-air sensor] <Insert device designation>.

          - Conditions of the Test:

            - High Temperature: Outdoor-air temperature above [65 deg F (18 deg C)] <Insert temperature>.

            - Low Temperature: Outdoor-air temperature below [65 deg F (18 deg C)] <Insert temperature>.

          - Acceptance Criteria:

            - High Temperature: Pump(s) are off when outside-air temperature is above [65 deg F (18 deg C)] <Insert temperature>.

            - Low Temperature: Pump(s) are on when outside-air temperature is below [65 deg F (18 deg C)] <Insert temperature>.

      - CHILLER SYSTEM Cx TESTS

        - Start-and-Stop Condenser-Water Pump(s):

          - Prerequisites: Installation verification of the following:

            - Startup of condenser-water pump(s) <Insert pump designation(s)>.

            - Startup of cooling tower <Insert cooling tower designation>.

            - Input Device: Water pressure transducer <Insert device designation>.

            - Input Device: [Space thermostat] [DDC system outdoor-air temperature] <Insert device designation>.

            - Input Device: [Time clock] [DDC system time schedule] <Insert device designation>.

            - Output Device: Hard wired through motor starter; [DDC system binary output] <Insert device designation>.

            - Output Device: [Time clock] [Binary output] <Insert device designation>.

            - Display the following at the operator's workstation:

              - Low-level cooling-tower sump alarm.

              - Outdoor-air temperature.

              - Cooling (software) demand indication.

              - Time and time schedule.

              - Condenser-water pump(s) on-off status.

              - Condenser-water pump(s) on-off indication.

              - Condenser-water flow indication.

          - Scope:

            - Condenser-water system, including condenser-water pump(s), cooling towers, and associated controls.

          - Purpose:

            - Condenser-water pump(s) lockout.

            - Condenser-water pump(s) start.

            - Condenser-water pump(s) shutdown.

            - Low-level cooling-tower sump alarm.

            - Condenser-water pump(s) time-of-day schedule.

          - Conditions of the Test:

            - Verify Lockout: Start with condenser-water pump enable-input devices in the "disable" state to prevent pump start. One by one, place the enable-input devices in the "enable" state, and then return each to the "disable" state before placing the next enable-input device to the "enable" state.

            - Verify Start: Start with condenser-water pump enable-input devices in the "disable" state to prevent pump start. One by one, place the enable-input devices in the "enable" state.

            - Verify Shutdown: Place all enable-input devices in the "enable" state to allow the pump(s) to start. One by one, place the enable-input devices in the "disable" state, and then return each to the "enable" state before placing the next enable-input device to the "disable" state.

            - Verify Schedule: Compare condenser-water pump start-and-stop schedule times with Owner-approved time-of-day schedule.

          - Acceptance Criteria:

            - Lockout: No single enable-input device starts the pump(s) when released to the "enable" state.

            - Start: Condenser-water pump(s) start when, and only when, all enable-input devices are in the "enable" state.

            - Shutdown: Each enable-input device stops the condenser-water pump(s) when placed in the "disable" state, regardless of the state of other enable-input devices.

            - Schedule: Condenser-water pump start-and-stop schedule times agree with Owner-approved time-of-day schedule.

        - Start-and-Stop Chilled-Water Pump(s):

          - Prerequisites: Installation verification of the following:

            - Startup of chilled-water pump(s) <Insert pump designation(s)>.

            - Startup of condenser-water pump(s) <Insert pump designation(s)>.

            - Startup of cooling tower <Insert cooling tower designation>.

            - Input Device: Flow switch in condenser-water circuit <Insert device designation>.

            - Output Device: [Starter] [DDC system command to starter] <Insert device designation> relay.

            - Display one of the following at the operator's workstation:

              - Chilled-water flow indication.

              - Condenser-water flow indication.

              - Chilled-water pump(s) on-off status.

              - Chilled-water pump(s) on-off indication.

          - Scope: Chilled-water system, including chilled-water pump(s), associated controls, and condenser-water system controls.

          - Purpose:

            - Chilled-water pump(s) start.

            - Chilled-water pump(s) shutdown.

          - Conditions of the Test:

            - Verify Start: Start with chilled-water pump enable-input device in the "disable" state to prevent pump start. Place the enable-input device in the "enable" state.

            - Verify Shutdown: Start with the enable-input device in the "enable" state to allow the pump(s) to run. Then place the enable-input device in the "disable" state.

          - Acceptance Criteria:

            - Start: Chilled-water pump(s) start when, and only when, the enable-input device is in the "enable" state.

            - Shutdown: The enable-input device stops the chilled-water pump(s) when placed in the "disable" state.

        - Start-and-Stop Cooling-Tower Fans(s):

          - Prerequisites: Installation verification of the following:

            - Input Device: Flow switch in condenser-water circuit <Insert device designation>.

            - Output Device: [Starter] [DDC system command to starter] <Insert device designation> relay.

            - Display:

              - Condenser-water flow indication.

              - Cooling-tower fan(s) on-off indication.

          - Scope: Condenser-water system, including cooling tower, condenser-water pump(s), and associated controls.

          - Purpose:

            - Cooling-tower fan(s) start.

            - Cooling-tower fan(s) shutdown.

          - Conditions of the Test:

            - Verify Start: Start with cooling-tower fan enable-input device in the "disable" state to prevent fan(s) start. Place the enable-input device in the "enable" state.

            - Verify Shutdown: Start with the enable-input device in the "enable" state to allow the fan(s) to run. Then place the enable-input device in the "disable" state.

          - Acceptance Criteria:

            - Start: Chilled-water pump(s) start when, and only when, the enable-input device is in the "enable" state.

            - Shutdown: The enable-input device stops the chilled-water pump(s) when placed in the "disable" state.

        - Alternative Chiller(s):

          - Prerequisites: Installation verification of the following:

            - Input Device: [Electric alternator] [DDC system software] <Insert device designation>.

            - Output Device: [Chiller] [DDC system command to chiller] <Insert device designation> terminal strip.

            - Display:

              - Chiller(s) on-off indication.

              - Chiller failure alarm.

          - Scope:

            - Chilled-water system and associated controls.

            - Condenser-water system and associated controls.

          - Purpose:

Retain first two subparagraphs below if system has two chillers.

            - Lead-lag rotation of chillers.

            - Replacement of failed chiller in rotation.

Retain first three subparagraphs below if system has three or more chillers.

            - Adding and dropping chillers as follows: <Insert sequence and parameters>.

            - Replacement of failed chiller in add/drop sequence.

            - Chiller failure alarm initiation.

          - Conditions of the Test:

            - Lead-Lag Rotation - Chiller Start: Create a number of chilled-water system start-stop cycles equal to the number of chillers plus one.

            - Lead-Lag Rotation - Lead Chiller Fail: Disable the lead chiller while it is running.

            - Lead-Lag Rotation - Lag Chiller Fail: Disable a lag chiller while it is running.

            - Lead-Lag Rotation - Chiller Start Fail: Disable a chiller while it is in standby mode. Initiate a lead-lag rotation call for the disabled chiller to start.

Retain last four subparagraphs above or first two subparagraphs below.

            - Add/Drop Sequence - Increasing Demand: Increase chilled-water demand incrementally to observe the corresponding addition of chillers. Increase demand gradually as the load approaches the set point for adding the next chiller, to permit observation of the actual load at the time the next chiller is enabled.

            - Add/Drop Sequence - Decreasing Demand: Decrease chilled-water demand incrementally to observe the corresponding dropping of chillers. Decrease demand gradually as the load approaches the set point for dropping the next chiller, to permit observation of the actual load at the time the next chiller is disabled.

          - Acceptance Criteria:

            - Lead-Lag Rotation - Chiller Start: On each chilled-water system start event, the [other] [next] chiller in rotation starts as the lead chiller, and the previous lead chiller, is designated as the [last-]lag chiller.

            - Lead-Lag Rotation - Lead Chiller Fail: When the lead chiller fails, the [other] [next] chiller in rotation starts as the lead chiller, and a chiller failure alarm, is initiated for the failed chiller.

            - Lead-Lag Rotation - Lag Chiller Fail: When the lag chiller fails, [the next chiller in rotation starts as the lead chiller, and ]a chiller failure alarm is initiated for the failed chiller.

            - Lead-Lag Rotation - Chiller Start Fail: When a chiller fails to start, [the next chiller in rotation starts in its place, and ]a chiller failure alarm is initiated for the failed chiller.

Retain last four subparagraphs above or four subparagraphs below.

            - Add/Drop Sequence - Increasing Demand: Chillers are added at the specified load set point, plus or minus [5] <Insert number> percent. Chilled-water supply temperature remains stable within plus or minus [2.0 deg F (1.1 deg C)] <Insert temperature> of set point.

            - Add/Drop Sequence - Decreasing Demand: Chillers are dropped at the specified load set point, plus or minus [5] <Insert number> percent. Chilled-water supply temperature remains stable within plus or minus [2.0 deg F (1.1 deg C)] <Insert temperature> of set point.

            - Add/Drop Sequence - Operating Chiller Fail: When an operating chiller fails, the next chiller in sequence starts and a chiller failure alarm is initiated for the failed chiller.

            - Add/Drop Sequence - Chiller Start Fail: When a chiller fails to start, the next chiller in sequence starts in its place and a chiller failure alarm is initiated for the failed chiller.

      - TERMINAL UNIT EQUIPMENT Cx TESTS

        - VAV Terminal Air Units with Coils:

          - Prerequisites: Installation verification of the following:

            - Occupancy Input Device: Occupancy sensor.

            - Occupancy Output Device: DDC system binary output.

            - Room Temperature Input Device: [Room thermostat] [Electronic temperature sensor].

            - Room Temperature Output Device: [Pneumatic] [Electronic] damper actuators and control-valve operators.

            - Display the following at the operator's workstation:

              - Room/area served.

              - Room occupied/unoccupied.

              - Room temperature indication.

              - Room temperature set point.

              - Room temperature set point, occupied.

              - Room temperature set point, unoccupied.

              - Air-damper position as percentage open.

              - Control-valve position as percentage open.

          - Scope: VAV terminal air units with [hydronic] [steam] coils in supply-air systems, and associated controls.

          - Purpose:

            - Occupancy-dependent room temperature set-point reset.

            - Room temperature control.

          - Conditions of the Test:

            - Cx Test Demonstration Sampling Rate: [10] <Insert number> percent of each model/size unit.

            - Temperature Control - Occupied: Start with the room unoccupied. Occupy the room and observe the change to occupied status. Observe temperature control until room temperature is stable at occupied set point, plus or minus [1.0 deg F (0.6 deg C)] <Insert temperature>.

            - Temperature Control - Unoccupied: Start with the room occupied. Vacate the room and observe the change to unoccupied status. Observe temperature control until room temperature is stable at unoccupied set point, plus or minus [1.0 deg F (0.6 deg C)] <Insert temperature>.

          - Acceptance Criteria:

            - Temperature Control - Occupied:

              - Control system status changes from "occupied" to "unoccupied" after the specified time.

              - Room temperature is stable at occupied set point, plus or minus [1.0 deg F (0.6 deg C)] <Insert temperature> within [10] <Insert number> minutes of occupancy. Room temperature does not overshoot or undershoot set point by more than [2.0 deg F (1.1 deg C)] <Insert temperature> during transition.

            - Temperature Control - Unoccupied:

              - Control system status changes from "unoccupied" to "occupied" [immediately] [after five minutes of continuous occupancy].

              - Room temperature is stable at unoccupied set point, plus or minus [1.0 deg F (0.6 deg C)] <Insert temperature> within [30] <Insert number> minutes of occupancy.

      - AIR-HANDLING SYSTEM Cx TESTS

Retain applicable paragraphs below for Project's air-handling unit(s). If a project has more than one type of air-handling unit, copy this article and re-edit for each product.

        - Supply Fan(s) Variable-Volume Control:

          - Prerequisites: Installation verification of the following:

            - Volume-Control Input Device: [Static-pressure transmitter] [Differential-pressure switch] sensing supply-duct static pressure referenced to conditioned-space static pressure.

            - Volume-Control Output Device: [Receiver controller] [DDC system analog output] [DDC system analog output to digital-to-pneumatic transducer] to modulating damper actuator. Set inlet guide vanes to [minimum] [closed] position when fan is stopped.

Retain last two subparagraphs above for fans equipped with variable inlet vanes; retain first two subparagraphs below for fans equipped with variable-speed drives.

            - Volume-Control Input Device: [Static-pressure transmitter] [Differential-pressure switch] sensing supply-duct static pressure referenced to conditioned-space static pressure.

            - Volume-Control Output Device: [Receiver controller] [DDC system analog output] to motor speed controller. Set variable-speed drive to minimum speed when fan is stopped.

            - High-Pressure Input Device: Static-pressure transmitter sensing supply-duct static pressure referenced to static pressure outside the duct.

            - High-Pressure Output Device: [Receiver controller] [DDC system binary output] to [alarm panel] [motor starter].

            - Display the following at the operator's workstation:

              - Supply-fan-discharge static-pressure indication.

              - Supply-fan-discharge static-pressure set point.

              - Supply-fan airflow rate.

              - Supply-fan [inlet vane position] [speed].

          - Scope: VAV supply fan units and associated controls.

          - Purpose:

            - Supply-air discharge static pressure control.

            - Response to excess supply-air discharge static pressure condition.

          - Conditions of the Test:

            - Minimum supply-air flow.

            - Midrange Supply-Air Flow: [50 to 60] <Insert number(s)> percent of maximum.

            - Maximum supply-air flow.

            - Excess supply-air discharge static pressure.

          - Acceptance Criteria:

            - At all supply-air flow rates, and during changes in supply-air flow, discharge air static pressure is at set point plus or minus [2] <Insert number> percent.

            - Fan stops and an alarm is initiated at the operator's workstation when supply-air discharge static pressure is at the excess static pressure, plus or minus [2] <Insert number> percent.

        - Air-Handler Mixed-Air Control:

          - Prerequisites: Installation verification of the following:

            - Minimum Position Input Device: [Time clock] [DDC system time schedule] .

            - Output Device: [Receiver controller] [DDC system analog output] [DDC system analog output to digital-to-pneumatic transducer] to modulating damper actuator(s).

            - Heating Reset Input Device: [Room thermostat] [DDC system software] .

            - [Supply] [Mixed]-Air Temperature Input Device: [Duct-mounted thermostat] [Electronic temperature sensor].

            - Cooling Reset Input Device: Outdoor- and return-air, duct-mounted [thermostats] [electronic temperature sensors].

            - Display the following at the operator's workstation:

              - Mixed-air-temperature indication.

              - Mixed-air-temperature set point.

              - Mixed-air damper position.

          - Scope: Air handler with mixed-air control and associated controls.

          - Purpose:

            - Occupied time control.

            - Minimum damper position control.

            - Heating reset control.

            - [Supply] [Mixed]-air temperature control.

            - Cooling reset control.

            - Unoccupied time control.

          - Conditions of the Test:

            - Occupied Time Control: Start in unoccupied schedule. Advance to occupied schedule time.

            - Minimum Damper Position Control: Command system to mode in which minimum damper position is required.

            - Heating Reset Control: Create a call for heating.

            - [Supply] [Mixed]-Air Temperature Control: Override [supply] [mixed]-air temperature set point to a value [2.0 deg F (1.1 deg C)] <Insert temperature> above current [supply] [mixed]-air temperature.

            - Cooling Reset Control: Override outdoor-air [temperature to a value that exceeds return-air temperature] [enthalpy to a value that exceeds return-air enthalpy].

            - Unoccupied Time Control: Advance to unoccupied schedule time.

            - Control Data Trend Log: Set up a data trend log of the following input device values and output device commands. Record data at [hourly] <Insert alternative recording frequency> intervals. Submit trend data for [24-hour] <Insert time> periods in which natural conditions require heating reset control, [supply] [mixed]-air temperature control, and cooling reset control.

              - Minimum position input device.

              - Heating reset input device.

              - [Supply] [Mixed]-air temperature input device.

              - Cooling reset input device.

          - Acceptance Criteria:

            - Occupied Time Control: Mixed-air control is active in occupied mode.

            - Minimum Damper Position Control: Controller [opens minimum outdoor-air dampers] [positions outdoor-air dampers to minimum position].

            - Heating Reset Control: Controller [closes minimum outdoor-air dampers] [sets outdoor-air dampers to minimum position].

            - [Supply] [Mixed]-Air Temperature Control: Controller modulates outdoor-, return-, and relief-air dampers to maintain temporary [supply] [mixed]-air temperature set point, plus or minus [1.0 deg F (0.6 deg C)] <Insert temperature>.

            - Cooling Reset Control: Controller sets outdoor-air dampers to minimum position when outdoor-air [temperature exceeds return-air temperature] [enthalpy exceeds return-air enthalpy].

            - Unoccupied Time Control: Controller positions outdoor- and relief-air dampers closed and return-air dampers open.

            - Control Data Trend Log: Data verify control in accordance with sequence of control.

END OF SECTION 230800