Copyright 2022 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 230923 - DIRECT DIGITAL CONTROL (DDC) SYSTEM FOR HVAC

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED 2009, LEED v4, LEED v4.1, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using the hypertext links.

- GENERAL

      - SUMMARY

        - Section Includes: Direct digital control (DDC) system for HVAC.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 230923.13 "Energy Meters" for thermal and electric power energy meters that connect to DDC systems.

          - Section 230923.17 "Level Instruments" for liquid-level switches, sensors, and transmitters that connect to DDC systems.

          - Section 230923.22 "Position Instruments" for limit switches that connect to DDC systems.

          - Section 230923.33 "Vibration Instruments" for vibration instruments that connect to DDC systems.

          - Section 230923.43 "Weather Stations" for weather stations that connect to DDC systems.

          - Section 230993.11 "Sequence of Operations for HVAC DDC" for control sequences in DDC systems.

          - Section 270553 "Identification for Communications Systems" for identification requirements for communications components.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - Algorithm: A logical procedure for solving a recurrent mathematical problem. A prescribed set of well-defined rules or processes for solving a problem in a finite number of steps.

        - Analog: A continuously varying signal value, such as current, flow, pressure, or temperature.

        - BACnet Specific Definitions:

          - BACnet: Building Automation Control Network Protocol, ASHRAE 135. A communications protocol allowing devices to communicate data and services over a network.

          - BACnet Interoperability Building Blocks (BIBBs): BIBB defines a small portion of BACnet functionality that is needed to perform a particular task. BIBBs are combined to build the BACnet functional requirements for a device.

          - BACnet/IP: Defines and allows using a reserved UDP socket to transmit BACnet messages over IP networks. A BACnet/IP network is a collection of one or more IP subnetworks that share the same BACnet network number.

          - BACnet Testing Laboratories (BTL): Organization responsible for testing products for compliance with ASHRAE 135, operated under direction of BACnet International.

        - Binary: Two-state signal where a high signal level represents "ON" or "OPEN" condition and a low signal level represents "OFF" or "CLOSED" condition. "Digital" is sometimes used interchangeably with "Binary" to indicate a two-state signal.

        - Controller: Generic term for any standalone, microprocessor-based, digital controller residing on a network, used for local or global control. Three types of controllers are indicated: network controllers, programmable application controllers, and application-specific controllers.

        - Control System Integrator: An entity that assists in expansion of existing enterprise system and support of additional operator interfaces to I/O being added to existing enterprise system.

        - COV: Changes of value.

        - DDC System Provider: Authorized representative of, and trained by, DDC system manufacturer and responsible for execution of DDC system Work indicated.

        - Distributed Control: Processing of system data is decentralized and control decisions are made at subsystem level. System operational programs and information are provided to remote subsystems and status is reported back. On loss of communication, subsystems to be capable of operating in a standalone mode using the last best available data.

        - E/P: Voltage to pneumatic.

        - Gateway: Bidirectional protocol translator that connects control systems that use different communication protocols.

        - HLC: Heavy load conditions.

        - I/O: System through which information is received and transmitted. I/O refers to analog input (AI), binary input (BI), analog output (AO) and binary output (BO). Analog signals are continuous and represent control influences such as flow, level, moisture, pressure, and temperature. Binary signals convert electronic signals to digital pulses (values) and generally represent two-position operating and alarm status. "Digital," (DI) and (DO), is sometimes used interchangeably with "Binary," (BI) and (BO), respectively.

        - I/P: Current to pneumatic.

        - LAN: Local area network.

        - LNS: LonWorks Network Services.

        - LON Specific Definitions:

          - FTT-10: Echelon Transmitter-Free Topology Transceiver.

          - LonMark International: Association comprising suppliers and installers of LonTalk products. Association provides guidelines for implementing LonTalk protocol to ensure interoperability through a standard or consistent implementation.

          - LonTalk: An open standard protocol developed by Echelon Corporation that uses a "Neuron Chip" for communication. LonTalk is a register trademark of Echelon.

          - LonWorks: Network technology developed by Echelon.

          - Node: Device that communicates using CTA-709.1-D protocol and that is connected to a CTA-709.1-D network.

          - Node Address: The logical address of a node on the network, consisting of a Domain number, Subnet number, and Node number. "Node number" portion of an address is a number assigned to device during installation, is unique within a subnet, and is not a factory-set unique Node ID.

          - Node ID: A unique 48-bit identifier assigned at factory to each CTA-709.1-D device. Sometimes called a "Neuron ID."

          - Program ID: An identifier (number) stored in a device (usually, EEPROM) that identifies node manufacturer, functionality of device (application and sequence), transceiver used, and intended device usage.

          - Standard Configuration Property Type (SCPT): Pronounced "skip-it." A standard format type maintained by LonMark for configuration properties.

          - Standard Network Variable Type (SNVT): Pronounced "snivet." A standard format type maintained by LonMark used to define data information transmitted and received by individual nodes. "SNVT" is used in two ways. It is an acronym for "Standard Network Variable Type" and is often used to indicate a network variable itself (i.e., it can mean "a network variable of a standard network variable type").

          - Subnet: Consists of a logical grouping of up to 127 nodes, where logical grouping is defined by node addressing. Each subnet is assigned a number, which is unique within a Domain. See "Node Address."

          - TP/FT-10: Free Topology Twisted Pair network defined by CTA-709.3 and is most common media type for a CTA-709.1-D control network.

          - TP/XF-1250: High-speed, 1.25 Mbps, twisted-pair, doubly terminated bus network defined by "LonMark Interoperability Guidelines" and typically used only to connect multiple TP/FT-10 networks.

          - User-Defined Configuration Property Type (UCPT): Pronounced "u-keep-it." A Configuration Property format type that is defined by device manufacturer.

          - User-Defined Network Variable Type (UNVT): Network variable format defined by device manufacturer. UNVTs create non-standard communications that other vendors' devices may not correctly interpret and may negatively impact system operation. UNVTs are not allowed.

        - Low Voltage: As defined in NFPA 70 for circuits and equipment operating at less than 50 V or for remote-control, signaling power-limited circuits.

        - Mobile Device: A data-enabled phone or tablet computer capable of connecting to a cellular data network and running a native control application or accessing a web interface.

        - Modbus TCP/IP: An open protocol for exchange of process data.

        - MS/TP: Master-slave/token-passing, ISO/IEC/IEEE 8802-3. Datalink protocol LAN option that uses twisted-pair wire for low-speed communication.

        - MTBF: Mean time between failures.

        - Network Controller: Digital controller, which supports a family of programmable application controllers and application-specific controllers, that communicates on peer-to-peer network for transmission of global data.

        - Network Repeater: Device that receives data packet from one network and rebroadcasts it to another network. No routing information is added to protocol.

        - Peer to Peer: Networking architecture that treats all network stations as equal partners.

        - POT: Portable operator's terminal.

        - RAM: Random access memory.

        - RF: Radio frequency.

        - Router: Device connecting two or more networks at network layer.

        - Server: Computer used to maintain system configuration, historical and programming database.

        - TCP/IP: Transport control protocol/Internet protocol.

        - UPS: Uninterruptible power supply.

        - USB: Universal Serial Bus.

        - User Datagram Protocol (UDP): This protocol assumes that the IP is used as the underlying protocol.

        - VAV: Variable air volume.

        - WLED: White light emitting diode.

      - PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a conference.

        - Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Multiple Submissions:

          - If multiple submissions are required to execute work within schedule, first submit a coordinated schedule clearly defining intent of multiple submissions. Include a proposed date of each submission with a detailed description of submittal content to be included in each submission.

          - Clearly identify each submittal requirement indicated and in which submission the information will be provided.

          - Include an updated schedule in each subsequent submission with changes highlighted to easily track the changes made to previous submitted schedule.

        - Product Data:

          - Construction details, material descriptions, dimensions of individual components and profiles, and finishes.

          - Operating characteristics, electrical characteristics, and furnished accessories indicating process operating range, accuracy over range, control signal over range, default control signal with loss of power, calibration data specific to each unique application, electrical power requirements, and limitations of ambient operating environment, including temperature and humidity.

          - Product description with complete technical data, performance curves, and product specification sheets.

          - Installation, operation, and maintenance instructions including factors effecting performance.

          - Bill of materials of indicating quantity, manufacturer, and extended model number for each unique product.

First 15 subparagraphs below are examples only of products to include.

            - Workstations.

            - Printers.

            - Servers.

            - Gateways.

            - Routers.

            - Protocol analyzers.

            - DDC controllers.

            - Enclosures.

            - Electrical power devices.

            - UPS units.

            - Accessories.

            - Instruments.

            - Control dampers and actuators.

            - Control valves and actuators.

            - <Insert product>.

          - When manufacturer's product datasheets apply to a product series rather than a specific product model, clearly indicate and highlight only applicable information.

          - Each submitted piece of product literature to clearly cross reference specification and drawings that submittal is to cover.

        - Software Submittal:

          - Cross-referenced listing of software to be loaded on each operator workstation, server, gateway, <Insert product,> and DDC controller.

          - Description and technical data of all software provided and cross-referenced to products in which software will be installed.

          - Operating system software, operator interface and programming software, color graphic software, DDC controller software, maintenance management software, and third-party software.

          - Include a flow diagram and an outline of each subroutine that indicates each program variable name and units of measure.

          - Listing and description of each engineering equation used with reference source.

          - Listing and description of each constant used in engineering equations and a reference source to prove origin of each constant.

          - Description of operator interface to alphanumeric and graphic programming.

          - Description of each network communication protocol.

          - Description of system database, including all data included in database, database capacity, and limitations to expand database.

          - Description of each application program and device drivers to be generated, including specific information on data acquisition and control strategies showing their relationship to system timing, speed, processing burden, and system throughout.

          - Controlled Systems: Instrumentation list with element name, type of device, manufacturer, model number, and product data. Include written description of sequence of operation including schematic diagram.

        - Shop Drawings:

          - General Requirements:

            - Include cover drawing with Project name, location, Owner, Architect, Contractor, and issue date with each Shop Drawings submission.

            - Include a drawing index sheet listing each drawing number and title that matches information in each title block.

            - Drawings Size: <Insert requirements>.

          - Include plans, elevations, sections, and mounting details where applicable.

          - Include details of product assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

          - Detail means of vibration isolation and show attachments to rotating equipment.

          - Plan Drawings indicating the following:

            - Screened backgrounds of walls, structural grid lines, HVAC equipment, ductwork, and piping.

            - Room names and numbers with coordinated placement to avoid interference with control products indicated.

            - Each desktop workstation network port, server, gateway, router, DDC controller, control panel instrument connecting to DDC controller, and damper and valve connecting to DDC controller, if included in Project.

            - Exact placement of products in rooms, ducts, and piping to reflect proposed installed condition.

            - Network communication cable and raceway routing.

            - Information, drawn to scale, of <Insert requirements>.

            - Proposed routing of wiring, cabling, conduit, and tubing; coordinated with building services for review before installation.

          - Schematic drawings for each controlled HVAC system indicating the following:

            - I/O points labeled with point names shown. Indicate instrument range, normal operating set points, and alarm set points. Indicate fail position of each damper and valve, if included in Project.

            - I/O listed in table format showing point name, type of device, manufacturer, model number, and cross-reference to product data sheet number.

            - A graphic showing location of control I/O in proper relationship to HVAC system.

            - Wiring diagram with each I/O point having a unique identification and indicating labels for all wiring terminals.

            - Unique identification of each I/O that to be consistently used between different drawings showing same point.

            - Elementary wiring diagrams of controls for HVAC equipment motor circuits including interlocks, switches, relays, and interface to DDC controllers.

            - Narrative sequence of operation.

            - Graphic sequence of operation, showing all inputs and output logical blocks.

          - Control panel drawings indicating the following:

            - Panel dimensions, materials, size, and location of field cable, raceways, and tubing connections.

            - Interior subpanel layout, drawn to scale and showing all internal components, cabling and wiring raceways, nameplates, and allocated spare space.

            - Front, rear, and side elevations and nameplate legend.

            - Unique drawing for each panel.

          - DDC system network riser diagram indicating the following:

            - Each device connected to network with unique identification for each.

            - Interconnection of each different network in DDC system.

            - For each network, indicate communication protocol, speed, and physical means of interconnecting network devices, such as copper cable type, or optical fiber cable type. Indicate raceway type and size for each.

            - Each network port for connection of an operator workstation or other type of operator interface with unique identification for each.

          - DDC system electrical power riser diagram indicating the following:

            - Each point of connection to field power with requirements (volts/phase//hertz/amperes/connection type) listed for each.

            - Each control power supply including, as applicable, transformers, power-line conditioners, transient voltage suppression and high filter noise units, DC power supplies, and UPS units with unique identification for each.

            - Each product requiring power with requirements (volts/phase//hertz/amperes/connection type) listed for each.

            - Power wiring type and size, race type, and size for each.

          - Monitoring and control signal diagrams indicating the following:

            - Control signal cable and wiring between controllers and I/O.

            - Point-to-point schematic wiring diagrams for each product.

            - Control signal tubing to sensors, switches, and transmitters.

            - Process signal tubing to sensors, switches, and transmitters.

Retain first subparagraph below for pneumatically actuated products.

            - Pneumatic main air and control signal tubing to pneumatic [damper] [and] [valve] actuators, pilot-positioners if applicable, and associated transducers.

          - Color graphics indicating the following:

            - Itemized list of color graphic displays to be provided.

            - For each display screen to be provided, a true color copy showing layout of pictures, graphics, and data displayed.

            - Intended operator access between related hierarchical display screens.

        - System Description:

          - Full description of DDC system architecture, network configuration, operator interfaces and peripherals, servers, controller types and applications, gateways, routers and other network devices, and power supplies.

          - Complete listing and description of each report, log and trend for format and timing, and events that initiate generation.

          - System and product operation under each potential failure condition including, but not limited to, the following:

            - Loss of power.

            - Loss of network communication signal.

            - Loss of controller signals to inputs and outpoints.

            - Operator workstation failure.

            - Server failure.

            - Gateway failure.

            - Network failure.

            - Controller failure.

            - Instrument failure.

            - Control damper and valve actuator failure.

            - <Insert potential failure conditions>.

          - Complete bibliography of documentation and media to be delivered to Owner.

          - Description of testing plans and procedures.

          - Description of Owner training.

Retain "Samples" Paragraph below for applications requiring special attention.

        - Samples:

          - For each of the following exposed product(s), installed in finished space for approval of selection of aesthetic characteristics:

            - Gas instruments specified in Section 230923.16 "Gas Instruments."

            - Moisture instruments specified in Section 230923.19 "Moisture Instruments."

            - Motion instruments specified in Section 230923.21 "Motion Instruments."

            - Pressure instruments specified in Section 230923.23 "Pressure Instruments."

            - Temperature instruments specified in Section 230923.27 "Temperature Instruments."

            - <Insert devices>.

Retain "Delegated Design Submittals" Paragraph below if design services have been delegated to Contractor.

        - Delegated Design Submittals: For DDC system products and installation indicated as being delegated.

          - Supporting documentation showing DDC system design complies with performance requirements indicated, including calculations and other documentation necessary to prove compliance.

          - Schedule and design calculations for control dampers and actuators.

            - Flow at Project design and minimum flow conditions.

            - Face velocity at Project design and minimum airflow conditions.

            - Pressure drop across damper at Project design and minimum airflow conditions.

            - AMCA 500-D damper installation arrangement used to calculate and schedule pressure drop, as applicable to installation.

            - Maximum close-off pressure.

            - Leakage airflow at maximum system pressure differential (fan close-off pressure).

            - Torque required at worst case condition for sizing actuator.

            - Actuator selection indicating torque provided.

            - Actuator signal to control damper (on, close, or modulate).

            - Actuator position on loss of power.

            - Actuator position on loss of control signal.

          - Schedule and design calculations for control valves and actuators.

            - Flow at Project design and minimum flow conditions.

            - Pressure-differential drop across valve at Project design flow condition.

            - Maximum system pressure-differential drop (pump close-off pressure) across valve at Project minimum flow condition.

            - Design and minimum control valve coefficient with corresponding valve position.

            - Maximum close-off pressure.

            - Leakage flow at maximum system pressure differential.

            - Torque required at worst case condition for sizing actuator.

            - Actuator selection indicating torque provided.

            - Actuator signal to control damper (on, close or modulate).

            - Actuator position on loss of power.

            - Actuator position on loss of control signal.

          - Schedule and design calculations for selecting flow instruments.

            - Instrument flow range.

            - Project design and minimum flow conditions with corresponding accuracy, control signal to transmitter, and output signal for remote control.

            - Extreme points of extended flow range with corresponding accuracy, control signal to transmitter, and output signal for remote control.

            - Pressure-differential loss across instrument at Project design flow conditions.

            - Where flow sensors are mated with pressure transmitters, provide information for each instrument separately and as an operating pair.

Retain "Sustainable Design Submittals" Paragraph below if required to attain sustainability rating or to track sustainability submittals.

        - Sustainable Design Submittals:

          - <Double click to insert sustainable design text for Energy Star labeling.>

          - <Double click to insert sustainable design text for adhesives and sealants.>

      - INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Retain "Coordination Drawings" Paragraph below where coordination is required for installation of products and materials by separate installers. Preparation of coordination drawings requires participation of each trade involved; coordinate with other Sections specifying products and materials to be included. See Section 013100 "Project Management and Coordination."

        - Coordination Drawings:

          - Plan drawings, reflected ceiling plans, or Building Information Model (BIM), and corresponding product installation details, drawn to scale, showing the items described in this Section and coordinated with all building trades.

Coordinate "Qualification Statements" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article. If inserting additional entities or specialist, add qualifications to "Quality Assurance" Article.

        - Qualification Statements:

          - Systems Provider's Qualification Data:

            - Resume of project manager assigned to Project.

            - Resumes of application engineering staff assigned to Project.

            - Resumes of installation and programming technicians assigned to Project.

            - Resumes of service technicians assigned to Project.

            - Brief description of past project including physical address, floor area, number of floors, building system cooling and heating capacity, and building's primary function.

            - Description of past project DDC system, noting similarities to Project scope and complexity indicated.

            - Names of staff assigned to past project that will also be assigned to execute work of this Project.

            - Owner contact information for past project including name, phone number, and email address.

            - Contractor contact information for past project including name, phone number, and email address.

            - Architect[ and Engineer] contact information for past project including name, phone number, and email address.

          - Manufacturer's qualification data.

          - Testing agency's qualification data.

Retain "Welding certificates" Paragraph below if retaining "Welding Qualifications" Paragraph in "Quality Assurance" Article.

        - Welding certificates.

Retain "Product Certificates" Paragraph below to require submittal of product certificates from manufacturers.

        - Product Certificates:

          - Data Communications Protocol Certificates:

Retain one of first two subparagraphs below. Retain first subparagraph if compliance with ASHRAE 135 is required; retain second if LonWorks is required.

            - Certifying that each proposed DDC system component complies with ASHRAE 135.

            - Certifying that each proposed DDC system component complies with LonWorks.

Retain subparagraph below to require submittal of product certificates from manufacturers.

          - <Insert list of products>.

        - Test and Evaluation Reports:

          - Product Test Reports: For DDC system equipment and components, for tests performed by [a qualified testing agency] [manufacturer] [manufacturer and witnessed by a qualified testing agency].

Retain "Preconstruction Test Reports" Subparagraph below if specifying preconstruction testing in "Preconstruction Testing" Article as Contractor's responsibility.

          - Preconstruction Test Reports: For each separate test performed.

        - Source Quality-Control Reports: For DDC system equipment and components.

Retain "Field Quality-Control Reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field Quality-Control Reports: For DDC system equipment and components.

        - Sample warranty.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For DDC system.

          - In addition to items specified in Section 017823 "Operation and Maintenance Data," include the following:

            - Project Record Drawings of as-built versions of submittal Shop Drawings provided in electronic PDF format.

            - Testing and commissioning reports and checklists of completed final versions of reports, checklists, and trend logs.

            - As-built versions of submittal Product Data.

            - Names, addresses, email addresses, and 24-hour telephone numbers of Installer and service representatives for DDC system and products.

            - Operator's manual with procedures for operating control systems including logging on and off, handling alarms, producing point reports, trending data, overriding computer control, and changing set points and variables.

            - Programming manuals with description of programming language and syntax, of statements for algorithms and calculations used, of point database creation and modification, of program creation and modification, and of editor use.

            - Engineering, installation, and maintenance manuals that explain how to do the following:

              - Design and install new points, panels, and other hardware.

              - Perform preventive maintenance and calibration.

              - Debug hardware problems.

              - Repair or replace hardware.

            - Documentation of all programs created using custom programming language including set points, tuning parameters, and object database.

            - Backup copy of graphic files, programs, and databases on electronic media.

            - List of recommended spare parts with part numbers and suppliers.

            - Complete original-issue documentation, installation, and maintenance information for furnished third-party hardware including computer equipment and sensors.

            - Complete original-issue copies of furnished software, including operating systems, custom programming language, operator workstation software, and graphics software.

            - Licenses, guarantees, and warranty documents.

            - Recommended preventive maintenance procedures for system components, including schedule of tasks such as inspection, cleaning, and calibration; time between tasks; and task descriptions.

            - Owner training materials.

      - MAINTENANCE MATERIAL SUBMITTALS

See Section 017700 "Closeout Procedures" for submission of maintenance material items.

        - Extra Stock Material: Furnish extra materials and parts to Owner that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

        - Include product manufacturers' recommended parts lists for proper product operation over [four] <Insert time>-year period following warranty period. Parts list to be indicated for each year.

Retain first paragraph below for product parts inventory over an extended operating period.

        - Furnish parts, as indicated by manufacturer's recommended parts list, for product operation during [one] [two] <Insert time>-year period following warranty period.

Retain paragraph below for spare product inventory.

        - Furnish quantity indicated of matching product(s) in Project inventory for each unique size and type of following:

Subparagraphs below are examples only of extra materials that may be required.

          - Network Controller: [One] <Insert quantity>.

          - Programmable Application Controller: [One] <Insert quantity>.

          - Application-Specific Controller: [One] <Insert quantity>.

          - General-Purpose Relay: [One] <Insert quantity>.

          - Multifunction Time-Delay Relay: [One] <Insert quantity>.

          - Latching Relay: [One] <Insert quantity>.

          - Current-Sensing Relay: [One] <Insert quantity>.

          - Combination On-Off Status Sensor and On-Off Relay: [One] <Insert quantity>.

          - Transformer: [One] <Insert quantity>.

          - DC Power Supply: [One] <Insert quantity>.

          - <Insert product>.

      - QUALITY ASSURANCE

        - DDC System Manufacturer Qualifications:

          - Nationally recognized manufacturer of DDC systems and products.

          - DDC systems with similar requirements to those indicated for a continuous period of [five] [10] <Insert number> years within time of bid.

          - DDC systems and products that have been successfully tested and in use on at least [three] [five] <Insert number> past projects.

          - Having complete published catalog literature, installation, operation, and maintenance manuals for all products intended for use.

          - Having full-time in-house employees for the following:

            - Product research and development.

            - Product and application engineering.

            - Product manufacturing, testing, and quality control.

            - Technical support for DDC system installation training, commissioning, and troubleshooting of installations.

            - Owner operator training.

        - DDC System Provider Qualifications:

          - Authorized representative of, and trained by, DDC system manufacturer.

          - In-place facility located within <Insert distance> of Project.

          - Demonstrate past experience with installation of DDC system products being installed for period within [three] [five] <Insert number> consecutive years before time of bid.

          - Demonstrate past experience on [five] <Insert number> projects of similar complexity, scope, and value.

          - Demonstrate past experience of each [person] <Insert requirement> assigned to Project.

          - Staffing resources of competent and experienced full-time employees that are assigned to execute work according to schedule.

          - Service and maintenance staff assigned to support Project during warranty period.

          - Product parts inventory to support ongoing DDC system operation for a period of not less than [five] <Insert number> years after Substantial Completion.

          - DDC system manufacturer's backing to take over execution of the Work if necessary to comply with requirements indicated. Include Project-specific written letter, signed by manufacturer's corporate officer, if requested.

Retain "Testing Agency Qualifications" Paragraph below if Contractor selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article. Qualification requirements are in addition to those specified in Section 014000 "Quality Requirements."

        - Testing Agency Qualifications: Member company of NETA.

          - Testing Agency's Field Supervisor: Certified by NETA to supervise on-site testing.

Retain "Welding Qualifications" Paragraph below if shop or field welding is required. If retaining, also retain "Welding certificates" Paragraph in "Informational Submittals" Article.

        - Welding Qualifications: Qualify procedures and personnel in accordance with the following welding codes:

Retain first subparagraph below for structural welding of steel.

          - AWS D1.1/D1.1M.

Retain first subparagraph below for structural welding of aluminum.

          - AWS D1.2/D1.2M.

Retain first subparagraph below for structural welding of sheet steel.

          - AWS D1.3/D1.3M.

Retain subparagraph below for structural welding of reinforcing steel.

          - AWS D1.4/D1.4M.

        - Pipe and Pressure-Vessel Welding Qualifications: Qualify procedures and operators in accordance with ASME Boiler and Pressure Vessel Code.

      - MOCKUPS

        - Build mockups to verify selections made under Sample submittals, to demonstrate aesthetic effects, to set quality standards for materials and execution, and to set quality standards for fabrication and installation.

Retain one of first two subparagraphs below, or both.

          - Build mockups of completed installation where products are exposed to view and are located in areas with aesthetic requirements that warrant special attention, including the following spaces:

In first subparagraph below, list specific areas requiring mockups, such as main lobbies, executive offices, conference rooms, and boardrooms.

            - <Insert specific locations for mockups>.

          - Build mockups of completed installation for areas as indicated on Drawings.

          - Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Owner specifically approves such deviations by Change Order.

Retain subparagraph below if the intention is to make an exception to the default requirement in Section 014000 "Quality Requirements" for demolishing and removing mockups.

          - Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

      - PRECONSTRUCTION TESTING

Retain this article for preconstruction testing. Project-specific preconstruction testing of assemblies can be expensive but may be the best means of proving that performance requirements are met.

        - Preconstruction Testing Service: [Owner will engage] [Engage] a qualified testing agency to perform preconstruction testing on field mockups.

Retain first subparagraph below if configurations of assemblies are not indicated on Drawings.

          - <Insert configurations of assemblies>.

          - Provide test assemblies representative of proposed materials and construction.

          - Build laboratory mockups at testing agency facility; use personnel, materials, and methods of construction that will be used at Project site.

          - Notify Architect [seven] <Insert number> days in advance of dates and times when laboratory mockups will be tested.

        - Preconstruction Testing: Performed by a qualified testing agency on manufacturer's standard assemblies.

Subparagraph below describes Project-specific preconstruction testing requirements.

          - <Insert preconstruction requirements>.

      - WARRANTY

When warranties are required and available, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

        - Special Warranty: Manufacturer and Installer agree to repair or replace products that fail in materials or workmanship within specified warranty period.

          - Adjust, repair, or replace failures at no additional cost or reduction in service to Owner.

          - Include updates or upgrades to software and firmware if necessary to resolve deficiencies.

            - Install updates only after receiving Owner's written authorization.

          - Perform warranty service during normal business hours and commence within [8] [16] [24] <Insert number> hours of Owner's warranty service request.

Verify warranty periods.

          - Warranty Period: [Two] <Insert number> year(s) from date of Substantial Completion.

            - For Gateway: [Two] [Three] <Insert number>-year parts and labor warranty for each.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - DIRECT DIGITAL CONTROL (DDC) SYSTEM FOR HVAC

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

      - DDC SYSTEM DESCRIPTION

        - Microprocessor-based monitoring and control including analog/digital conversion and program logic. A control loop or subsystem in which digital and analog information is received and processed by a microprocessor, and digital control signals are generated based on control algorithms and transmitted to field devices to achieve a set of predefined conditions.

          - DDC system consisting of[ high-speed,] peer-to-peer network of distributed DDC controllers[, other network devices], operator interfaces, and software.

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

      - WEB ACCESS

Retain this article to require web access to DDC system.

In paragraph below, retain "web based" or "web compatible" option, or both. See the Evaluations for discussion. Consult manufacturers about web-access capabilities of their DDC system offerings. Limiting to only one method of web access may exclude some manufacturers.

        - DDC system to be [web based] [or] [web compatible].

Retain "Web-Based Access to DDC System" Subparagraph below if retaining "web based" option in paragraph above.

          - Web-Based Access to DDC System:

            - DDC system software based on server thin-client architecture, designed around open standards of web technology. DDC system server accessed using a web browser over DDC system network, using Owner's LAN, and remotely over Internet[ through Owner's LAN].

            - Intent of thin-client architecture is to provide operators complete access to DDC system via a web browser. No special software other than a web browser is required to access graphics, point displays, and trends; to configure trends, points, and controllers; and to edit programming.

            - Password-protected web access.

Retain "Web-Compatible Access to DDC System" Subparagraph below if retaining "web compatible" option in paragraph above.

          - Web-Compatible Access to DDC System:

            - [Workstation] [and] [or] [server] to perform overall system supervision and configuration, graphical user interface, management report generation, and alarm annunciation.

            - DDC system to support web browser access to building data. Operator using a standard web browser is able to access control graphics and change adjustable set points.

            - Password-protected web access.

      - PERFORMANCE REQUIREMENTS

Coordinate "Delivery of Selected Control Devices" Paragraph below with "Control Devices for Installation by Installers" and "Control Devices for Equipment Manufacturer Factory Installation" articles.

        - Delivery of Selected Control Devices: Deliver to equipment and systems manufacturers for factory installation and to HVAC systems installers for field installation.

Retain "Delegated Design, Qualified Professional Engineer" or "Delegated Design, Qualified Professional" Paragraph below if Contractor is required to assume responsibility for design.

        - Delegated Design, Qualified Professional Engineer: Engage a qualified professional engineer, as defined in Section 014000 "Quality Requirements," to design DDC system to satisfy requirements indicated.

        - Delegated Design, Qualified Professional: Engage a qualified professional to design DDC system to satisfy requirements indicated.

          - System Performance Objectives:

            - DDC system manages HVAC systems.

            - DDC system operates HVAC systems to achieve optimum operating costs while using least possible energy and maintaining specified performance.

            - DDC system responds to power failures, HVAC equipment failures, and adverse and emergency conditions encountered through connected I/O points.

            - DDC system operates while unattended by an operator and through operator interaction.

            - DDC system records trends and transactions of events and produces report information such as performance, energy, occupancies, and equipment operation.

        - Surface-Burning Characteristics: Products installed in ducts, equipment, and return-air paths complying with ASTM E84; testing by a qualified testing agency. Identify products with appropriate markings of applicable testing agency.

          - Flame-Spread Index: [25] <Insert value> or less.

          - Smoke-Developed Index: [50] <Insert value> or less.

        - DDC System Speed:

          - Response Time of Connected I/O:

First option in first four subparagraphs below is taken from ASHRAE's Guideline 13.

            - Update AI point values connected to DDC system at least every [five] [two] seconds for use by DDC controllers. Points used globally to also comply with this requirement.

            - Update BI point values connected to DDC system at least every [five] [two] <Insert number> seconds for use by DDC controllers. Points used globally to also comply with this requirement.

            - AO points connected to DDC system to begin to respond to controller output commands within [two] [one] second(s). Global commands to also comply with this requirement.

            - BO point values connected to DDC system to respond to controller output commands within [two] [one] <Insert number> second(s). Global commands to also comply with this requirement.

          - Display of Connected I/O:

            - Update and display analog point COV connected to DDC system at least every [10] [five] <Insert number> seconds for use by operator.

            - Update and display binary point COV connected to DDC system at least every [10] [five] <Insert number> seconds for use by operator.

            - Update and display alarms of analog and digital points connected to DDC system within [45] [30] [15] <Insert number> seconds of activation or change of state.

            - Update graphic display refresh within [eight] [four] <Insert number> seconds.

            - Point change of values and alarms displayed from workstation to workstation when multiple operators are viewing from multiple workstations to not exceed graphic refresh rate indicated.

        - Network Bandwidth: Design each network of DDC system to include spare bandwidth with DDC system operating under normal and heavy load conditions indicated. Calculate bandwidth usage, and apply a safety factor to ensure that requirement is satisfied when subjected to testing under worst case conditions. Minimum spare bandwidth as follows:

          - Level 1 Networks: [20] [30] <Insert value>.

          - Level 2 Networks: [20] [30] <Insert value>.

          - Level 3 Networks: [10] [20] [30] <Insert value>.

          - <Insert requirements>.

Retain "DDC System Data Storage" Paragraph below to provide DDC system data archived storage over an extended operating period.

        - DDC System Data Storage:

          - Include capability to archive not less than [24] [36] [48] [60] <Insert number> consecutive months of historical data for all I/O points connected to system, including alarms, event histories, transaction logs, trends, and other information indicated.

          - Local Storage:

            - Provide [server ]with data storage indicated. Server(s) to use IT industry standard database platforms and be capable of functions described in "DDC Data Access" Paragraph.

Retain "Cloud Storage" Subparagraph below if security of data is acceptable to Owner.

          - Cloud Storage:

            - Provide [application-based] [and] [web browser] interfaces to configure, upload, download, and manage data and to service plan with storage adequate to store all data for term indicated. Cloud storage uses IT industry standard database platforms and is capable of functions described in "DDC Data Access" Paragraph.

Retain "DDC Data Access" Paragraph below for systems using local data storage or systems that store information locally and in the cloud. Change terminology as required. Coordinate with "Servers" Article.

        - DDC Data Access:

          - When logged into the system, operator able to also interact with any DDC controllers connected to DDC system as required for functional operation of DDC system.

          - Use for application configuration; for archiving, reporting, and trending of data; for operator transaction archiving and reporting; for network information management; for alarm annunciation; and for operator interface tasks and controls application management.

        - Future Expandability:

          - DDC system size is expandable to an ultimate capacity of at least [1.25] [1.5] [two] <Insert number> times total I/O points indicated.

          - Design and install system networks to achieve ultimate capacity with only addition of DDC controllers, I/O, and associated wiring and cable. Design and install initial network infrastructure to support ultimate capacity without having to remove and replace portions of network installation.

          - Operator interfaces installed initially do not require hardware and software additions and revisions for system when operating at ultimate capacity.

        - Input Point Values Displayed Accuracy: Meet following end-to-end overall system accuracy, including errors associated with meter, sensor, transmitter, lead wire or cable, and analog to digital conversion.

Coordinate values used in subparagraphs below with accuracy of instruments specified in related Sections. Values below cannot be better than other values used elsewhere.

          - Energy:

            - Thermal: Within [5] [3] [1] <Insert number> percent of reading.

            - Electric Power: Within [1] <Insert number> percent of reading.

            - Requirements indicated on Drawings for meters not supplied by utility.

          - Flow:

            - Air: Within [5] [2] <Insert number> percent of design flow rate.

            - Air (Terminal Units): Within [10] [5] <Insert number> percent of design flow rate.

            - Fuel Oil: Within [2] [5] <Insert number> percent of design flow rate.

            - Natural Gas: Within [2] [5] <Insert number> percent of design flow rate.

            - Water: Within [2] [5] <Insert number> percent of design flow rate.

            - Steam: Within [5] <Insert number> percent of design flow rate.

          - Gas:

            - Carbon Dioxide: Within [50] <Insert value> ppm.

            - Carbon Monoxide: Within [5] <Insert number> percent of reading.

            - Oxygen: Within [5] <Insert number> percent of reading.

            - Refrigerant: Within [5] <Insert number> percent of reading.

            - VOCs: Within [5] <Insert number> percent of reading.

          - Moisture (Relative Humidity):

            - Air: Within [5] [2] <Insert number> percent RH.

            - Space: Within [5] [2] <Insert number> percent RH.

            - Outdoor: Within [5] [2] <Insert number> percent RH.

          - Level: Within [5] [2] <Insert number> percent of reading.

          - Pressure:

            - Air, Ducts and Equipment: [1] [0.5] <Insert number> percent of instrument [range] [span].

            - Space: Within [1] [0.5] [0.25] <Insert number> percent of instrument [range] [span].

            - Water: Within [1] [0.5] [0.25] <Insert number> percent of instrument [range] [span].

            - Steam: Within [1] [0.5] [0.25] <Insert number> percent of instrument [range] [span].

          - Speed: Within [10] [5] <Insert number> percent of reading.

          - Temperature, Dew Point:

            - Air: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - Space: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - Outdoor: Within [3 deg F (1.5 deg C)] [2 deg F (1 deg C)] <Insert value>.

          - Temperature, Dry Bulb:

            - Air: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - Space: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - Outdoor: Within [2 deg F (1 deg C)] [1 deg F (0.5 deg C)] <Insert value>.

            - Chilled Water: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - Condenser Water: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - Heating Hot Water: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - Energy Recovery Runaround Liquid: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - Steam: Within [2 deg F (1 deg C)] [1 deg F (0.5 deg C)] <Insert value>.

            - Temperature Difference: Within [0.1 deg F (0.05 deg C)] [0.25 deg F (0.15 deg C)] <Insert value>.

            - <Insert system>.

            - Other Temperatures Not Indicated: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

          - Temperature, Wet Bulb:

            - Air: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - Space: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - Outdoor: Within [2 deg F (1 deg C)] [1 deg F (0.5 deg C)] <Insert value>.

          - Vibration: Within [5] [10] <Insert number> percent of reading.

        - Precision of I/O Reported Values: Values reported in database and displayed to have following precision:

          - Current:

            - Milliamperes: Nearest 1/100th of a milliampere.

            - Amperes: Nearest 1/10th of an ampere up to 100 A; nearest ampere for 100 A and more.

          - Energy:

            - Electric Power:

              - Rate (Watts): Nearest 1/10th of a watt through 1000 W.

              - Rate (Kilowatts): Nearest 1/10th of a kilowatt through 1000 kW; nearest kilowatt above 1000 kW.

              - Usage (Kilowatt-Hours): Nearest kilowatt through 10,000 kW; nearest 10 kW between 10,000 and 100,000 kW; nearest 100 kW for above 100,000 kW.

            - Fuel Oil (Usage): For gallons, nearest 1/10th of a gallon up to 100 gal.; nearest gallon for above 100 gal. (For liters, nearest 1/10th of a liter up to 1000 L; nearest liter for above 1000 L).

            - Natural Gas (Usage): Nearest 1/10th of a unit (cubic feet, MCF, therm) up to 100 units; nearest unit for above 100 units (For MCM, nearest 1/10th of an MCM up to 1000 MCM; nearest MCM for above 1000 MCM).

            - Thermal, Rate:

              - Heating: For British thermal units per hour, nearest British thermal unit per hour up to 1000 Btu/h; nearest 10 Btu/h between 1000 and 10,000 Btu/h; nearest 100 Btu/h for above 10,000 Btu/h. For MBh, round to nearest MBh up to 1000 MBh; nearest 10 MBh between 1000 and 10,000 MBh; nearest 100 MBh above 10,000 MBh (For watts, nearest watt up to 1000 W; for kilowatts, round to nearest kilowatt up to 1000 kW; nearest 10 kW between 1000 and 10 000 kW; nearest 100 kW for above 10 000 kW).

              - Cooling: For tons, nearest ton up to 1000 tons; nearest 10 tons between 1000 and 10,000 tons; nearest 100 tons above 10,000 tons (For watts, nearest watt up to 1000 W; for kilowatts, round to nearest kilowatt up to 1000 kW; nearest 10 kW between 1000 and 10 000 kW; nearest 100 kW for above 10 000 kW).

            - Thermal, Usage:

              - Heating: For British thermal unit, nearest British thermal unit up to 1000 Btu; nearest 10 Btu between 1000 and 10,000 Btu; nearest 100 Btu for above 10,000 Btu. For MBtu, round to nearest MBtu up to 1000 MBtu; nearest 10 MBtu between 1000 and 10,000 MBtu; nearest 100 MBtu above 10,000 MBtu (For watt-hours, nearest watt-hour up to 1000 Wh; for kilowatt-hours, round to nearest kilowatt-hour up to 1000 kWh; nearest 10 kWh between 1000 and 10 000 kWh; nearest 100 kWh for above 10 000 kWh).

              - Cooling: For ton-hours, nearest ton-hours up to 1000 ton-hours; nearest 10 ton-hours between 1000 and 10,000 ton-hours; nearest 100 tons above 10,000 tons (For watt-hours, nearest watt-hour up to 1000 Wh; for kilowatt-hours, round to nearest kilowatt-hour up to 1000 kWh; nearest 10 kWh between 1000 and 10 000 kWh; nearest 100 kWh for above 10 000 kWh).

          - Flow:

            - Air: Nearest 1/10th of a cubic feet per minute through 100 cfm; nearest cubic feet per minute between 100 and 1000 cfm; nearest 10 cfm between 1000 and 10,000 cfm; nearest 100 cfm above 10,000 cfm (Nearest 1/10th of a liter per second through 100 L/s; nearest liter per second between 100 and 1000 L/s; nearest 10 L/s between 1000 and 10 000 L/s; nearest 100 L/s above 10 000 L/s).

            - Fuel Oil: Nearest 1/10th of a gallon per minute through 100 gpm; nearest gallon per minute between 100 and 1000 gpm (Nearest 1/10th of a liter per second through 100 L/s; nearest liter per second between 100 and 1000 L/s).

            - Natural Gas: Nearest 1/10th of a cubic feet per hour through 100 cfh; nearest cubic feet per hour between 100 and 1000 cfh; nearest 10 cfh between 1000 and 10,000 cfh; nearest 100 cfh above 10,000 cfh (Nearest 1/100th of a cubic meter per hour through 100 cmh; nearest 1/10th cmh between 100 and 1000 cmh; nearest cubic meter per hour above 1000 cmh).

            - Water: Nearest 1/10th of a gallon per minute through 100 gpm; nearest gallon per minute between 100 and 1000 gpm; nearest 10 gpm between 1000 and 10,000 gpm; nearest 100 gpm above 10,000 gpm (Nearest 1/10th of a liter per second through 100 L/s; nearest liter per second between 100 and 1000 L/s; nearest 10 L/s between 1000 and 10 000 L/s; nearest 100 L/s above 10 000 L/s).

            - Steam: Nearest 1/10th of a pound per hour through 100 lb/h; nearest pound per hour between 100 and 1000 lb/h; nearest 10 lb/h above 1000 lb/h (Nearest 1/10th of a liter per second through 100 L/s; nearest liter per second between 100 and 1000 L/s; nearest 10 L/s above 1000 L/s).

          - Gas:

            - Carbon Dioxide (ppm): Nearest ppm.

            - Carbon Monoxide (ppm): Nearest ppm.

            - Oxygen (Percentage): Nearest 1/10th of 1 percent.

            - Refrigerant (ppm): Nearest ppm.

            - Volatile Organic Compounds (ppm): Nearest ppm

          - Moisture (Relative Humidity):

            - Relative Humidity (Percentage): Nearest 1 percent.

          - Level: Nearest 1/100th of an inch through 10 inches; nearest 1/10 of an inch between 10 and 100 inches; nearest inch above 100 inches (Nearest 1/100th of a millimeter through 10 mm; nearest 1/10th of a millimeter between 10 and 100 mm; nearest millimeter above 100 mm).

          - Speed:

            - Rotation (rpm): Nearest 1 rpm.

            - Velocity: Nearest 1/10th of feet per minute through 100 fpm; nearest feet per minute between 100 and 1000 fpm; nearest 10 fpm above 1000 fpm (Nearest 1/100th of a meter per second through 10 m/s; nearest 1/10th of a meter per second above 10 m/s).

          - Position, Dampers and Valves (Percentage Open): Nearest 1 percent.

          - Pressure:

            - Air, Ducts and Equipment: Nearest 1/10th of an inch water closet (Nearest pascal up to 1000 Pa; nearest 10 Pa above 1000 Pa).

            - Space: Nearest 1/100th of an inch water closet (Nearest 1/10th of a pascal).

            - Steam: Nearest 1/10th of pounds per square inch gauge through 100 psig; nearest pounds per square inch gauge above 100 psig (Nearest kilopascal through 1000 kPa; nearest 10 kPa above 1000 kPa).

            - Water: Nearest 1/10 of a pound per square inch gauge through 100 psig; nearest pound per square inch gauge above 100 psig (Nearest kilopascal through 1000 kPa; nearest 10 kPa above 1000 kPa).

          - Temperature:

            - Air, Ducts and Equipment: Nearest 1/10th of a degree.

            - Outdoor: Nearest degree.

            - Space: Nearest 1/10th of a degree.

            - Chilled Water: Nearest 1/10th of a degree.

            - Condenser Water: Nearest 1/10th of a degree.

            - Heating Hot Water: Nearest degree.

            - Heat Recovery Runaround: Nearest 1/10th of a degree.

            - Steam: Nearest degree.

          - Vibration: Nearest 1/10th of an inch per second (Nearest 1/10th of a millimeter per second).

          - Voltage: Nearest 1/10 V up to 100 V; nearest volt above 100 V.

        - Control Stability: Control variables indicated within the following limits:

Coordinate values used in eight subparagraphs below with values used in "Input Point Values Displayed Accuracy" Paragraph in this article and with accuracy of instruments specified in related Sections. Values below cannot be better than other values used elsewhere.

          - Flow:

            - Air, Ducts and Equipment, except Terminal Units: Within [5] [2] <Insert number> percent of design flow rate.

            - Air, Terminal Units: Within [10] [5] <Insert number> percent of design flow rate.

            - Water: Within [2] [5] <Insert number> percent of design flow rate.

            - Steam: Within [5] <Insert number> percent of design flow rate.

          - Gas:

            - Carbon Dioxide: Within [50] <Insert value> ppm.

            - Carbon Monoxide: Within [5] <Insert number> percent of reading.

            - Oxygen: Within [5] <Insert number> percent of reading.

          - Moisture (Relative Humidity):

            - Air: Within [5] [2] <Insert number> percent RH.

            - Space: Within [5] [2] <Insert number> percent RH.

            - Outdoor: Within [5] [2] <Insert number> percent RH.

          - Level: Within [5] [2] <Insert number> percent of reading.

          - Pressure:

            - Air, Ducts and Equipment: [1] [0.5] <Insert number> percent of instrument [range] [span].

            - Space: Within [1] [0.5] [0.25] <Insert number> percent of instrument [range] [span].

            - Water: Within [1] [0.5] [0.25] <Insert number> percent of instrument [range] [span].

            - Steam: Within [1] [0.5] [0.25] <Insert number> percent of instrument [range] [span].

          - Temperature, Dew Point:

            - Air: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - Space: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

          - Temperature, Dry Bulb:

            - Air: Within [2 deg F (1 deg C)] [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - Space: Within [2 deg F (1 deg C)] [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - Chilled Water: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - Condenser Water: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - Heating Hot Water: Within [2 deg F (1 deg C)] [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - Energy Recovery Runaround Liquid: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - <Insert system>.

          - Temperature, Wet Bulb:

            - Air: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

            - Space: Within [1 deg F (0.5 deg C)] [0.5 deg F (0.2 deg C)] <Insert value>.

        - Environmental Conditions for Controllers, Gateways, and Routers:

          - Products to operate without performance degradation under ambient environmental temperature, pressure, and humidity conditions encountered for installed location.

            - If product alone cannot comply with requirement, install product in a protective enclosure that is isolated and protected from conditions impacting performance. Enclosure to be internally insulated, electrically heated, cooled, and ventilated as required by product and application.

          - Protect products with enclosures satisfying the following minimum requirements unless more stringent requirements are indicated. House products not available with integral enclosures complying with requirements indicated in protective secondary enclosures. Installed location dictates the following NEMA 250 enclosure requirements:

            - Outdoors, Protected: [Type 2] [Type 3] [Type 12] <Insert type>.

            - Outdoors, Unprotected: [Type 4] [Type 4X].

            - Indoors, Heated with Filtered Ventilation: [Type 1] [Type 2] <Insert type>.

            - Indoors, Heated with Non-Filtered Ventilation: [Type 2] [Type 12] <Insert type>.

            - Indoors, Heated and Air-Conditioned: [Type 1] <Insert type>.

            - Mechanical Equipment Rooms:

              - Chiller and Boiler Rooms: [Type 12] [Type 4] [Type 4X] <Insert type>.

              - Air-Moving Equipment Rooms: [Type 1] [Type 2] [Type 12] <Insert type>.

            - Localized Areas Exposed to Washdown: [Type 4] [Type 4X] <Insert type>.

            - Within Duct Systems and Air-Moving Equipment Not Exposed to Possible Condensation: [Type 2] [Type 3] [Type 12] <Insert type>.

            - Within Duct Systems and Air-Moving Equipment Exposed to Possible Condensation: [Type 4] [Type 4X] <Insert type>.

            - Hazardous Locations: Explosion-proof rating for condition.

            - <Insert location and enclosure requirements>.

        - Environmental Conditions for Instruments and Actuators:

          - Instruments and actuators to operate without performance degradation under the ambient environmental temperature, pressure, humidity, and vibration conditions specified and encountered for installed location.

            - If instruments and actuators alone cannot comply with requirement, install instruments and actuators in protective enclosures that are isolated and protected from conditions impacting performance. Enclosure is internally insulated, electrically heated[, cooled], and ventilated as required by instrument and application.

          - Protect instruments, actuators, and accessories with enclosures satisfying the following minimum requirements unless more stringent requirements are indicated. House instruments and actuators not available with integral enclosures complying with requirements indicated in protective secondary enclosures. Installed location is to dictate the following NEMA 250 enclosure requirements:

            - Outdoors, Protected: [Type 2] [Type 3] [Type 12] <Insert type>.

            - Outdoors, Unprotected: [Type 4] [Type 4X].

            - Indoors, Heated with Filtered Ventilation: [Type 1] [Type 2] <Insert type>.

            - Indoors, Heated with Non-Filtered Ventilation: [Type 2] [Type 12] <Insert type>.

            - Indoors, Heated and Air-conditioned: [Type 1] <Insert type>.

            - Mechanical Equipment Rooms:

              - Chiller and Boiler Rooms: [Type 12] [Type 4] [Type 4X] <Insert type>.

              - Air-Moving Equipment Rooms: [Type 1] [Type 2] [Type 12] <Insert type>.

            - Localized Areas Exposed to Washdown: [Type 4] [Type 4X] <Insert type>.

            - Within Duct Systems and Air-Moving Equipment Not Exposed to Possible Condensation: [Type 2] [Type 3] [Type 12] <Insert type>.

            - Within Duct Systems and Air-Moving Equipment Exposed to Possible Condensation: [Type 4] [Type 4X] <Insert type>.

            - Hazardous Locations: Explosion-proof rating for condition.

            - <Insert location and enclosure requirements>.

Retain "DDC System Reliability" Paragraph below for projects with critical reliability requirements.

        - DDC System Reliability:

          - Design, install, and configure DDC controllers, [gateways,] [routers,] [and] <Insert product> to yield a MTBF of at least [40,000] [20,000] <Insert number> hours, based on a confidence level of at least [90] <Insert number> percent. MTBF value includes any failure for any reason to any part of products indicated.

          - If required to comply with MTBF indicated, include DDC system and product redundancy to maintain DCC system, and associated systems and equipment being controlled, operational, and under automatic control.

Coordinate requirement in subparagraph below with Drawings.

          - See Drawings for critical systems and equipment that require a higher degree of DDC system redundancy than MTBF indicated.

Retain "Electric Power Quality" Paragraph below for applications requiring additional protection. Consult Project electrical engineer.

        - Electric Power Quality:

          - Power-Line Surges:

            - Protect [susceptible ]DDC system products connected to ac power circuits from power-line surges to comply with requirements of IEEE C62.41.1 and IEEE C62.41.2.

            - Do not use fuses for surge protection.

            - Test protection in the normal mode and in the common mode, using the following two waveforms:

              - 10-by-1000-microsecond waveform with a peak voltage of 1500 V and a peak current of 60 A.

              - 8-by-20-microssecond waveform with a peak voltage of 1000 V and a peak current of 500 A.

          - Power Conditioning:

            - Protect [susceptible ]DDC system products connected to ac power circuits from irregularities and noise rejection. Characteristics of power-line conditioner are as follows:

              - At 85 percent load, output voltage to not deviate by more than plus or minus 1 percent of nominal when input voltage fluctuates between minus 20 percent to plus 10 percent of nominal.

              - During load changes from zero to full load, output voltage to not deviate by more than [2] [3] <Insert number> percent of nominal.

              - Accomplish full correction of load switching disturbances within [five] <Insert number> cycles, and 95 percent correction within [two] <Insert number> cycles of onset of disturbance.

              - Total harmonic distortion to not exceed [2] [3] <Insert number> percent at full load.

          - Ground Fault: Protect products from ground fault by providing suitable grounding. Products to not fail due to ground fault condition.

        - Backup Power Source:

          - Serve DDC system products that control HVAC systems and equipment served by a backup power source also from a backup power source.

Retain "UPS" Paragraph below for applications requiring uninterrupted power.

        - UPS:

          - DDC system products powered by UPS units are to include the following:

First five subparagraphs below are examples only for equipment that should be provided with UPS.

            - Servers.

            - Gateways.

            - DDC controllers[, except application-specific controllers].

            - Desktop workstations.

            - <Insert equipment>.

Retain first subparagraph below to power instruments or actuators through UPS.

          - DDC system instruments and actuators powered by UPS units are to include the following:

            - Instruments: [Where indicated on Drawings; ]where associated with the following systems controlled by DDC system:

              - <Insert list of systems>.

Retain first subparagraph below to power damper actuators through UPS. Usually, this is only required for actuators with required response time less than time needed to bring backup power online.

            - Damper Actuators: [Where indicated on Drawings; ]where associated with the following systems controlled by DDC system:

              - <Insert list of systems>.

Retain first subparagraph below to power valve actuators through UPS. Usually, this is only required for actuators with required response time less than time needed to bring backup power online.

            - Valve Actuators: [Where indicated on Drawings; ]where associated with the following systems controlled by DDC system:

              - <Insert list of systems>.

Retain "Continuity of Operation after Electric Power Interruption" Paragraph below for applications with systems and equipment connected to backup power systems that must remain operational without operator intervention. Coordinate requirement with other Sections.

        - Continuity of Operation after Electric Power Interruption:

          - Equipment and associated factory-installed controls, field-installed controls, electrical equipment, and power supply connected to building normal and backup power systems are to automatically return equipment and associated controls to operating state occurring immediately before loss of normal power, without need for manual intervention by operator when power is restored either through backup power source or through normal power if restored before backup power is brought online.

      - PANEL-MOUNTED, MANUAL OVERRIDE SWITCHES

Retain "Manual Override of Control Dampers" Paragraph below to provide manual override capability for control dampers.

        - Manual Override of Control Dampers:

          - Include panel-mounted, two-position, selector switch for each automatic control damper being controlled by DDC controller.

          - Label each switch with damper designation served by switch.

          - Label switch positions to indicate either "Manual" or "Auto" control signal to damper.

          - With switch in "Auto" position, control signal to damper actuator with control loop output signal from DDC controller.

          - With switch in "Manual" position, control signal to damper actuator at panel with either an integral or a separate switch to include local control.

            - For Binary Control Dampers: Manual two-position switch with "Close" and "Open" switch positions indicated. With switch in "Close" position, close damper. With switch in "Open" position, open damper.

            - For Analog Control Dampers: A gradual switch with "Close" and "Open" switch limits indicated. Operator switches knob to adjust damper to any position from close to open.

          - DDC controller to monitor and report position of each manual override selector switch. With switch placed in "manual" position, DDC controller to signal an override condition to alert operator that damper is under manual, not automatic, control.

Retain first subparagraph below to require override independent of DDC controller. Some manufacturers offer manual override feature integral to DDC controller, thus making the manual override feature more affordable. Standalone manual override switches will increase cost of manual override feature.

          - Configure manual override switches to allow operator to manually operate damper while at panel without DDC controller [installed] [and] [operational].

          - Terminal equipment including [VAV units,] [fan-coil units,] [and] [unit heaters] do not require manual override unless otherwise indicated by sequence of operation.

Retain "Manual Override of Control Valves" Paragraph below to provide manual override capability for control valves.

        - Manual Override of Control Valves:

          - Include panel-mounted, two-position, selector switch for each automatic control valve being controlled by DDC controller.

          - Label each switch with valve designation served by switch.

          - Label switch positions to indicate either "Manual" or "Auto" control signal to valve.

          - With switch in "Auto" position, control signal to valve actuator with a control loop output signal from DDC controller.

          - With switch in "Manual" position, control signal to valve actuator at panel with either an integral or a separate switch to include local control.

            - For Binary Control Valves: Manual two-position switch with "Close" and "Open" switch positions indicated. With switch in "Close" position, close valve. With switch in "Open" position, open valve.

            - For Analog Control Valves: A gradual switch with "Open" and "Close" switch limits indicated. Operator rotates switch knob to adjust valve to any position from close to open.

          - DDC controller to monitor and report position of each manual override selector switch. With switch placed in "manual" position, DDC controller to signal an override condition to alert operator that valve is under manual, not automatic, control.

Retain first subparagraph below to require override independent of DDC controller. Some manufacturers offer manual override feature integral to DDC controller, thus making the manual override feature more affordable. Standalone manual override switches will increase cost of manual override feature.

          - Configure manual override switches to allow operator to manually operate valve while at panel without DDC controller [installed] [and] [operational].

          - Terminal equipment including [VAV units,] [fan-coil units,] [and] [unit heaters] do not require manual override unless otherwise indicated by sequence of operation.

      - SYSTEM ARCHITECTURE

        - System architecture consisting of no more than [two] [or] [three] <Insert number> levels of LANs.

          - Level 2 LAN: Connect network controllers and operator workstations.

          - Level 1 or Level 2 LAN: Connect [Level 1] [or] [Level 2] programmable application controllers to other programmable application controllers and to network controllers.

          - Level 2 or Level 3 LAN: Connect [Level 2] [or] [Level 3] application-specific controllers to [programmable application controllers and to network controllers] [application-specific controllers].

Coordinate requirements in "Minimum Data Transfer and Communication Speed" Paragraph below with "Networks" Article to ensure that speed requirements retained for a project can be achieved by networks retained for a project.

        - Minimum Data Transfer and Communication Speed:

In first subparagraph below, retain "100" or "10" option for Ethernet networks. Retain "2.5" option for ATA 878.1 networks. Retain "1.25" option for CTA-709.1-D networks.

          - LAN Connecting Operator Workstations and Network Controllers: [100] [10] [2.5] [1.25] <Insert value> Mbps.

          - LAN Connecting Programmable Application Controllers: [1000] [100] <Insert value> kbps.

          - LAN Connecting Application-Specific Controllers: [115,000] [76,800] [38,400] [19,200] <Insert value> bps.

        - Provide dedicated[ and separated] DDC system LANs that are not shared with other building systems and tenant data and communication networks.

        - Provide modular system architecture with inherent ability to expand to not less than [1.25] [1.5] [two] <Insert number> times system size indicated with no impact to performance indicated.

        - Configure architecture to [eliminate] [or] [minimize] need to remove and replace existing network equipment for system expansion.

        - Make number of LANs and associated communication transparent to operator. Configure all I/O points residing on any LAN to be capable of global sharing between all system LANs.

        - Design system to eliminate dependence on any single device for system alarm reporting and control execution. Design each controller to operate independently by performing own control, alarm management, and historical data collection.

        - Special Network Architecture Requirements:

          - Air-Handling Systems: For control applications of an air-handling system that consists of air-handling unit(s) and VAV terminal units, include a dedicated LAN of application-specific controllers serving VAV terminal units connected directly to controller that is controlling air-handling-system air-handling unit(s). Basically, create DDC system LAN that aligns with air-handling system being controlled.

          - <Insert additional requirements>.

      - DDC SYSTEM OPERATOR INTERFACES

        - Operator Means of System Access: Operator able to access entire DDC system through any of multiple means including, but not limited to, the following:

          - Desktop and portable workstation with hardwired connection through LAN port.

          - Portable operator terminal with hardwired connection through LAN port.

          - Portable operator workstation with wireless connection through LAN router.

          - Mobile device and application with secured wireless connection through LAN router or cellular data service.

          - Remote connection through web access.

        - Make access to system, regardless of operator means used, transparent to operator.

        - Network Ports: For hardwired connection of desktop or portable workstation. Network port easily accessible, properly protected, clearly labeled, and installed at the following locations:

First seven subparagraphs below are examples only.

          - Each mechanical equipment room.

          - Each boiler room.

          - Each chiller room.

          - Each outdoor on-grade yard and elevated platform with equipment connected to DDC system.

          - Each different roof level with roof-mounted equipment connected to DDC system.

          - Security system command center.

          - Fire-alarm system command center.

          - <Insert additional locations>.

        - Desktop Workstations:

Retain option in first subparagraph below if workstations are not furnished with DDC system but are furnished by Owner. Consult Owner.

          - Connect [Owner-furnished ]desktop workstation(s) to DDC system Level 1 LAN through a communications port directly on LAN or through a communications port on a DDC controller.

          - Able to communicate with any device located on any DDC system LAN.

        - Portable Workstations:

Retain option in first subparagraph below if workstations are not furnished with DDC system but are furnished by Owner. Consult Owner.

          - Connect [Owner-furnished ]portable workstation(s) to DDC system Level 1 LAN through a communications port directly on LAN or through a communications port on a DDC controller.

          - Able to communicate with any device located on any DDC system LAN.

          - Connect to DDC system [Level 2] [or] [Level 3] LAN through a communications port on an application-specific controller, or a room temperature sensor connected to an application-specific controller.

          - Connect to system through a wireless router connected to Level 1 LAN.

          - Connect to system through a cellular broadband data service.

          - Portable workstation able to communicate with any device connected to any system LAN regardless of point of physical connection to system.

          - Monitor, program, schedule, adjust set points, and report capabilities of I/O connected anywhere in system.

          - Have dynamic graphic displays that are identical to desktop workstations.

        - POT:

          - Connect DDC controller through a communications port local to controller.

          - Able to communicate with any DDC system controller that is directly connected [or with LAN] [or connected to DDC system].

        - Mobile Device (Tablet and Smart Phone):

          - Connect Owner-furnished mobile devices to system through a wireless router connected to LAN[ and cellular data service].

          - Able to communicate with any DDC controller connected to DDC system using [dedicated application] [and] [secure web access].

        - Critical Alarm Reporting:

          - Send operator-selected critical alarms to notify operator of critical alarms that require immediate attention.

          - Send alarm notification to multiple recipients that are assigned for each alarm.

          - Notify recipients by any or all means, including email, text message, and prerecorded phone message to mobile and landline phone numbers.

        - Simultaneous Operator Use: Capable of accommodating up to [five] [10] [20] <Insert number> simultaneous operators that are accessing DDC system through any of operator interfaces indicated.

      - NETWORKS

        - Acceptable networks for connecting workstations, mobile devices, and network controllers include the following:

Retain applicable subparagraphs below to suit DDC system size and complexity. See the Evaluations.

          - ATA 878.1, ARCNET.

          - CTA-709.1-D.

          - IP.

          - ISO/IEC/IEEE 8802-3, Ethernet.

          - <Insert type>.

        - Acceptable networks for connecting programmable application controllers include the following:

Retain applicable subparagraphs below to suit DDC system size and complexity. See the Evaluations.

          - ATA 878.1, ARCNET.

          - CTA-709.1-D.

          - IP.

          - ISO/IEC/IEEE 8802-3, Ethernet.

          - <Insert type>.

        - Acceptable networks for connecting application-specific controllers include the following:

Retain applicable subparagraphs below to suit DDC system size and complexity. See the Evaluations.

          - ATA 878.1, ARCNET.

          - CTA-709.1-D.

          - TIA 485-A.

          - IP.

          - ISO/IEC/IEEE 8802-3, Ethernet.

          - <Insert type>.

      - NETWORK COMMUNICATION PROTOCOL

See the Evaluations for additional information on network communication protocols.

        - Use network communication protocol(s) that are open to Owner and available to other companies for use in making future modifications to DDC system.

Retain "ASHRAE 135 Protocol" Paragraph below to limit entire DDC system communication protocol to ASHRAE 135.

        - ASHRAE 135 Protocol:

          - Use ASHRAE 135 communication protocol as sole and native protocol used throughout entire DDC system.

          - DDC system to not require use of gateways except to integrate HVAC equipment and other building systems and equipment; not required to use ASHRAE 135 communication protocol.

          - If used, gateways to connect to DDC system using ASHRAE 135 communication protocol and Project object properties and read/write services indicated by interoperability schedule.

          - Use operator workstations, controllers, and other network devices that are tested and listed by BTL.

Retain "CTA-709.1-D Protocol" Paragraph below to limit entire DDC system communication protocol to CTA-709.1-D.

        - CTA-709.1-D Protocol:

          - Open implementation of LonWorks technology using CTA 709.1-D communication protocol and using LonMark SNVTs as defined in LonMark SNVT list exclusively for communication throughout DDC system.

          - Use LNS for all network management including addressing and binding of network variables.

            - Submit final LNS database with Project closeout submittals.

            - All devices are to be online and commissioned into LNS database.

          - Use CTA-709.1-D protocol for all connected device. Install so SCPT output from any node on network can be bound to any other node in the domain.

Retain "Industry Standard Protocols" Paragraph below to give choice to use one or multiple industry standard protocols.

        - Industry Standard Protocols:

          - Use any one or a combination of the following industry standard protocols for network communication while complying with other DDC system requirements indicated:

First four subparagraphs below are examples only.

            - ASHRAE 135.

            - CTA-709.1-D.

            - Modbus Application Protocol Specification V1.1b3.

            - <Insert standard protocol>.

          - Operator workstations [and network controllers ]are to communicate through [ASHRAE 135] [or] [CTA-709.1-D] protocol.

          - Provide portions of DDC system networks using ASHRAE 135 communication protocol as an open implementation of network devices complying with ASHRAE 135. Use network devices that are tested and listed by BTL.

          - Provide portions of DDC system networks using CTA-709.1-D communication protocol as an open implementation of LonWorks technology using CTA-709.1-D communication protocol and using LonMark SNVTs as defined in LonMark SNVT list exclusively for DDC system.

          - Provide portions of DDC system networks using Modbus Application Protocol Specification V1.1b3 communication protocol as an open implementation of network devices and technology complying with Modbus Application Protocol Specification V1.1b3.

          - Use gateways to connect networks and network devices with different protocols.

      - DDC SYSTEM WIRELESS NETWORKS

        - Use [Zigbee] [or] [an open industry standard and technology used by multiple DDC system manufacturers] <Insert wireless technology> technology to create a wireless mesh network to provide wireless connectivity for network devices at multiple system levels including communications from programmable application controllers and application-specific controllers to temperature sensors and from network controllers to programmable application controllers and application-specific controllers.

        - Design and install wireless networks to comply with DDC system performance requirements indicated using wireless network devices that can co-exist on same network with hardwired devices.

        - Provide hardwired controllers capable of retrofitting to wireless devices with no special software.

        - Provide a wireless coordinator for wireless interface between programmable application controllers, application-specific controllers, and network controllers.

        - Wireless Coordinators:

          - Use for initiation and formation of each wireless mesh network.

          - Use direct-sequence spread spectrum RF technology.

          - Operate on 2.4 GHz ISM Band.

          - Comply with IEEE 802.15.4 for low-power, low duty-cycle RF transmitting systems.

          - FCC compliant to 47 CFR 15, Subpart B, Class A.

          - Operate as a bidirectional transceiver with sensors and routers to confirm and synchronize data transmission.

          - Capable of communication with sensors and routers up to a maximum distance of 250 ft. (76 m) in line of sight.

          - Include visual indicators to provide diagnostic information required for operator verification of operation.

        - Wireless Routers:

          - Use wireless routers with any controller to provide a wireless interface to a network controller, through a wireless coordinator.

          - Use direct-sequence spread spectrum RF technology.

          - Operate on 2.4 GHz ISM Band.

          - Comply with IEEE 802.15.4 for low-power, low duty-cycle RF transmitting systems.

          - FCC compliant to 47 CFR 15, Subpart B, Class A.

          - Operate as a bidirectional transceiver with other mesh network devices to ensure network integrity.

          - Capable of communication with other mesh network devices at a maximum distance of 250 ft. (76 m) in line of sight.

          - Include indication for use in commissioning and troubleshooting.

        - Wireless Temperature Sensors:

          - Wireless temperature sensors to sense and transmit room temperatures, temperature set point, room occupancy notification, and low battery condition to an associated router.

          - Use direct-sequence spread spectrum RF technology.

          - Operate on 2.4 GHz ISM Band.

          - Comply with IEEE 802.15.4 for low-power, low duty-cycle RF transmitting systems.

          - FCC compliant to 47 CFR 15, Subpart B, Class A.

          - Include set-point adjustment between [55 to 85 deg F (13 to 30 deg C)] <Insert range>.

          - Configure so multiple sensors can report to a router connected to DDC controller for averaging or high and low selection.

        - One-to-One Wireless Network Receivers:

          - One-to-one wireless receivers receive wireless RF signals containing temperature data from multiple wireless room temperature sensors and communicate information to programmable application controllers or application-specific controllers.

            - Use direct-sequence spread spectrum RF technology.

            - Operate on 2.4 GHz ISM Band.

            - Comply with IEEE 802.15.4 for low-power, low duty-cycle RF transmitting systems.

            - FCC compliant to 47 CFR 15, Subpart B, Class A.

            - Operate as a bidirectional transceiver with sensors to confirm and synchronize data transmission.

            - Capable of communication up to a distance of 200 ft. (61 m).

            - Include visual indication of the following:

              - Power.

              - Receiver activity.

              - Wireless RF transmission from wireless sensors.

              - No transmission, weak signal, adequate signal, or excellent signal.

        - One-to-One Wireless Network Sensors:

          - One-to-one wireless sensors sense and report room temperatures to one-to-one receiver.

            - Use direct-sequence spread spectrum RF technology.

            - Operate on 2.4 GHz ISM Band.

            - Comply with IEEE 802.15.4 for low-power, low duty-cycle RF transmitting systems.

            - FCC compliant to 47 CFR 15, Subpart B, Class A.

            - Include set-point adjustment between 55 to 85 deg F (13 to 30 deg C).

      - DESKTOP WORKSTATIONS

Retain this article if desktop workstations are to be included as part of DDC system. Consult Owner to determine if Owner will furnish desktop workstations or if Owner wants desktop workstations provided as part of DDC system.

If multiple desktop workstations having unique requirements are required, copy this article and re-edit for each workstation's requirements.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: A tower or all-in-one computer designed for normal use at a single, semipermanent location.

        - Performance Requirements:

          - May dictate equipment exceeding minimum requirements indicated.

          - ENERGY STAR compliant.

        - Personal Computer:

          - Minimum Processor Speed: <Insert gigahertz>.

          - RAM:

            - Capacity: [8] <Insert value> [GB].

            - Speed and Type: [1333] <Insert value> MHz, <Insert type>.

          - Hard Drive:

            - Media: [Solid state] [Rotating disc, nominal rotational speed of 7200 rpm] [Hybrid solid-state and rotating disc].

            - Number of Hard Drives: [One] [Two] <Insert number>.

            - Capacity: <Insert number and measurement unit>.

            - Minimum Average Seek Time: <Insert number and measurement unit>.

            - Cache Buffer Size: <Insert number and measurement unit>.

            - <Insert requirements>.

          - Second Hard Drive:

            - Media: [Solid state] [Rotating disc, nominal rotational speed of 7200 rpm] [Hybrid solid-state and rotating disc].

            - Capacity: <Insert number and measurement unit>.

            - Minimum Average Seek Time: <Insert number and measurement unit>.

            - Cache Buffer Size: <Insert number and measurement unit>.

            - <Insert requirements>.

          - Optical Read and Write Drive:

            - Include with at least 2 MB of data buffer.

            - Type: <Insert type>.

            - Minimum Data Buffer Capacity: <Insert number and measurement unit>.

            - Minimum Average Access Time: <Insert number> ms.

            - Nominal Data Transfer Rates:

              - Reading: <Insert value> [MB] [TB]/s.

              - Writing: <Insert value> [MB] [TB]/s.

            - Average access time of 150 ms or less.

            - MTBF of at least 100,000 power-on hours.

          - At least four expansion slots of [32] [64] <Insert number> bit.

          - Video Card:

            - Resolution: [1920 by 1200] <Insert values> pixels.

            - RAM: <Insert value> [MB] [GB] [TB].

            - Controller Speed: <Insert value> [MHz] [GHz].

            - On-Board Memory Speed: <Insert value> [MHz] [GHz].

            - On-Board Memory Data Width: <Insert number> bit.

          - Sound Card:

            - At least 128 voice wavetable synthesis.

            - Capable of delivering three-dimensional sound effects.

            - High-resolution, 16-bit stereo digital audio recording and playback with user-selectable sample rates up to 48,000 Hz.

          - Network Interface Card: Include card with connection, as applicable.

            - 10-100-1000 base TX Ethernet with RJ-45 connector port.

            - 100 base FX Ethernet with SC or ST port.

        - Wireless Ethernet, 802.11 ac:

Retain "Optical Modem" Subparagraph below for direct connection to optical fiber cable.

          - Optical Modem: Full duplex link for connection to optical fiber cable provided.

          - I/O Ports:

            - Two USB 3.0 ports on front panel, six on back panel, and three internal on motherboard.

            - One serial port.

            - One parallel port.

            - Two PS/2 ports.

            - One RJ-45.

            - One stereo line-in and headphone/line-out on back panel.

            - One microphone and headphone connector on front panel.

            - One IEEE 1394 on front and back panel with PCI-e card.

            - One ESATA port on back panel.

          - Battery: Life of at least three years to maintain system clock/calendar and ROM, at a minimum.

        - Keyboard:

          - 101 enhanced keyboard.

          - Full upper- and lowercase ASCII keyset, numeric keypad, dedicated cursor control keypad, and 12 programmable function keys.

          - Wireless operation within up to 72 inches (1800 mm) in front of workstation.

        - Pointing Device:

          - Two- or three-button mouse.

          - Wireless operation within up to 72 inches (1800 mm) in front of workstation.

        - Flat Panel Display Monitor:

Copy and re-edit "Display" Subparagraph below if requirements are different for multiple displays.

          - Display:

            - Color display with <Insert inches (mm)> diagonal viewable area.

            - [Digital] [or] [analog] input signal.

            - Aspect Ratio: [16 to 9] <Insert value>.

            - Antiglare display.

            - Response Time: <Insert number> ms.

            - Dynamic Contrast Ratio: [50000 to 1] <Insert ratio>.

            - Brightness: [250 cd/sq. m] <Insert value>.

            - Tilt adjustable base.

            - ENERGY STAR compliant.

            - Resolution: [1920 by 1080] <Insert value> pixels at 60 Hz with pixel size of [0.277] <Insert number> mm or smaller.

            - Number of Displays: [One] [Two] <Insert number>.

        - Speakers:

          - Two, with individual controls for volume, bass and treble.

          - Signal to Noise Ratio: At least 65 dB.

          - Power: At least 4 W per speaker/channel.

          - Magnetic shielding to prevent distortion on the video monitor.

        - I/O Cabling: Include applicable cabling to connect I/O devices.

      - PORTABLE WORKSTATIONS

Retain this article if portable workstations are to be included as part of DDC system. Consult Owner to determine if Owner will furnish operators with portable workstations.

If multiple portable workstations having unique requirements are required, copy this article and re-edit to specify requirements for each workstation.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: A self-contained computer designed to allow for normal use in different locations and conditions.

        - Performance Requirements:

          - Performance requirements may dictate equipment exceeding minimum requirements indicated.

          - ENERGY STAR compliant.

          - Hardware and software to support local downloading to DDC controllers.

          - Data transfer rate to DDC controller is to be at network speed.

        - Processor:

          - Minimum Processor Speed: <Insert gigahertz>.

          - RAM:

            - Capacity: <Insert value> [GB] [TB].

            - Speed and Type: <Insert value> MHz, <Insert type>.

Copy and re-edit "Hard Drive" Subparagraph below if requirements are different for multiple hard drives.

          - Hard Drive:

            - Number of Hard Drives: [One] [Two] <Insert number>.

            - Capacity: <Insert number and measurement unit>.

            - Minimum Average Seek Time: <Insert number and measurement unit>.

            - Cache Buffer Size: <Insert number and measurement unit>.

            - <Insert requirements>.

          - Video Card: <Insert number and measurement unit> of RAM.

        - I/O Ports:

          - Serial port.

          - Shared port for external keyboard or mouse.

          - Four USB 3.0 ports.

          - Ethernet port.

          - HDMI port.

          - IEEE 1394 port.

        - Battery:

          - Capable of supporting operation of portable workstation for a minimum of [8] <Insert number> hours.

          - Battery life of at least three years.

          - Battery charge time of less than three hours.

          - Spare Battery(ies): [One] [Two].

        - Keyboard:

          - 85-key [backlit ]keyboard.

          - Full upper- and lowercase ASCII keyset.

        - Integral Pointing Device: Touchpad with two buttons. Gesture enabled.

        - Display:

          - <Insert inches (mm)> diagonal or larger high-definition WLED color display.

          - Antiglare screen.

          - [1920 by 1080] <Insert value> pixel resolution.

          - Brightness: 300 nits.

        - Network Interfaces:

          - Network Interface Card: Include card with connection, as application.

            - 10-100-1000 base TX Ethernet with RJ-45 connector port.

            - 100 base FX Ethernet with SC or ST port.

          - Wireless:

            - Internal with integrated antenna, capable of supporting WiFi standards 802.11 a/b/g/n.

        - Digital Video Disc Rewrite Recorder (DVD+/-RW):

          - Compatible with DVD discs and data, audio, recordable, and rewritable compact discs.

          - Nominal Data Transfer Rates:

            - Reading: <Insert number> [MB] [TB]/s.

            - Writing: <Insert number> [MB] [TB]/s.

          - 160-ms access time.

        - Accessories:

Retain any of first eight subparagraphs below.

          - Nylon carrying case.

          - Docking station.

          - Mobile broadband card.

          - Wireless optical mouse.

          - <Insert value> [GB] [TB] portable hard drive.

          - Light-sensitive web cam and noise-cancelling digital array microphone.

          - Category 6a patch cable. Minimum cable length is to be <Insert length>.

          - HDMI cable. Minimum cable length is to be <Insert length>.

          - <Insert accessories>.

      - PORTABLE OPERATOR TERMINALS

        - Description: Handheld device with integral keypad or touch screen operator interface.

        - Display: Multiple lines of text display for use in operator interaction with DDC system.

        - Cable: Flexible [coiling ]cable, at least 36 inches (900 mm) long, with a plug-in jack for connection to DDC controllers, network ports, or instruments with an integral LAN port. As an alternative to hardwired connection, POTs may be accessible to DDC controllers through a wireless network connection.

        - Power POTs through network connection.

        - Connection of POTs to DDC system to not interrupt or interfere with normal network operation in any way, prevent alarms from being transmitted, or preclude central initiated commands and system modification.

        - POTs to give operator ability to do the following:

Subparagraphs below are examples only.

          - Display and monitor BI point status.

          - Change BO point set point (on or off, open or closed).

          - Display and monitor analog point values.

          - Change analog control set points.

          - Command a setting of AO point.

          - Display and monitor I/O point in alarm.

          - Add a new or delete an existing I/O point.

          - Enable and disable I/O points, initiators, and programs.

          - Display and change time and date.

          - Display and change time schedules.

          - Display and change run-time counters and run-time limits.

          - Display and change time and event initiation.

          - Display and change control application and DDC parameters.

          - Display and change programmable offset values.

          - Access DDC controller initialization routines and diagnostics.

          - <Insert requirements>.

      - SERVERS

Retain this article for DDC systems with data storage requirements that exceed the available storage of operator workstations and controllers.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: x86-based permanently installed computer used for client-server computing.

        - Mounting: [Rack] [Blade] [Tower] [Tower able to be rack mounted].

        - Power: [Single] [Dual] power supply, minimum [300] <Insert value> W.

        - Performance Requirements:

          - Performance requirements may dictate equipment exceeding minimum requirements indicated.

          - ENERGY STAR compliant.

          - Minimum Processor Speed: <Insert gigahertz>.

          - RAM:

            - Capacity: <Insert value> [GB] [TB].

            - Speed and Type: <Insert value> MGz, <Insert type>.

            - Expandable Capacity: <Insert value> [GB] [TB].

See the Evaluations for discussion of redundant array of independent discs levels.

          - Redundant Array of Independent Discs: [Zero] [One] [Two] [Three] [Four] [Five] <Insert number> configuration.

          - Drive Bays: Eight at 2.5 inches (65 mm) or eight at 3.5 inches (90 mm).

          - Hard-Drive Storage: [Two] [Three] [Four] drives each with <Insert value> [GB] [TB] storage and nominal rotational speed of 7200 rpm.

          - Network Interface: [Dual-port gigabit Ethernet] [Optical fiber].

          - DVD +RW drive.

          - Color, flat-screen display with <Insert inches (mm)> diagonal viewable area.

          - Keyboard and mouse.

          - Next-day on-site warranty for [two] [three] <Insert number>-year period following Substantial Completion.

        - Servers are to include the following:

          - Full-feature backup server (server and backup minimum requirement).

          - Software licenses.

          - Cable installation between server(s) and network.

        - Web Server:

          - If required to be separate, include web server hardware and software to match, except backup server is not required.

          - Firewalls between server web and networks.

          - Password protection for access to server from web server.

          - Cable installation between the server(s) and building Ethernet network.

        - Power each server through a [dedicated ]UPS unit.

      - PRINTERS

Retain this article if printers are to be included as part of DDC system. Consult Owner to determine if Owner will furnish printers.

        - Black and White Laser Printer:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - [1200 by 1200] <Insert value> dots per inch resolution.

          - First sheet printed within 10 seconds.

          - <Insert number> page per minute rated print speed at best quality mode.

          - Print buffer with at least <Insert value> MB of RAM, expandable to at least 288 MBs.

          - Complies with ENERGY STAR requirements.

          - Capable of handling letter- and legal-size paper and overhead transparencies.

          - Two paper trays; one tray with <Insert number> sheet capacity, and one tray with <Insert number> sheet capacity.

          - At least <Insert number> page toner/cartridge capacity.

        - Color Laser Printer:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - [1200 by 1200] <Insert value> dots per inch resolution black and white, [1200 by 1200] <Insert value> dots per inch resolution black and white and color.

          - First sheet printed within 10 seconds.

          - <Insert number> page per minute rated print speed at best quality mode.

          - Print buffer with at least [512] <Insert value> MB of RAM, expandable to at least [one] <Insert value> GB.

          - Complies with ENERGY STAR requirements.

          - Capable of handling letter- and legal-size paper and overhead transparencies.

          - Two paper trays; one tray with <Insert number> sheet capacity, and one tray with 500 <Insert number> sheet capacity.

          - Two-sided printing.

          - At least <Insert number> page toner/cartridge capacity.

        - Color Inkjet Printer:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Inkjet technology with true four-color printing (black, cyan, magenta, and yellow).

          - Print quality of [1200 by 600] <Insert value> dots per inch with black on inkjet paper and [4800 by 1200] <Insert value> dots per inch color printing on premium photo paper.

          - Rated speed of <Insert number> pages per minute printing black and white in normal mode and <Insert number> pages per minute printing color in normal mode.

          - Two paper trays; one tray with <Insert number> sheet capacity, and one tray with <Insert number> sheet capacity.

          - Capable of handling letter- and legal-size paper and overhead transparencies.

          - <Insert value> MB of RAM.

          - Duplex printing (printing on both sides of paper).

        - Dot Matrix Printer:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Letter-quality, wide-carriage, 24-pin dot matrix printer.

          - <Insert number> kb print buffer.

          - Minimum Print Speed:

            - <Insert number> characters per second (draft).

            - <Insert number> characters per second (letter quality).

          - [Seven] <Insert number> print fonts.

          - Continuous - forms feed with manual single sheet feed.

          - Capable of handling 16-inch- (400-mm-) wide continuous-feed paper.

      - SYSTEM SOFTWARE

        - System Software Minimum Requirements:

          - Real-time multitasking and multiuser [32-] [or] [64-]bit operating system that allows concurrent multiple operator workstations operating and concurrent execution of multiple real-time programs and custom program development.

          - Operating system capable of operating DOS and Microsoft Windows applications.

          - Database management software to manage all data on an integrated and non-redundant basis. Additions and deletions to database are to be without detriment to existing data. Include cross linkages so no data required by a program can be deleted by an operator until that data have been deleted from respective programs.

          - Network communications software to manage and control multiple network communications to provide exchange of global information and execution of global programs.

          - Operator interface software to include day-to-day operator transaction processing, alarm and report handling, operator privilege level and data segregation control, custom programming, and online data modification capability.

          - Scheduling software to schedule centrally based time and event, temporary, and exception day programs.

        - Operator Interface Software:

          - Minimize operator training through use of English language prorating and English language point identification.

          - Minimize use of a typewriter-style keyboard through use of a pointing device similar to a mouse.

          - Make operator sign-off a manual operation or, if no keyboard or mouse activity takes place, an automatic sign-off.

          - Make automatic sign-off period programmable from one to 60 minutes in one-minute increments on a per operator basis.

          - Record operator sign-on and sign-off activity and send to printer.

          - Security Access:

            - Use password control for operator access to DDC system.

            - Assign an alphanumeric password (field assignable) to each operator.

            - Grant operators access to DDC system by entry of proper password.

            - Use same operator password regardless of which computer or other operator interface means are used.

            - Automatically update additions or changes made to passwords.

            - Assign each operator an access level to restrict access to data and functions the operator is cable of performing.

            - Provide software with at least five access levels.

            - Assign each menu item an access level so that a one-for-one correspondence between operator assigned access level(s) and menu item access level(s) is required to gain access to menu item.

            - Display menu items to operator with those capable of access highlighted. Make menu and operator access level assignments online programmable and under password control.

          - Data Segregation:

            - Include data segregation for control of specific data routed to a workstation, to an operator or to a specific output device, such as a printer.

            - Include at least [32] <Insert number> segregation groups.

            - Make segregation groups selectable such as "fire points," "fire points on second floor," "space temperature points," "HVAC points," and so on.

            - Make points assignable to multiple segregation groups. Display and output of data to printer or monitor is to occur where there is a match of operator or peripheral segregation group assignment and point segregations.

            - Make alarms displayed and printed at each peripheral to which segregation allows, but only those operators assigned to peripheral and having proper authorization level will be allowed to acknowledge alarms.

            - Assign operators and peripherals to multiple segregation groups and make all assignments online programmable and under password control.

          - Operators able to perform commands including, but not limited to, the following:

            - Start or stop selected equipment.

            - Adjust set points.

            - Add, modify, and delete time programming.

            - Enable and disable process execution.

            - Lock and unlock alarm reporting for each point.

            - Enable and disable totalization for each point.

            - Enable and disable trending for each point.

            - Override control loop set points.

            - Enter temporary override schedules.

            - Define holiday schedules.

            - Change time and date.

            - Enter and modify analog alarm limits.

            - Enter and modify analog warning limits.

            - View limits.

            - Enable and disable demand limiting.

            - Enable and disable duty cycle.

            - Display logic programming for each control sequence.

            - <Insert requirements>.

          - Reporting:

            - Generated automatically and manually.

            - Sent to displays, printers and disc files.

            - Types of Reporting:

              - General listing of points.

              - List points currently in alarm.

              - List of off-line points.

              - List points currently in override status.

              - List of disabled points.

              - List points currently locked out.

              - List of items defined in a "Follow-Up" file.

              - List weekly schedules.

              - List holiday programming.

              - List of limits and deadbands.

              - <Insert types>.

          - Summaries: For specific points, for a logical point group, for an operator selected group(s), or for entire system without restriction due to hardware configuration.

        - Graphic Interface Software:

          - Include a full interactive graphical selection means of accessing and displaying system data to operator. Include at least five levels with the penetration path operator assignable (for example, site, building, floor, air-handling unit, and supply temperature loop). Native language descriptors assigned to menu items are to be operator defined and modifiable under password control.

          - Include a hierarchical-linked dynamic graphic operator interface for accessing and displaying system data and commanding and modifying equipment operation. Interface is to use a pointing device with pull-down or penetrating menus, color, and animation to facilitate operator understanding of system.

          - Include at least 10 levels of graphic penetration with the hierarchy operator assignable.

          - Make descriptors for graphics, points, alarms, and such modifiable through operator's workstation under password control.

          - Make graphic displays online user definable and modifiable using the hardware and software provided.

          - Make data displayed within a graphic assignable regardless of physical hardware address, communication, or point type.

          - Make graphics online programmable and under password control.

          - Make points assignable to multiple graphics where necessary to facilitate operator understanding of system operation.

          - Graphics to also contain software points.

          - Penetration within a graphic hierarchy is to display each graphic name as graphics are selected to facilitate operator understanding.

          - Provide a back-trace feature to permit operator to move upward in the hierarchy using a pointing device. Back trace to show all previous penetration levels. Include operator with option of showing each graphic full-screen size with back trace as horizontal header or by showing a "stack" of graphics, each with a back trace.

          - Display operator accessed data on the monitor.

          - Provide operator with ability to select further penetration using pointing device to click on a site, building, floor, area, equipment, and so on. Display defined and linked graphic below that selection.

          - Include operator with means to directly access graphics without going through penetration path.

          - Make dynamic data assignable to graphics.

          - Display points (physical and software) with dynamic data provided by DDC system with appropriate text descriptors, status or value, and engineering unit.

          - Use color, rotation, or other highly visible means, to denote status and alarm states. Make colors variable for each class of points, as chosen by operator.

          - Provide dynamic points with operator adjustable update rates on a per point basis from [one] <Insert value> second to over a [minute] <Insert value>.

          - For operators with appropriate privilege, command points directly from display using pointing device.

            - For an analog command point such as set point, display current conditions and limits so operator can position new set point using pointing device.

            - For a digital command point such as valve position, show valve in current state such as open or closed so operator could select alternative position using pointing device.

            - Include a keyboard equivalent for those operators with that preference.

          - Give operator ability to split or resize viewing screen into quadrants to show one graphic on one quadrant of screen and other graphics or spreadsheet, bar chart, word processing, curve plot, and other information on other quadrants on screen. This feature allows real-time monitoring of one part of system while displaying other parts of system or data to better facilitate overall system operation.

          - Help Features:

            - Online context-sensitive help utility to facilitate operator training and understanding.

            - Bridge to further explanation of selected keywords and contain text and graphics to clarify system operation.

              - If help feature does not have ability to bridge on keywords for more information, provide a complete set of user manuals in an indexed word-processing program, which runs concurrently with operating system software.

            - Available for Every Menu Item:

              - Index items for each system menu item.

          - Provide graphic generation software to allow operator ability to add, modify, or delete system graphic displays.

            - Include libraries of symbols depicting HVAC symbols such as fans, coils, filters, dampers, valves pumps, and electrical symbols[ similar to those indicated].

            - Use a pointing device in conjunction with a drawing program to allow operator to perform the following:

              - Define background screens.

              - Define connecting lines and curves.

              - Locate, orient, and size descriptive text.

              - Define and display colors for all elements.

              - Establish correlation between symbols or text and associated system points or other displays.

        - Project-Specific Graphics: Graphics documentation including, but not limited to, the following:

First two subparagraphs below are examples only.

          - Site plan showing each building, and additional site elements, which are being controlled or monitored by DDC system.

          - Plan for each building floor, including interstitial floors, and each roof level of each building, showing the following:

First four subparagraphs below are examples only.

            - Room layouts with room identification and name.

            - Locations and identification of all monitored and controlled HVAC equipment and other equipment being monitored and controlled by DDC system.

            - Location and identification of each hardware point being controlled or monitored by DDC system.

            - <Insert requirements>.

          - Control schematic for each of following, including a graphic system schematic representation[, similar to that indicated on Drawings,] with point identification, set point and dynamic value indication[, sequence of operation] [and] [control logic diagram].

          - Graphic display for each piece of equipment connected to DDC system through a data communications link. Include dynamic indication of all points associated with equipment.

          - DDC system network riser diagram that shows schematic layout for entire system including all networks and all controllers, [gateways] [operator workstations] [and] [other network devices].

        - Customizing Software:

          - Software to modify and tailor DDC system to specific and unique requirements of equipment installed, to programs implemented and to staffing and operational practices planned.

          - Online modification of DDC system configuration, program parameters, and database using menu selection and keyboard entry of data into preformatted display templates.

          - At a minimum, include the following modification capability:

            - Operator Assignment: Designation of operator passwords, access levels, point segregation, and auto sign-off.

            - Peripheral Assignment: Assignment of segregation groups and operators to consoles and printers, designation of backup workstations and printers, designation of workstation header points, and enabling and disabling of printout of operator changes.

            - System Configuration and Diagnostics: Communications and peripheral port assignments, DDC controller assignments to network, DDC controller enable and disable, assignment of command trace to points, and application programs and initiation of diagnostics.

            - System Text Addition and Change: English or native language descriptors for points, segregation groups and access levels and action messages for alarms, run time, and trouble condition.

            - Time and Schedule Change: Time and date set, time and occupancy schedules, exception and holiday schedules, and daylight-savings time schedules.

            - Point related change capability is to include the following:

              - System and point enable and disable.

              - Run-time enable and disable.

              - Assignment of points to segregation groups, calibration tables, lockout, and run time and to a fixed I/O value.

              - Assignment of alarm and warning limits.

            - Application program change capability is to include the following:

              - Enable and disable of software programs.

              - Programming changes.

              - Assignment of comfort limits, global points, time and event initiators, time and event schedules and enable and disable time and event programs.

          - Provide software to allow operator ability to add points, or groups of points, to DDC system and to link them to energy optimization and management programs. Make additions and modifications online programmable using operator workstations, downloaded to other network devices and entered into their databases. After verification of point additions and associated program operation, upload and record database on hard drive and disc for archived record.

          - Include high-level language programming software capability for implementation of custom DDC programs. Include a compiler, linker, and up- and down-load capability.

          - Include a library of DDC algorithms, intrinsic control operators, arithmetic, logic, and relational operators for implementation of control sequences. Also include, at a minimum, the following:

            - Proportional control (P).

            - Proportional plus integral (PI).

            - Proportional plus integral plus derivative (PID).

            - Adaptive and intelligent self-learning control.

              - Algorithm monitors loop response to output corrections and adjust loop response characteristics in accordance with time constant changes imposed.

              - Algorithm operates in a continuous self-learning manner and retains in memory a stored record of system dynamics so that on system shut down and restart, learning process starts from where it left off.

          - Fully implemented intrinsic control operators including sequence, reversing, ratio, time delay, time of day, highest select AO, lowest select AO, analog controlled digital output, analog control AO, and digitally controlled AO.

          - Logic operators such as "And," "Or," "Not," and others that are part of a standard set available with a high-level language.

          - Arithmetic operators such as "Add," "Subtract," "Multiply," "Divide," and others that are part of a standard set available with a high-level language.

          - Relational operators such as "Equal to," "Not Equal to," "Less Than," "Greater Than," and others that are part of a standard set available with a high-level language.

        - Alarm Handling Software:

          - Include alarm handling software to report all alarm conditions monitored and transmitted through DDC controllers[, gateways] [and other network devices].

          - Include first in, first out handling of alarms in accordance with alarm priority ranking, with most critical alarms first, and with buffer storage in case of simultaneous and multiple alarms.

          - Make alarm handling active at all times to ensure that alarms are processed even if an operator is not currently signed on to DDC system.

          - Alarms display is to include the following:

            - Indication of alarm condition such as "Abnormal Off," "Hi Alarm," and "Low Alarm."

            - "Analog Value" or "Status" group and point identification with native language point descriptor such as "Space Temperature, Building 110, 2nd Floor, Room 212."

            - Discrete per point alarm action message, such as "Call Maintenance Dept. Ext-5561."

            - Include extended message capability to allow assignment and printing of extended action messages. Capability is to be operator programmable and assignable on a per point basis.

          - Direct alarms to appropriate operator workstations, printers, and individual operators by privilege level and segregation assignments.

          - Send email alarm messages to designated operators.

          - Send email, page, text, and voice messages to designated operators for critical alarms.

          - Categorize and process alarms by class.

            - Class 1:

              - Associated with fire, security, and other extremely critical equipment monitoring functions; have alarm, trouble, return to normal, and acknowledge conditions printed and displayed.

              - Unacknowledged alarms to be placed in unacknowledged alarm buffer.

              - All conditions make an audible alarm sound and require individual acknowledgment to silence audible sound.

            - Class 2:

              - Critical, but not life-safety related, and processed same as Class 1 alarms, except do not require individual acknowledgment.

              - Acknowledgement may be through a multiple alarm acknowledgment.

            - Class 3:

              - General alarms; printed, displayed, and placed in unacknowledged alarm buffer queues.

              - Configure so each new alarm received makes an audible alarm sound that are silenced by "acknowledging" alarm or by pressing a "silence" key.

              - Make acknowledgement of queued alarms either on an individual basis or through a multiple alarm acknowledgement.

              - Print alarms returning to normal condition without an audible alarm sound or require acknowledgment.

            - Class 4:

              - Routine maintenance or other types of warning alarms.

              - Alarms to be printed only, with no display, no audible sound and no acknowledgment required.

          - Include an unacknowledged alarm indicator on display to alert operator that there are unacknowledged alarms in system. Operator able to acknowledge alarms on an individual basis or through a multiple alarm acknowledge key, depending on alarm class.

          - To ensure that no alarm records are lost, make it possible to assign a backup printer to accept alarms in case of failure of primary printer.

        - Reports and Logs:

          - Include reporting software package that allows operator to select, modify, or create reports using DDC system I/O point data available.

          - Setup each report so data content, format, interval, and date are operator definable.

          - Sample and store report data on DDC controller, within storage limits of DDC controller, and then uploaded to archive on [workstation] [server] for historical reporting.

          - Make it possible for operators to obtain real-time logs of all I/O points by type or status, such as alarm, point lockout, or normal.

          - Store reports and logs on [workstations] [and] [servers] hard drives in a format that is readily accessible by other standard software applications, including spreadsheets and word processing.

          - Make reports and logs readily printable and set to be print either on operator command or at a specific time each day.

        - Standard Reports: Provide standard DDC system reports with operator ability to customize reports later.

          - All I/O: With current status and values.

          - Alarm: All current alarms, except those in alarm lockout.

          - Disabled I/O: All I/O points that are disabled.

          - Alarm Lockout I/O: All I/O points in alarm lockout, whether manual or automatic.

          - Alarm Lockout I/O in Alarm: All I/O in alarm lockout that are currently in alarm.

          - Logs:

            - Alarm history.

            - System messages.

            - System events.

            - Trends.

            - <Insert requirement>.

        - Custom Reports: Operator able to easily define and prepare any system data into a daily, weekly, monthly, annual, or other historical report. Reports to include a title with time and date stamp.

Retain "Tenant Override Reports" Paragraph below if required to report individual tenant use of above building standard HVAC operation.

        - Tenant Override Reports: Prepare Project-specific reports.

          - Daily report showing total time in hours that each tenant has requested after-hours HVAC.

          - Weekly report showing daily total time in hours that each tenant has requested after-hours HVAC.

          - Monthly report showing daily total time in hours that each tenant has requested after-hours HVAC.

          - Annual summary report that shows after-hours HVAC usage on a monthly basis.

Retain "HVAC Equipment Reports" Paragraph below to require Project-specific HVAC equipment reports to be prepared by a DDC system installer.

        - HVAC Equipment Reports: Prepare Project-specific reports.

          - Chiller Report: Daily report showing operating conditions of each chiller in accordance with ASHRAE 147 including, but not limited to, the following:

Revise subparagraphs below to suit Project. Include DDC system with instruments required to provide information indicated.

            - Chilled-water entering temperature.

            - Chilled-water leaving temperature.

            - Chilled-water flow rate.

            - Chilled-water inlet and outlet pressures.

            - Evaporator refrigerant pressure and temperature.

            - Condenser refrigerant pressure and liquid temperature.

            - Condenser-water entering temperature.

            - Condenser-water leaving temperature.

            - Condenser-water flow rate.

            - Refrigerant levels.

            - Oil pressure and temperature.

            - Oil level.

            - Compressor refrigerant discharge temperature.

            - Compressor refrigerant suction temperature.

            - Addition of refrigerant.

            - Addition of oil.

            - Vibration levels or observation that vibration is not excessive.

            - Motor amperes per phase.

            - Motor volts per phase.

            - Refrigerant monitor level (PPM).

            - Purge exhaust time or discharge count.

            - Ambient temperature (dry bulb and wet bulb).

            - Date and time logged.

            - <Insert requirement>.

          - <Insert requirements for each type of HVAC equipment requiring a report>.

Retain "Utility Reports" Paragraph below to require Project-specific utility reports to be prepared by a DDC system installer.

        - Utility Reports: Prepare Project-specific reports.

Revise subparagraphs below to suit Project. Include DDC system with instruments required to provide reports indicated.

          - Electric Report:

            - Include weekly report showing daily electrical consumption and peak electrical demand with time and date stamp for each meter.

            - Include monthly report showing the daily electrical consumption and peak electrical demand with time and date stamp for each meter.

            - Include annual report showing monthly electrical consumption and peak electrical demand with time and date stamp for each meter.

            - For each weekly, monthly, and annual report, include sum total of submeters combined by load type, such as lighting, receptacles, and HVAC equipment showing daily electrical consumption and peak electrical demand.

            - For each weekly, monthly, and annual report, include sum total of all submeters in building showing electrical consumption and peak electrical demand.

          - Natural Gas Report:

            - Include weekly, monthly, and annual report showing daily natural gas consumption and peak natural gas demand with time and date stamp for each meter.

            - For each weekly, monthly, and annual report, include sum total of submeters combined by load type, such as boilers and service water heaters showing daily natural gas consumption and peak natural gas demand.

            - For each weekly, monthly, and annual report, include sum total of all submeters in building showing natural gas consumption and peak natural gas demand.

          - Service Water Report:

            - Include weekly, monthly, and annual report showing daily service water consumption and peak service water demand with time and date stamp for each meter.

            - For each weekly, monthly, and annual report, include sum total of submeters combined by load type, such as cooling tower makeup and irrigation showing daily service water consumption and peak service water demand.

            - For each weekly, monthly. and annual report, include sum total of all submeters in building showing service water consumption and peak service water demand.

          - <Insert requirements for each utility requiring a report>.

Retain "Energy Reports" Paragraph below for projects with emphasis on energy performance.

        - Energy Reports: Prepare Project-specific daily, weekly, monthly, [and annual] [, annual and since-installed] energy reports.

Revise subparagraphs below to suit Project.

          - Prepare report for each purchased energy utility, indicating the following:

            - Time being reported with beginning and end date, and time indicated.

            - Consumption in units of measure commonly used to report specific utility consumption over time.

            - Gross area served by utility.

            - Consumption per unit area served using utility-specific unit of measure.

            - Cost per utility unit.

            - Utility cost per unit area.

            - Convert all utilities to a common energy consumption unit of measure and report for each utility.

            - Consumption per unit area using common unit of measure.

Retain first subparagraph below to report renewable energy.

          - Prepare report for each renewable energy source, indicating the following:

            - Time being reported with beginning and end date, and time indicated.

            - Harvested energy in units of measure commonly used to report specific harvested energy consumption over time.

            - Gross area served by renewable energy source.

            - Harvested energy per unit area served using specific unit of measure.

            - Cost per purchased utility unit displaced by renewable energy.

            - Cost savings attributed to harvested energy source.

            - Cost savings per unit area attributed to harvested energy.

            - Convert all renewable energy sources to a common energy consumption unit of measure and report for each.

            - Harvested energy per unit area using common unit of measure.

Retain first subparagraph below to report energy by submetered areas.

          - Prepare purchased energy utility report for each submetered area that indicates the following:

            - Time being reported with beginning and end date, and time indicated.

            - Gross area served.

            - Energy consumption by energy utility type.

            - Energy consumption per unit area by energy utility type.

            - Total energy consumption of all utilities in common units of measure.

            - Total energy consumption of all utilities in common units of measure per unit area.

            - Unit energy cost by energy utility type.

            - Energy cost by energy utility type.

            - Energy cost per unit area by energy utility type.

            - Total cost of all energy utilities.

            - Total cost of all energy utilities per unit area.

          - Prepare Project total purchased energy utility report that combines all purchased energy utilities and all areas served. Project total energy report is to indicate the following:

            - Time being reported with beginning and end date, and time indicated.

            - Gross area served.

            - Energy consumption by energy utility type.

            - Energy consumption per unit area by energy utility type.

            - Total energy consumption of all utilities in common units of measure.

            - Total energy consumption of all utilities in common units of measure per unit area.

            - Unit energy cost by energy utility type.

            - Energy cost by energy utility type.

            - Energy cost per unit area by energy utility type.

            - Total cost of all energy utilities.

            - Total cost of all energy utilities per unit area.

Retain "HVAC System Efficiency Reports" Paragraph below for projects with emphasis on energy performance.

        - HVAC System Efficiency Reports: Prepare Project-specific [daily] [weekly] [monthly] [and annual] [, annual and since-installed] HVAC system efficiency reports.

Revise subparagraphs below to suit Project.

          - Prepare report for [each ]chilled-water system, indicating the following:

            - Time being reported with beginning and end date, and time indicated.

            - Cooling energy supplied during period.

            - Power energy consumed during period by cooling equipment used to produce cooling energy supplied.[ List power consumed for each individual piece of equipment in system and summed total of all equipment in system.]

            - Energy efficiency coefficient of performance determined by dividing power energy consumed into cooling energy supplied.

            - Energy efficiency determined by dividing cooling energy supplied into power energy consumed.

            - Units of measure used in report to be consistent with units indicated for system.

          - Prepare report for [each ]heating hot-water system, indicating the following:

            - Time being reported with beginning and end date, and time indicated.

            - Heating energy supplied during period.

            - Fuel consumed during period by boilers used to produce heating energy supplied.[ List fuel consumed for each individual piece of equipment in system and summed total of all equipment in system.]

            - Energy efficiency determined by dividing heating energy supplied into fuel energy consumed.

            - Units of measure used in report are to be consistent with units indicated for system.

          - Prepare report for [each ]steam system, indicating the following:

            - Time being reported with beginning and end date, and time indicated.

            - Heating energy supplied during period.

            - Fuel consumed during period by boilers used to produce heating energy supplied.[ List fuel consumed for each individual piece of equipment in system and summed total of all equipment in system.]

            - Energy efficiency determined by dividing heating energy supplied into fuel energy consumed.

            - Units of measure used in report are to be consistent with units indicated for system.

          - <Insert requirements for each HVAC system requiring a report>.

Retain "Weather Reports" Paragraph below to require Project-specific weather reports to be prepared by a DDC system installer.

        - Weather Reports:

Revise subparagraphs below to suit Project. Include DDC system with instruments required to provide reports indicated.

          - Include daily report showing the following:

            - Daily minimum, maximum, and average outdoor dry-bulb temperature.

            - Daily minimum, maximum, and average outdoor wet-bulb temperature.

            - Daily minimum, maximum, and average outdoor dew point temperature.

            - Number of heating degree-days for each day calculated from a base temperature of [55 deg F (13 deg C)] <Insert temperature>.

            - Number of cooling degree-days for each day calculated from a base temperature of [65 deg F (18 deg C)] <Insert temperature>.

            - Daily minimum, maximum, and average outdoor carbon dioxide level.

            - Daily minimum, maximum, and average relative humidity.

            - Daily minimum, maximum, and average barometric pressure.

            - Daily minimum, maximum, and average wind speed and direction.

          - Include weekly report showing the following:

            - Daily minimum, maximum, and average outdoor dry-bulb temperature.

            - Daily minimum, maximum, and average outdoor wet-bulb temperature.

            - Daily minimum, maximum, and average outdoor dew point temperature.

            - Number of heating degree-days for each day calculated from a base temperature of [55 deg F (13 deg C)] <Insert temperature>.

            - Number of cooling degree-days for each day calculated from a base temperature of [65 deg F (18 deg C)] <Insert temperature>.

            - Weekly minimum, maximum, and average outdoor carbon dioxide level.

            - Daily minimum, maximum, and average relative humidity.

            - Daily minimum, maximum, and average barometric pressure.

            - Daily minimum, maximum, and average wind speed and direction.

          - Include monthly report showing the following:

            - Daily minimum, maximum, and average outdoor dry-bulb temperature.

            - Daily minimum, maximum, and average outdoor wet-bulb temperature.

            - Daily minimum, maximum, and average outdoor dew point temperature.

            - Number of heating degree-days for each day calculated from a base temperature of [55 deg F (13 deg C)] <Insert temperature>.

            - Number of cooling degree-days for each day calculated from a base temperature of [65 deg F (18 deg C)] <Insert temperature>.

            - Monthly minimum, maximum, and average outdoor carbon dioxide level.

            - Daily minimum, maximum, and average relative humidity.

            - Daily minimum, maximum, and average barometric pressure.

            - Daily minimum, maximum, and average wind speed and direction.

          - Include annual (12-month) report showing the following:

            - Monthly minimum, maximum, and average outdoor dry-bulb temperature.

            - Monthly minimum, maximum, and average outdoor wet-bulb temperature.

            - Monthly minimum, maximum, and average outdoor dew point temperature.

            - Number of heating degree-days for each month calculated from a base temperature of [55 deg F (13 deg C)] <Insert temperature>.

            - Number of cooling degree-days for each month calculated from a base temperature of [65 deg F (18 deg C)] <Insert temperature>.

            - Annual minimum, maximum, and average outdoor carbon dioxide level.

            - Monthly minimum, maximum, and average relative humidity.

            - Daily minimum, maximum, and average barometric pressure.

            - Daily minimum, maximum, and average wind speed and direction.

        - Standard Trends:

          - Trend all I/O point present values, set points, and other parameters indicated for trending.

          - Associate trends into groups, and setup a trend report for each group.

          - Store trends within DDC controller and uploaded to hard drives automatically on reaching [75] <Insert number> percent of DDC controller buffer limit, or by operator request, or by archiving time schedule.

          - Preset trend intervals for each I/O point after review with Owner.

          - Make trend intervals operator selectable from 10 seconds up to 60 minutes. Make minimum number of consecutive trend values stored at one time 100 per variable.

          - When drive storage memory is full, overwrite oldest data with most recent data.

          - Make archived and real-time trend data available for viewing numerically and graphically by operators.

        - Custom Trends: Operator-definable custom trend log for any I/O point in DDC system.

          - Include each trend with interval, start time, and stop time.

          - Sample and store data on DDC controller, within reaching [75] <Insert number> percent storage limits of DDC controller, and then uploaded to archive on [workstation] [server] hard drives.

          - Make data retrievable for use in spreadsheets and standard database programs.

        - Programming Software:

          - Include programming software to execute sequences of operation indicated.

          - Include programming routines in simple and easy to follow logic with detailed text comments describing what the logic does and how it corresponds to sequence of operation.

Retain "as follows" option in first subparagraph below to limit the type of programming software to a specific type. Retain "any of the following" option to allow choice to use any programming type. Retain "one of the following" option to allow choice to allow use of just one of multiple programming types indicated. Revise subparagraphs to limit programming options.

          - Programming Software: [As follows] [Any of the following] [One of the following]:

Graphic-based programming is the easiest method of programming options indicated and best suited for operators with limited programming experience. Not all DDC system manufacturers offer graphic-based programming. Consult manufacturers.

            - Graphic Based: Use a library of function blocks made from preprogrammed code designed for DDC control systems.

              - Assemble function blocks with interconnection lines that represent to control sequence in a flowchart.

              - Make programming tools viewable in real time to show present values and logical results of each function block.

            - Menu Based: Done by entering parameters, definitions, conditions, requirements, and constraints.

            - Line by Line and Text Based: Programming is to declare variable types such as local, global, real, integer, and so on, at the beginning of the program. Use descriptive comments frequently to describe programming code.

          - Include means for detecting programming errors and testing software control strategies with a simulation tool before implementing in actual control. Simulation tool may be inherent with programming software or as a separate product.

Retain "Database Management Software" Paragraph below for DDC systems with database requirements that use SQL. Coordinate with other DDC system database requirements indicated.

        - Database Management Software:

          - Where a separate SQL database is used for information storage, include database management software that separates database monitoring and managing functions by supporting multiple separate windows.

          - Secure database access using standard SQL authentication including ability to access data for use outside of DDC system applications.

          - Include database management function summarizing information on trend, alarm, event, and audit for the following database management actions:

            - Backup.

            - Purge.

            - Restore.

          - Database management software supporting the following:

            - Statistics: Display database server information and trend, alarm, event, and audit information on database.

            - Maintenance: Include method of purging records from trend, alarm, event, and audit databases by supporting separate screens for creating a backup before purging, selecting database, and allowing for retention of a selected number of day's data.

            - Backup: Include means to create a database backup file and select a storage location.

            - Restore: Include a restricted means of restoring a database by requiring operator to have proper security level.

          - Information of current database activity, including the following:

            - Ready.

            - Purging record from a database.

            - Action failed.

            - Refreshing statistics.

            - Restoring database.

            - Shrinking a database.

            - Backing up a database.

            - Resetting Internet information services.

            - Starting network device manager.

            - Shutting down the network device manager.

            - Action successful.

          - Database management software monitoring functions is to continuously read database information once operator has logged on.

          - Include operator notification through on-screen pop-up display and email message when database value has exceeded a warning or alarm limit.

          - Monitoring settings window with the following Sections:

            - Allow operator to set and review scan intervals and start times.

            - Email: Allow operator to create and review email and phone text messages to be delivered when a warning or an alarm is generated.

            - Warning: Allow operator to define warning limit parameters, set reminder frequency, and link email message.

            - Alarm: Allow operator to define alarm limit parameters, set reminder frequency, and link email message.

            - Database Login: Protect system from unauthorized database manipulation by creating a read access and a write access for each of trend, alarm, event, and audit databases as well as operator proper security access to restore a database.

          - Monitoring settings taskbar with following informational icons:

            - Normal: Indicates by color and size, or other easily identifiable means, that all databases are within their limits.

            - Warning: Indicates by color and size, or other easily identifiable means, that one or more databases have exceeded their warning limit.

            - Alarm: Indicates by color and size, or other easily identifiable means, that one or more databases have exceeded their alarm limit.

      - ANALYTICS SOFTWARE

Retain this article for Project requiring analytics. Consult Owner to discuss need for analytics software and specific requirements.

        - Scope: Incorporate analytics software into DDC System:

Retain "Licensing, without Recurring Cost" or "Licensing" Subparagraph below, or both.

          - Licensing, without Recurring Cost: No re-occurring cost for licensing and subscriptions.

          - Licensing: With or without re-occurring cost for licensing and subscriptions.

            - For products with re-occurring costs, provide incremental costs broken down over a [five] [10] <Insert value>-year operating period that begins at Substantial Completion.

            - Setup service agreements direct to Owner.

          - Purpose: Analyze energy and operational data to identify faults and opportunities for improved performance and reduced energy use.

          - Verification: Verify that HVAC systems and associated sequence of operations are executing as specified or as described on Drawings, through the analysis of energy and operational data, identification of faults showing where control sequences are not functioning as prescribed, and identification of opportunities for improved performance in the operation of systems.

        - Use during Project Life:

          - During Construction: Use for verification of performance during startup, commissioning, and final acceptance of DDC system.

          - During Warranty Period: Use for continuous operational tuning of DDC system and verification of operation and designed to identify warranty issues preemptively, thus reducing failures and potential down time.

          - After Warranty Period: Use to diagnose ongoing operational degradation and for Owner to perform continuous monitoring-based commissioning.

        - Minimum Features and Capabilities:

          - Operating Systems: Current version of Windows-based operating systems.

          - Time Series Database: Database technology, designed for efficient storage and analysis of large volumes of time series data, using tagging to model and describe data; supports an open-source tagging standard.

          - Data Import: Ability to accept and normalize data from a variety of sources including SQL compatible databases, CSV format files, XML format files or web services, and other EDI techniques. Once imported, software is to provide a unified data format to enable analytics algorithms to identify patterns across different data sets.

          - Open Interfaces: Open, REST-based APIs to enable integration with third-party software applications. Open APIs are to enable data to be entered/imported into database, exported from database, posting of analytic queries, and output of analytic results. APIs are to be fully documented and available as part of standard product.

          - Host: Local deployed on DDC system network.

          - Weather Data Service: Built-in worldwide weather service providing weather data including, but not limited to, the following:

            - Current temperature.

            - High temperature for the day.

            - Low temperature for the day.

            - Sunrise and sunset times.

            - Relative humidity.

            - Degree days (heating and cooling with adjustable balance point value).

            - Seven-day forecast.

            - Historical weather data extending back at least one year.

          - Email Notification: Automatic notification of detected issues via email including, but not limited to, the following:

            - Immediate notification of detected issues.

            - Daily digest or summary of detected issues.

            - Ability to delineate which notifications are sent to which recipients down to the level of specifying individual issues sent to individual recipients.

        - Hardware Requirements:

          - Host on a server in a virtual environment complying with Owner's security requirements.

          - Comply with standard software and hardware profiles required by Owner.

        - Analytic Rules:

          - Custom Rule Development: Develop customized rules and algorithms tailored to operational needs and characteristics of individual facilities and needs of monitoring and verification project and fault-detection requirements of Project without depending on manufacturer for rule development. Provide tools for user development and full documentation.

          - Standard Analytic Functions: Library of standard analytic functions is to use these standard analytic functions as elements to build custom analytic rules for specific needs of individual facilities.

          - Existing library of not less than 200 standard analytic rules written for applications similar to those required for this Project.

        - Reporting:

          - Standard Views of Analytic Results: Standard views to present analytic results, automatically generated when issues are found by analytic rules including, but not limited to, the following:

            - Rules violations across a portfolio of sites, rules violations per site, including time, date, and duration of all violations.

            - Ability to assign cost relationships to rule logic to provide cost per violation.

            - Standard filters to enable operator to easily look at rule violations by site, data, and violation type for any selected date or date range.

            - Automatic calculation and presentation of Key Performance Indicators (KPIs) and to define custom KPIs as needed.

          - Custom Views of Analytic Results:

            - Any standard system view is to be able to be saved as a custom report including its configuration criteria, e.g., time range, sites, rule violations, or other configuration options as applicable to standard system view.

            - Created by making queries against the database and saving the query as a saved report executed by single mouse click.

            - Export: Support report views export into CSV, Excel, XML, and HTML format, accomplished in a couple of mouse clicks.

        - Energy-Specific Reporting and Information Presentation Tools:

          - Greenhouse Gas Analysis: Energy/carbon dioxide relationships; easily changed and added without involvement of software manufacturer.

          - Energy Baseline: Quantify and define energy consumption and demand baselines (including weather normalization metrics) and compare actual and forecasted energy demand and consumption against those baselines.

          - Benchmarking: Multisite benchmarking to compare energy consumption and demand profiles and baselines across all buildings within Owner's portfolio.

          - Forecasting: Forecast near-future loads by using historic trends and forecasted weather data.

          - Financial Analysis: Calculate costs based on energy consumption and demand and energy costs and associate costs with any faults discovered by any analytic function and perform model- or tariff-based calculations to determine costs.

          - Tracking of Key Performance Indicators: Definition and tracking of user-defined key performance indicators/operational metrics. Examples include energy demand and consumption normalized for area and weather, peak demand, and consumption shown with minimum and maximum ranges across any user-selectable period.

          - Correlation of Energy Use with Equipment Operation: Automatically present views showing correlation between energy demand and consumption and operation of loads associated with that usage. Include the following:

            - All submeters and virtual meters.

            - Weather data as a selectable item.

        - Implementation:

          - Apply analytic rules to all HVAC systems and equipment monitored and controlled by DDC system. To extent available, use a subset of rules in existing rules library.

          - Implement rules to aid in determining proper operation of any HVAC system with a programmed sequence of operation.

          - Generate reports to aid in verification of proper operation during initial system startup and commissioning to supplement (not replace) commissioning agent reports.

          - Prepare quarterly reports summarizing faults detected and KPIs, including recommended corrective action.

        - Training:

          - Train Owner sufficiently to use software without need for external support.

      - MAINTENANCE MANAGEMENT SOFTWARE

Retain this article for Project with rigorous requirements for maintenance management. Consult Owner to discuss requirements for maintenance.

        - Scope:

          - Include complete and functional software-driven maintenance management system to perform scheduling of preventive maintenance and generation of work orders, for mechanical and electrical equipment and systems, and other equipment and systems indicated.

          - Automatically generate work orders from alarm conditions, run time, and calendar time. For each work order generated, list parts, tools, and craftspeople and define task to be performed.

          - Use work orders generated to schedule a repair or preventive maintenance routine.

          - Use work orders to track completion of work, parts used, and total cost of repair.

          - Include a database inventory tracking system to automatically update inventory database to show quantity of tools, repair parts, and expendables used for a work order.

          - Print work orders and preventive maintenance schedules[ on a printer assigned solely to maintenance management function].

        - Additional Hardware Requirements:

          - Maintenance management software is to not require additional hardware[, except for an additional printer that is dedicated to maintenance management].

        - Integration: Integrate maintenance management software into DDC system.

        - Software Requirements:

          - From main menu of maintenance management system, use selection of icons to penetrate to individual functions described below.

          - Work Orders:

            - Automatically generate work orders initiated from alarm conditions, accumulated run time, or calendar time. Work orders generated are to specify a particular task to be accomplished including labor, material, and tools needed to accomplish work.

            - Include at least two of the following types of work orders:

              - Corrective and Emergency Maintenance: Generate for a specific job or repair for emergency, breakdown, or scheduled work.

              - Preventive Maintenance: Use on a periodic basis to generate preventive maintenance work orders.

            - Include the following functions:

              - Work Order Tracking: Perform every function related to processing work orders including creating, approving and initiating work orders, checking their status history, and closing or reworking them when appropriate.

              - Work Requests: Report any problems that require corrective maintenance activity generated by dispatchers and those people designated to request work orders.

              - Quick Reporting: Report work done on an open work order or a small job.

              - Work Manager: Specify type of labor to be applied to a specific work order at specific times. Include capability to dispatch one or more laborers to top-priority jobs on as-needed basis and to interrupt work in progress to reassign labor to higher priority tasks.

            - Reports:

              - Daily Maintenance Schedule by Supervisor: List a schedule of open work orders for a specified date by supervisor.

              - Equipment Cost Roll-up Report: Include a roll-up of equipment costs incurred since the date the report was last run.

              - Delinquent Work Order Report: List open work orders whose target completion date is earlier than the date the report is run.

              - Employee Job Assignments: List labor codes that have job assignments for specified date.

              - Daily Work Order Assignment: List work orders that have labor assignments for specified date.

              - Estimated versus Actual Work Order Costs: List a cost summary of outstanding work orders.

              - Open Work Orders Report: List open work orders for locations and equipment.

          - Inventory:

            - Include an inventory tracking system to keep track of stocked, non-stocked, and special-order items.

            - Link inventory tracking to database and when items are consumed, as noted on a work order issued by system, and automatically update inventory of stocked items.

            - Include the following functions:

              - Inventory Control: Enter, display, and update information on each inventory item. Allow viewing of master inventory records that are independent of storeroom locations or item/location records. Include a screen that lists inventory transactions that move items in or out of inventory or from one storeroom location to another. Minimum information tracked is to include the following:

                - Vendors supply items.

                - Item balances, including the bin and lot level for each storeroom location.

                - Alternative items.

              - Issues and Transfers: Issue stock directly from inventory, with or without a work order. When transfer of stock from one location to another location occurs, provide appropriate adjustments in stock balance record. Include a trace record of stock transfers from one storeroom to another.

              - Item Assembly Structures: Include modeling of equipment with inventory items and building of equipment and location hierarchies.

              - Metered Material Usage:

                - Track usage by a piece of equipment.

                - Record against a standing work order for a selected piece of equipment.

                - Include a material usage transaction for each item of material used and provide as an input to calculation for per unit material consumption report for a piece of equipment.

            - Reports:

              - Inventory Analysis Report: List for a given storeroom location, inventory items analysis information that allows quick identification of which inventory items represent greatest monetary investment for dollar value and rate of turnover.

              - Inventory Cycle Count Report: List for a specified storeroom, inventory items that are due to be cycle-counted, based on cycle-count frequency and last count date.

              - Economic Order Quantity Report: For a given storeroom location, display optimum economic ordering quantity for items in selected results set.

              - Inventory Pick Report: A pick list, by work order for items needed to be pulled from a designated storeroom's inventory for work orders having a target start date of specified date.

              - Suggested Order Report: List inventory items in selected results set that are due to be recorded, for a specified storeroom location, based on the following calculation: Suggest a reorder if current balance minus reserve quantity plus on-order quantity is less than reorder point.

              - Reorder Point Report: List selected set of items and optimum minimum level to have in stock based on demand, lead delivery time, and a reserve safety stock.

              - Inventory Valuation Report: Gives an accounting of cost of current inventory, for inventory records in a designated storeroom location.

              - Item Order Status: Lists items on order.

              - List of Expired Items: Lists expired lot items in a storeroom. Report is to include item number, description, expiration date, bin number, lot number, manufacturer lot number, and quantity of expired items in that lot and bin.

              - Item Availability at All Locations: Lists alternative storeroom locations for selected items.

              - Where Used Report: List equipment on which item is recorded as being used.

          - Equipment:

            - Include equipment and location records; establish relationships between equipment, between locations, and between equipment and locations; track maintenance costs; and enter and review meter readings.

            - Include the following functions:

              - Equipment: Store equipment numbers and corresponding information including equipment class, location, vendor, up/down status, and maintenance costs for each piece of equipment. Include building of equipment assemblies. Provide equipment assemblies hierarchical ordering for arrangement of buildings, departments, equipment, and sub-assemblies.

              - Operating Locations: Facilitate creation of records for operating locations of equipment, and track equipment that is used in multiple locations. In addition, allow hierarchical organization of equipment operating in facility by means of grouping equipment locations into areas of responsibility.

              - Failure Codes: Develop and display failure hierarchies to acquire an accurate history of types of failures that affect equipment and operating locations.

              - Condition Monitoring: Display time-related or limit measurements recorded for a piece of equipment. Generate work orders from this screen and to take immediate action on problem conditions.

            - Reports:

              - Availability Statistic by Location: List equipment availability by location over a user-specified period.

              - Equipment Failure Summary: List total number of failures by problem code for a piece of equipment for specified period.

              - Detailed Equipment Failure Report by Equipment: List of failure reports for the current piece of equipment for specified period.

              - Equipment Hierarchy Report: List of equipment.

              - Equipment History Graphs: Include a graphical report in histogram format that displays equipment breakdown history over a specified period.

              - Equipment Measurement Report: Tabular listing and description of each measurement point for a piece of equipment and history of measurements taken for that point.

              - Maintenance Cost by Equipment: List of transactions costs for elected equipment in the specified date range.

              - Failure Count by Equipment: Graphically report number of failures for each piece of equipment showing number of failures for each piece of equipment over a specified period, occurrence of each problem code within set of failures, and failures by problem code.

              - Failure Analysis Graphs: Graphically report number of failures for each piece of equipment over a specified period, number of occurrences of each problem code within set of failures, and failures by problem code.

              - Failure Code Hierarchy Report: List of failure codes in each level of failure hierarchy.

              - Location Failure Summary: A summary for each selected location of failures reported and any hierarchy level locations for specified period.

              - Failure Summary by Location: A summary of failures for selected location and their subordinate locations that are part of hierarchical system.

              - Detailed Failure Report by Location: List all failures for selected location and its subordinate locations that are part of hierarchical system.

              - Maintenance Cost by System: List of total costs reported in a given date range for locations in selected hierarchical system.

              - Location Hierarchy Report: Lists member locations of hierarchical system displayed in hierarchical fashion.

          - Purchasing:

            - Include preparation and generation of purchase requisitions and purchase orders; to report receipt of both items and services, match invoices with purchase orders and receipts and define and convert foreign currencies.

            - Include the following functions:

              - Purchase Requisition: Create and process purchase requisitions for items and services.

              - Purchase Orders: Create and process purchase orders for items and services from scratch or from purchase requisitions. Record receipts of items and services.

              - Invoices: Include functionality to match purchase orders with invoices and receipts. It is also possible to match a service receipt to an invoice. Project for entering of an invoice for bills that do not require purchase orders or receipts.

              - Currency Management: Define currencies and specify exchange rates. Include preparation of purchase requisitions and purchase orders in currency of vendor while tracking costs in systems base currency.

            - Reports:

              - Invoice Approval Report: Include an approval form for entered invoices.

              - Inventory Receipts Register: List purchase orders and inventory received for user-specified time frame.

              - Direct Purchase Back-Order Report: List of items ordered as a direct purchase not received by required delivery date.

              - Standard Purchase Order: A printing of primary purchase order with vendors shipping information, and items purchased.

              - Purchase Order Status Report: List of purchase orders whose status has changed during a certain period.

              - Standard Purchase Requisition: A printing of primary purchase requisition, including vendor name and shipping information.

          - Job Plans:

            - Include creation of a detailed description of work to be performed by work order. Job plan is to contain operations, procedures and list of estimated material, labor, and tools required for work.

          - Labor:

            - Store information on employees, contractors, and crafts and include the following functions:

              - Labor: Create, modify, and view employee records. Employee records are to contain pay rate, overtime worked, overtime refused, specials skills, and certifications.

              - Crafts: Create, modify, and view craftspeople records.

              - Labor Reporting: Report labor usage by employee or craft externally from work orders module.

            - Reports:

              - Employee Attendance Analysis: List of planned attendance, actual attendance, and vacation and sick time in hours as a percentage of planned attendance for selected employees for specified period.

              - Labor Productivity Analysis: List of actual labor hours by labor report category showing each by percentage.

              - Labor Availability versus Commitments by Crafts: A graphical report that details available labor hours versus committed work order hours by craft and day.

          - Calendars:

            - Establish calendar records indicating working time for equipment, location, craft, and labor records.

          - Resources:

            - Include entry and retrieval of data associated with resources required to maintain facility and to include the following functions:

              - Companies: Establish and update data on vendors and other companies.

              - Tools: Create and maintain information on the tools used on jobs. Make information contained within this module available to job plans and work orders.

              - Service Contracts: Specify information on service contracts with vendors or manufacturers.

          - Custom Applications:

            - Include creation of customized database tables and application screens that supplement functions specified.

          - Setup:

            - Include configuration of database, security, and setup applications.

            - Perform the following functions:

              - Reports and Other Applications: Register reports and other applications for use within system.

              - Documents: Enter, track, and link information from Drawings to equipment and inventory items.

              - Chart of Accounts: Add or modify accounts; set up financial periods; enter inventory accounts, company accounts, and resource recovery accounts; and define tax codes and rates.

              - Signature Security: Establish each user's access rights to modules, applications, screens, and options.

              - Database Configuration: Customize database, including adjusting field lengths and modifying data types.

              - Application Setup: Change position of icons and menu items on the main menu screen.

              - Application Launching: Allow for connecting of third-party applications to data fields and push buttons.

          - Utilities:

            - Include utilities module that allows system administrator to customize system and to maintain database.

            - Include the following functions:

              - Interactive SQL: Include access to database for database management functions of import/export and backup.

              - Edit Windows: Display a dialog box to customize an application.

              - Archive Data: Remove records from database and store them for future reference.

        - Documentation:

          - Include complete documentation for system consisting of a User Manual and Systems Administrator Guide.

          - Describe how to use each application module and screen with step-by-step instructions detailing entry and retrieval of data for functions specified.

          - Include a step-by-step description of how each report is defined and retrieved.

          - Bind documentation and clearly title it indicating volume number and use.

      - OFFICE APPLICATION SOFTWARE

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Include current version of office application software at time of Substantial Completion.

        - Office application software package to include multiple separate applications and use a common platform for all applications.

Retain any of first six subparagraphs below. Consult Owner.

          - Database.

          - Email.

          - Presentation.

          - Publishing.

          - Spreadsheet.

          - Word processing.

          - <Insert application>.

      - ASHRAE 135 GATEWAYS

Retain this article for DDC systems using ASHRAE 135 protocol.

Gateways require a thorough understanding of their application. Use caution when connecting non-BACnet to BACnet protocol. It may be more practical to select products that are already "BACnet ready." Research gateway manufacturers for price, options, and performance. Design for each gateway should include an interoperability schedule showing each point or event on non-BACnet side that BACnet "client" will read, and each parameter that BACnet network will write to for BACnet services, or BIBBs, defined in ASHRAE 135, Annex K.

        - Include BACnet communication ports, whenever available as an equipment OEM standard option, for integration via a single communication cable. BACnet-controlled plant equipment includes, but is not limited to, boilers, chillers, <Insert equipment,> and variable-speed drives.

        - Include gateways to connect BACnet to legacy systems where indicated, existing non-BACnet devices, and existing non-BACnet DDC-controlled equipment.

        - Include with each gateway an interoperability schedule showing each point or event on legacy side that BACnet "client" will read, and each parameter that BACnet network will write to. Describe this interoperability of BACnet services, or BIBBs, defined in ASHRAE 135, Annex K.

        - Gateway Minimum Requirements:

          - Read and view all readable object properties on non-BACnet network to BACnet network, and vice versa, where applicable.

          - Write to all writable object properties on non-BACnet network from BACnet network, and vice versa, where applicable.

          - Include single-pass (only one protocol to BACnet without intermediary protocols) translation from non-BACnet protocol to BACnet, and vice versa.

          - Comply with requirements of Data Sharing Read Property, Data Sharing Write Property, Device Management Dynamic Device Binding-B, and Device Management Communication Control BIBBs in accordance with ASHRAE 135.

          - Hardware, software, software licenses, and configuration tools for operator-to-gateway communications.

          - Backup programming and parameters on CD media with ability to modify, download, backup, and restore gateway configuration.

      - ASHRAE 135 PROTOCOL ANALYZER

Retain this article for DDC systems using ASHRAE 135 protocol.

Retain protocol analyzer after consulting Owner and confirming operators require it, because it takes a moderate level of skill and knowledge to use.

Protocol analyzer is typically software for connecting a computer to any ASHRAE 135 network for use in gathering basic system information. It is most useful for integration projects with poorly documented systems and where different manufacturers' products reside on same network.

        - Analyzer and required cables and fittings for connection to ASHRAE 135 network.

        - Include the following minimum capabilities:

          - Capture and store to a file data traffic on all network levels.

          - Measure bandwidth usage.

          - Filtering options with ability to ignore select traffic.

      - CTA-709.1-D NETWORK HARDWARE

Retain this article for DDC systems using LON protocol.

        - Routers:

          - Network routers, including routers configured as repeaters, are to comply with requirements of CTA-709.1-D and include connection between two or more CTA-709.3 TP/FT-10 channels or between two or more CTA-709.3 TP/FT-10 channels and a TP/XF-1250 channel.

          - IP Routers:

            - Perform layer three routing of CTA-709.1-D packets over an IP network in accordance with CTA-852-C.

            - Include appropriate connection to IP network and connections to CTA-709.3 TP/FT-10 or TP/XF-1250 network.

            - Support the Dynamic Host Configuration Protocol for IP configuration and use of an CTA-852-C Configuration Server (for CTA-852-C configuration), but do not rely on these services for configuration.

            - Capable of manual configuration via a console RS-232 port.

        - Gateways:

          - Perform bidirectional protocol translation from one non-CTA-709.1-D protocol to CTA-709.1-D.

          - Incorporate a network connection to TP/FT-10 network in accordance with CTA-709.3 and a connection for non-CTA-709.1-D network.

      - WIRELESS ROUTERS FOR OPERATOR INTERFACE

If wireless routers are required, retain dual-band or tri-band router type, or both. If retaining both types, indicate on Drawings or in an application article describing application of each type on Project.

        - Dual-Band Wireless Routers:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: High-speed, dual-band router with integral Ethernet ports and USB port.

          - Technology: IEEE 802.11; 2.4 and 5 GHz speed bands.

          - Wireless Speed: Up to [300] <Insert number> Mbps on 2.4 GHz band and up to [2400] <Insert number> Mbps on 5 GHz band.

          - Compatibility: IEEE 802.11 ac wireless devices.

          - Ethernet Ports: Four, gigabit (1000 Mbps).

          - USB Port: One, USB 2.0 or 3.0.

          - Wireless Security: Wi-Fi Protected Access (WPA) and WPA2 in accordance with IEEE 802.11.

        - Tri-Band Wireless Routers:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: High-speed, tri-band router with integral Ethernet ports and USB port.

          - Technology: IEEE 802.11; 2.4 and 5 GHz speed bands.

          - Wireless Speed: Up to [600] <Insert number> Mbps on 2.4 GHz band and up to [4800] <Insert number> Mbps on two 5 GHz bands.

In first subparagraph below, "ac" is older technology than "ax." However, "ax" technology provides a higher level of performance.

          - Compatibility: IEEE 802.11 [ac] [or] [ax] wireless devices.

          - Ethernet Ports: [Four] <Insert number>, gigabit [1000] [2500] <Insert number> Mbps.

          - USB Port: One, USB 2.0 or 3.0.

          - Wireless Security: Wi-Fi Protected Access (WPA) and WPA2 in accordance with IEEE 802.11.

      - DDC CONTROLLERS

        - DDC system consisting of a combination of network controllers, programmable application controllers, and application-specific controllers to satisfy performance requirements indicated.

        - DDC controllers to perform monitoring, control, energy optimization, and other requirements indicated.

        - DDC controllers are to use a multitasking, multiuser, real-time digital control microprocessor with a distributed network database and intelligence.

        - Each DDC controller is capable of full and complete operation as a completely independent unit and as a part of DDC system wide distributed network.

        - Environment Requirements:

          - Controller hardware suitable for anticipated ambient conditions.

          - Controllers located in conditioned space rated for operation at [32 to 120 deg F (0 to 50 deg C)] <Insert temperature range>.

          - Controllers located outdoors rated for operation at [40 to 150 deg F (4 to 65 deg C)] <Insert temperature range>.

        - Power and Noise Immunity:

          - Operate controller at 90 to 110 percent of nominal voltage rating and perform an orderly shutdown below 80 percent of nominal voltage.

          - Protect against electrical noise of 5 to 120 Hz and from keyed radios with up to 5 W of power located within 36 inches (900 mm) of enclosure.

Retain "DDC Controller Spare Processing Capacity" Paragraph below to require spare processing capacity for future growth.

        - DDC Controller Spare Processing Capacity:

          - Include spare processing memory for each controller. RAM, PROM, or EEPROM will implement requirements indicated with the following spare memory:

            - Network Controllers: [50] [60] [70] <Insert number> percent.

            - Programmable Application Controllers: Not less than [60] [70] [80] <Insert number> percent.

            - Application-Specific Controllers: Not less than [70] [80] [90] <Insert number> percent.

          - Memory for DDC controller's operating system and database are to include the following:

            - Monitoring and control.

            - Energy management, operation, and optimization applications.

            - Alarm management.

            - Historical trend data of all connected I/O points.

            - Maintenance applications.

            - Operator interfaces.

            - Monitoring of manual overrides.

Retain "DDC Controller Spare I/O Point Capacity" Paragraph below to require spare point capacity for future growth.

        - DDC Controller Spare I/O Point Capacity: Include spare I/O point capacity for each controller as follows:

          - Network Controllers:

            - [10] [20] <Insert number> percent of each AI, AO, BI, and BO point connected to controller.

            - Minimum Spare I/O Points per Controller:

              - AIs: [Two] [Three] <Insert number>.

              - AOs: [Two] [Three] <Insert number>.

              - BIs: [Three] [Five] <Insert number>.

              - BOs: [Three] [Five] <Insert number>.

Retain first subparagraph below to give option to use universal I/O. Universal I/O point can be used as AI, AO, BI, or BO.

              - Option to provide universal I/O to meet spare requirements.

          - Programmable Application Controllers:

            - [10] [20] <Insert number> percent of each AI, AO, BI, and BO point connected to controller.

            - Minimum Spare I/O Points per Controller:

              - AIs: [Two] [Three] <Insert number>.

              - AOs: [Two] [Three] <Insert number>.

              - BIs: [Three] [Five] <Insert number>.

              - BOs: [Three] [Five] <Insert number>.

Retain first subparagraph below to give option to use universal I/O. Universal I/O point can be used as AI, AO, BI, or BO.

              - Option to provide universal I/O to meet spare requirements.

          - Application-Specific Controllers:

            - [10] <Insert number> percent of each AI, AO, BI, and BO point connected to controller.

            - Minimum Spare I/O Points per Controller:

              - AIs: [One] [Two] <Insert number>.

              - AOs: [One] [Two] <Insert number>.

              - BIs: [One] [Two] <Insert number>.

              - BOs: [One] [Two] <Insert number>.

Retain subparagraph below to give option to use universal I/O. Universal I/O point can be used as AI, AO, BI, or BO.

              - Option to provide universal I/O to meet spare requirements.

        - Maintenance and Support: Include the following features to facilitate maintenance and support:

          - Mount microprocessor components on circuit cards for ease of removal and replacement.

          - Means to quickly and easily disconnect controller from network.

          - Means to quickly and easily access connect to field test equipment.

          - Visual indication that controller electric power is on, of communication fault or trouble, and that controller is receiving and sending signals to network.

        - General Requirements for CTA-709.1-D DDC Controllers:

          - LonMark certified.

          - Distinguishable and accessible switch, button, or pin, when pressed is to broadcast its 48-bit Node ID and Program ID over network.

          - TP/FT-10 transceiver in accordance with CTA-709.3 and connections for TP/FT-10 control network wiring.

          - TP/XF-1250 transceiver in accordance with CTA-709.3 and connections for TP/XF-1250 control network wiring.

          - Communicate using CTA-709.1-D protocol.

          - Controllers configured into subnets, as required, to comply with performance requirements indicated.

          - Network communication through LNS network management and database standard for CTA-709.1-D network devices.

          - Locally powered, not powered through network connection.

          - Functionality required to support applications indicated including, but not limited to, the following:

            - I/Os indicated and as required to support sequence of operation and application in which it is used. SNVTs to have meaningful names identifying the value represented by SNVT. Unless SNVT of an appropriate engineering type is unavailable, all network variables to be of SNVT with engineering units appropriate to value the variable represents.

            - Configurable through SCPTs defined in LonMark SCPT List, operator-defined UCPTs, network configuration inputs (NCIs) of SNVT type defined in LonMark SNVT List, NCIs of an operator-defined network variable type, or hardware settings on controller itself for all settings and parameters used by application in which it is used.

          - Programmable controllers comply with "LonMark Interoperability Guidelines" and have LonMark certification.

        - I/O Point Interface:

          - Connect hardwired I/O points to network, programmable application, and application-specific controllers.

          - Protect I/O points so shorting of point to itself, to another point, or to ground will not damage controller.

          - Protect I/O points from voltage up to 24 V of any duration so that contact will not damage controller.

          - AIs:

            - Include monitoring of low-voltage (0 to 10 V dc), current (4 to 20 mA) and resistance signals from thermistor and RTD sensors.

            - Compatible with, and field configurable to, sensor and transmitters installed.

            - Perform analog-to-digital (A-to-D) conversion with a minimum resolution of [8] [12] <Insert value> bits or better to comply with accuracy requirements indicated.

            - Signal conditioning including transient rejection for each AI.

            - Capable of being individually calibrated for zero and span.

            - Incorporate common-mode noise rejection of at least 50 dB from 0 to 100 Hz for differential inputs, and normal-mode noise rejection of at least 20 dB at 60 Hz from a source impedance of 10000 ohms.

            - External conversion resistors are not permitted.

          - AOs:

            - Perform analog-to-digital (A-to-D) conversion with a minimum resolution of [8] [12] <Insert value> bits or better to comply with accuracy requirements indicated.

            - Output signals range of [4 to 20 mA dc] [or] [0 to 10 V dc] as required to include proper control of output device.

            - Capable of being individually calibrated for zero and span.

            - Drift is to be not greater than 0.4 percent of range per year.

            - External conversion resistors are not permitted.

          - BIs:

            - Accept contact closures and ignore transients of less than 5 ms duration.

            - Isolate and protect against an applied steady-state voltage of up to 180 V ac peak.

            - Include a wetting current of at least 12 mA to be compatible with commonly available control devices and protected against effects of contact bounce and noise.

            - Sense "dry contact" closure without external power (other than that provided by controller) being applied.

            - Pulse accumulation input points complying with all requirements of BIs and accept up to 10 pulses per second for pulse accumulation. Include buffer to totalize pulses. Pulse accumulator is to accept rates of at least 20 pulses per second. Reset the totalized value to zero on operator's command.

          - BOs:

            - Include relay contact closures or triac outputs for momentary and maintained operation of output devices.

              - Relay contact closures to have a minimum duration of 0.1 second and at least 180 V of isolation.

              - Include electromagnetic interference suppression on all output lines to limit transients to non-damaging levels.

              - Minimum contact rating to be 1 A at 24 V ac.

              - Triac outputs to have at least 180 V of isolation and minimum contact rating of 1 A at 24 V ac.

            - Include BOs with two-state operation or a pulsed low-voltage signal for pulse-width modulation control.

            - BOs to be selectable for either normally open or normally closed operation.

            - Include tristate outputs (two coordinated BOs) for control of three-point, floating-type electronic actuators without feedback.

            - Limit use of three-point floating devices to VAV terminal unit control applications[, and other applications indicated on Drawings,] <Insert applications>. Control algorithms to operate actuator to one end of its stroke once every [12] [24] <Insert time> hours for verification of operator tracking.

      - NETWORK CONTROLLERS

        - General:

          - Include adequate number of controllers to achieve performance indicated.

          - Provide one or more independent, standalone, microprocessor-based network controllers to manage global strategies indicated.

          - Include enough memory to support its operating system, database, and programming requirements with spare memory indicated.

          - Share data between networked controllers and other network devices.

          - Operating system of controller to manage I/O communication signals to allow distributed controllers to share real and virtual object information and allow for central monitoring and alarms.

          - Include network controllers with a real-time clock.

          - Controller to continually check status of its processor and memory circuits. If an abnormal operation is detected, controller is to assume a predetermined failure mode and generate an alarm notification.

          - Make controllers fully programmable.

        - Communication:

          - Network controllers communicate with other devices on DDC system [Level 1] <Insert level> network.

          - Network controller to also perform routing if connected to network of programmable application controllers and application-specific controllers.

        - Operator Interface:

          - Equip controllers with a service communications port for connection to [desktop operator's workstation] [portable operator's workstation] [POT] [or] [mobile device].

Retain "Local Keypad and Display" Subparagraph below to require a local keypad and display. Requirement adds cost and is unnecessary for some applications.

          - Local Keypad and Display:

            - Equip controller with local keypad and digital display for interrogating and editing data.

            - Use of keypad and display requires a security password.

        - Serviceability:

          - Equip controller with diagnostic LEDs or other form of local visual indication of power, communication, and processor.

          - Connect wiring and cable connections to field-removable, modular terminal strips or to a termination card connected by a ribbon cable.

          - Maintain Basic Input Output System (BIOS) and programming information in event of power loss for at least [72] [96] <Insert number> hours.

      - PROGRAMMABLE APPLICATION CONTROLLERS

        - General:

          - Include adequate number of controllers to achieve performance indicated.

          - Provide enough memory to support its operating system, database, and programming requirements with spare memory indicated.

          - Share data between networked controllers and other network devices.

          - Include controller with operating system to manage I/O communication signals to allow distributed controllers to share real and virtual object information and allow for central monitoring and alarms.

          - Include controllers [that perform scheduling ]with a real-time clock.

          - Controller is to continually check status of its processor and memory circuits. If an abnormal operation is detected, controller assumes a predetermined failure mode and generates an alarm notification.

          - Fully programmable.

        - Communication:

          - Programmable application controllers are to communicate with other devices on network.

        - Operator Interface:

          - Equip controllers with a service communications port for connection to [desktop operator's workstation] [portable operator's workstation] [POT] [or] [mobile device].

Retain "Local Keypad and Display" Subparagraph below to require a local keypad and display. Requirement adds cost and is unnecessary for some applications.

          - Local Keypad and Display:

            - Equip controller with local keypad and digital display for interrogating and editing data.

            - Protect use of keypad and display by security password.

        - Serviceability:

          - Equip controller with diagnostic LEDs or other form of local visual indication of power, communication, and processor.

          - Connect wiring and cable connections to field-removable, modular terminal strips or to a termination card connected by a ribbon cable.

          - Maintain BIOS and programming information in event of power loss for at least 72 hours.

      - APPLICATION-SPECIFIC CONTROLLERS

        - Description: Microprocessor-based controllers, which through hardware or firmware design are dedicated to control a specific piece of equipment or system. Controllers are not fully user-programmable but are configurable and customizable for operation of equipment they are designed to control.

          - Capable of standalone operation and continued control functions without being connected to network.

          - Share data between networked controllers and other network devices.

        - Communication: Application-specific controllers are to communicate with other application-specific controllers and devices on network, and to programmable application controllers and network controllers.

        - Operator Interface: Equip controllers with a service communications port for connection to [desktop workstation] [portable operator's workstation] [POT] [or] [mobile device].[ Connection is to extend to port on space temperature sensor that is connected to controller.]

        - Serviceability:

          - Equip controller with diagnostic LEDs or other form of local visual indication of power, communication, and processor.

          - Connect wiring and cable connections to field-removable, modular terminal strips or to a termination card connected by a ribbon cable.

          - Use nonvolatile memory and maintain all BIOS and programming information in event of power loss.

      - CONTROLLER SOFTWARE

        - General:

          - Software applications are to reside and operate in controllers. Edit applications through operator workstations[ or mobile devices].

          - Identify I/O points by up to [30] <Insert number>-character point name and up to [16] <Insert number>-character point descriptor. Use same names throughout, including at operator workstations.

          - Execute control functions within controllers using DDC algorithms.

          - Configure controllers to use stored default values to ensure fail-safe operation. Use default values when there is a failure of a connected input instrument or loss of communication of a global point value.

        - Security:

          - Secure operator access using individual security passwords and user names.

          - Passwords restrict operator to points, applications, and system functions as assigned by system manager.

          - Record operator log-on and log-off attempts.

          - Protect from unauthorized use by automatically logging off after last keystroke. Make the delay time operator-definable.

        - Scheduling: Include capability to schedule each point or group of points in system. Each schedule is to consist of the following:

          - Weekly Schedules:

            - Include separate schedules for each day of week.

            - Each schedule should include capability for start, stop, optimal start, optimal stop, and night economizer.

            - Each schedule may consist of up to 10 events.

            - When a group of objects are scheduled together, include capability to adjust start and stop times for each member.

          - Exception Schedules:

            - Include ability for operator to designate any day of the year as an exception schedule.

            - Exception schedules may be defined up to a year in advance. Once an exception schedule is executed, it will be discarded and replaced by regular schedule for that day of week.

          - Holiday Schedules:

            - Include capability for operator to define up to 99 special or holiday schedules.

            - Place schedules on scheduling calendar with ability to repeated each year.

            - Operator able to define length of each holiday period.

        - System Coordination:

          - Include standard application for proper coordination of equipment.

          - Include operator with a method of grouping together equipment based on function and location.

          - Include groups that may be for use in scheduling and other applications.

        - Binary Alarms:

          - Set each binary point to alarm based on operator-specified state.

          - Include capability to automatically and manually disable alarming.

        - Analog Alarms:

          - Provide each analog object with both high and low alarm limits.

          - Include capability to automatically and manually disable alarming.

        - Alarm Reporting:

          - Include ability for operators to determine action to be taken in event of an alarm.

          - Route alarms to appropriate operator workstations based on time and other conditions.

          - Include ability for alarms to start programs, print, be logged in event logs, generate custom messages, and display graphics.

        - Remote Communication:

          - Include ability for system to notify operators by phone message, text message, and email in event of an alarm.

        - Electric Power Demand Limiting:

          - Monitor building or other operator-defined electric power consumption from signals connected to electric power meter or from a watt transducer or current transformer.

          - Predict probable power demand such that action can be taken to prevent exceeding demand limit. When demand prediction exceeds demand limit, action will be taken to reduce loads in a predetermined manner. When demand prediction indicates demand limit will not be exceeded, action will be taken to restore loads in a predetermined manner.

          - Accomplish demand reduction by the following means:

            - Reset air-handling-unit supply temperature set points.

            - Reset space temperature set points.

            - De-energize equipment based on priority.

          - Base demand-limiting parameters, frequency of calculations, time intervals, and other relevant variables on the means by which electric power service provider computes demand charges.

          - Include demand-limiting prediction and control for any individual meter monitored by system or for total of any combination of meters.

          - Include means operator to make the following changes online:

            - Addition and deletion of loads controlled.

            - Changes in demand intervals.

            - Changes in demand limit for meter(s).

            - Maximum shutoff time for equipment.

            - Minimum shutoff time for equipment.

            - Select rotational or sequential shedding and restoring.

            - Shed and restore priority.

          - Include the following information and reports, to be available on an hourly, daily, weekly, monthly, and annual basis:

            - Total electric consumption.

            - Peak demand.

            - Date and time of peak demand.

            - Daily peak demand.

        - Maintenance Management: Monitor equipment status and generate maintenance messages based on operator-designated run-time, starts, and calendar date limits.

        - Sequencing: Include application software based on sequences of operation indicated to properly sequence chillers, boilers, and other applicable HVAC equipment.

        - Control Loops:

          - Support any of the following control loops, as applicable to control required:

            - Two-position (on/off, open/close, slow/fast) control.

            - Proportional control.

            - Proportional plus integral (PI) control.

            - Proportional plus integral plus derivative (PID) control.

              - Include PID algorithms with direct or reverse action and anti-windup.

              - Algorithm to calculate a time-varying analog value used to position an output or stage a series of outputs.

              - Make controlled variable, set point, and PID gains operator-selectable.

            - Adaptive (automatic tuning).

        - Staggered Start: Prevent all controlled equipment from simultaneously restarting after a power outage. Make the order which equipment (or groups of equipment) is started, along with the time delay between starts, operator-selectable.

        - Energy Calculations:

          - Include software to allow instantaneous power or flow rates to be accumulated and converted to energy usage data.

          - Include algorithm that calculates a sliding-window average (rolling average). Make algorithm flexible to allow window intervals to be operator specified (such as 15, 30, or 60 minutes).

          - Include algorithm that calculates a fixed-window average. Use a digital input signal to define start of window period (such as signal from utility meter) to synchronize fixed-window average with that used by utility.

        - Anti-Short Cycling:

          - Protect BO points from short cycling.

          - Feature to allow minimum on-time and off-time to be selected.

        - On and Off Control with Differential:

          - Include algorithm that allows BO to be cycled based on a controlled variable and set point.

          - Use direct- or reverse-acting algorithm and incorporate an adjustable differential.

        - Run-Time Totalization:

          - Include software to totalize run-times for all BI [and BO ]points.

          - Assign a high run-time alarm, if required, by operator.

      - ENCLOSURES

        - General:

          - House each controller and associated control accessories in [single ]enclosure. Enclosure is to serve as central tie-in point for control devices such as switches, transmitters, transducers, power supplies, and transformers.

          - Do not house more than one controller in single enclosure.

          - Include enclosure door with key locking mechanism. Key locks alike for all enclosures and include one pair of keys per enclosure.

Retain first subparagraph below for windows in enclosure doors.

          - Equip doors of enclosures housing controllers and components with analog or digital displays with windows to allow visual observation of displays without opening enclosure door.

Retain one of first two subparagraphs below, or both, to restrict enclosure size.

          - Individual, wall-mounted, single-door enclosures maximum of [36 inches (900 mm)] <Insert dimension> wide and [48 inches (1200 mm)] [60 inches (1500 mm)] <Insert dimension> high.

          - Individual, wall-mounted, double-door enclosures maximum of [60 inches (1500 mm)] <Insert dimension> wide and [36 inches (900 mm)] <Insert dimension> high.

Retain first subparagraph below to allow freestanding enclosures.

          - Freestanding enclosures maximum of [48 inches (1200 mm)] <Insert dimension> wide and [72 inches (1800 mm)] <Insert dimension> high.

          - Include wall-mounted enclosures with brackets suitable for mounting enclosures to wall or freestanding support stand as indicated.

          - Supply each enclosure with complete set of as-built schematics, tubing, and wiring diagrams and product literature located in pocket on inside of door.[ For enclosures with windows, include pocket on bottom of enclosure.]

        - Internal Arrangement:

          - Arrange internal layout of enclosure to group and protect [pneumatic, ]electric, and electronic components associated with controller, but not an integral part of controller.

          - Arrange layout to group similar products together.

          - Include a barrier between line-voltage and low-voltage electrical and electronic products.

          - Factory or shop install products, tubing, cabling, and wiring complying with requirements and standards indicated.

          - Terminate field cable and wire using heavy-duty terminal blocks.

          - Include spare terminals, equal to not less than [10] [20] <Insert number> percent of used terminals.

          - Include spade lugs for stranded cable and wire.

          - Install maximum of two wires on each side of terminal.

          - Include enclosure field electric power supply with toggle-type switch located at entrance inside enclosure to disconnect power.

Retain first subparagraph below for enclosure-mounted receptacle.

          - Include enclosure with line-voltage nominal 20 A GFCI duplex receptacle for service and testing tools. Wire receptacle on hot side of enclosure disconnect switch and include with 5 A circuit breaker.

          - Mount products within enclosure on removable internal panel(s).

          - Include products mounted in enclosures with [engraved, laminated phenolic ]nameplates (black letters on a white background). Nameplates are to have at least 1/4-inch- (6-mm-) high lettering.

          - Route tubing cable and wire located inside enclosure within a raceway with continuous removable cover.

          - Label each end of cable, wire, and tubing in enclosure following an approved identification system that extends from field I/O connection and all intermediate connections throughout length to controller connection.

          - Size enclosure internal panel to include at least [15] [25] <Insert number> percent spare area on face of panel.

        - Environmental Requirements:

          - Evaluate temperature and humidity requirements of each product to be installed within each enclosure.

          - Calculate enclosure internal operating temperature considering heat dissipation of all products installed within enclosure and ambient effects (solar, conduction, and wind) on enclosure.

          - Where required by application, include temperature-controlled electrical heat to maintain inside of enclosure above minimum operating temperature of product with most stringent requirement.

          - Where required by application, include temperature-controlled ventilation fans with filtered louver(s) to maintain inside of enclosure below maximum operating temperature of product with most stringent requirement.

          - Include temperature-controlled cooling within the enclosure for applications where ventilation fans cannot maintain inside temperature of enclosure below maximum operating temperature of product with most stringent requirement.

          - Where required by application, include humidity-controlled electric dehumidifier or cooling to maintain inside of enclosure below maximum relative humidity of product with most stringent requirement and to prevent surface condensation within enclosure.

        - Wall-Mounted, NEMA 250, Type 1:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - NRTL listed in accordance with UL 50 or UL 50E.

          - Construct enclosure of steel, not less than the following:

            - Enclosure Size Less Than 24 Inches (600 mm): [0.053 inch (1.35 mm)] [or] [0.067 inch (1.7 mm)] thick.

            - Enclosure Size 24 Inches (600 mm) and Larger: [0.067 inch (1.7 mm)] [or] [0.093 inch (2.36 mm)] thick.

          - Finish enclosure inside and out with polyester powder coating that is electrostatically applied and then baked to bond to substrate.

            - Exterior Color: [White] [Gray] [Selected by Architect] [Manufacturer's standard] <Insert color>.

            - Interior Color: [White] [Gray] [Manufacturer's standard].

          - Hinged door full size of front face of enclosure and supported using the following:

            - Enclosures Sizes Less Than 36 Inches (900 mm) Tall: Multiple butt hinges.

            - Enclosures Sizes 36 Inches (900 mm) Tall and Larger: Continuous piano hinges.

          - Removable internal panel with [white] [or] [gray] polyester powder coating that is electrostatically applied and then baked to bond to substrate.

            - Size Less Than 24 Inches (600 mm): [Solid] [or] [perforated] steel, 0.053 inch (1.35 mm) thick.

            - Size 24 Inches (600 mm) and Larger: Solid [aluminum, 0.10 inch (3 mm)] [or] [steel, 0.093 inch (2.36 mm)] thick.

          - Internal panel mounting hardware, grounding hardware, and sealing washers.

          - Grounding stud on enclosure body.

          - Thermoplastic pocket on inside of door for record Drawings and Product Data.

        - Wall-Mounted, NEMA 250, Types 4 and 12:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - NRTL listed in accordance with UL 508A.

          - Seam and joints are continuously welded and ground smooth.

          - Where recessed enclosures are indicated, include enclosures with face flange for flush mounting.

          - Externally formed body flange around perimeter of enclosure face for continuous perimeter seamless gasket door seal.

          - Single-door enclosure sizes up to 60 inches tall by 36 inches wide (1500 mm tall by 900 mm wide).

          - Double-door enclosure sizes up to 36 inches tall by 60 inches wide (900 mm tall by 1500 mm wide).

          - Construct enclosure of steel, not less than the following:

            - Size Less Than 24 Inches (600 mm): [0.053 inch (1.35 mm)] [or] [0.067 inch (1.7 mm)] thick.

            - Size 24 Inches (600 mm) and Larger: 0.067 inch (1.7 mm) thick.

          - Finish enclosure with polyester powder coating that is electrostatically applied and then baked to bond to substrate.

            - Exterior Color: [White] [Gray] [Selected by Architect] [Manufacturer's standard] <Insert color>.

            - Interior Color: [White] [Gray] [Manufacturer's standard].

          - Corner-formed door, full size of enclosure face, supported using multiple concealed hinges with easily removable hinge pins.

            - Sizes through 24 Inches (600 mm) Tall: Two hinges.

            - Sizes between 24 Inches (600 mm) through 48 Inches (1200 mm) Tall: Three hinges.

            - Sizes Larger Than 48 Inches (1200 mm) Tall: Four hinges.

          - Double-door enclosures with overlapping door design to include unobstructed full-width access.

            - Single-door enclosures 48 inches (1200 mm) and taller, and all double-door enclosures, with three-point (top, middle and bottom) latch system.

          - Removable internal panel with [white] [or] [gray] polyester powder coating that is electrostatically applied and then baked to bond to substrate.

            - Size Less Than 24 Inches (600 mm): [Solid] [or] [perforated] steel, 0.053 inch (1.35 mm) thick.

            - Size 24 Inches (600 mm) and Larger: Solid [aluminum, 0.10 inch (3 mm)] [or] [steel, 0.093 inch (2.36 mm)] thick.

          - Internal panel mounting studs with hardware, grounding hardware, and sealing washers.

          - Grounding stud on enclosure body.

          - Thermoplastic pocket on inside of door for record Drawings and Product Data.

        - Wall-Mounted, NEMA 250, Type 4X-SS:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - NRTL listed in accordance with UL 508A.

          - Seams and joints are continuously welded and ground smooth.

          - Externally formed body flange around perimeter of enclosure face for continuous perimeter seamless gasket door seal.

          - Construct enclosure of [Type 304] [or] [Type 316L] stainless steel, not less than the following:

            - Size Less Than 24 Inches (600 mm): 0.053 inch (1.35 mm) thick.

            - Size 24 Inches (600 mm) and Larger: 0.067 inch (1.7 mm) thick.

          - Outside body and door of enclosure with brushed No. 4 finish.

Retain one of first two subparagraphs below for door hinge choices.

          - Corner-formed door, full size of enclosure face, supported using multiple concealed hinges with easily removable hinge pins.

            - Sizes through 24 Inches (600 mm) Tall: Two hinges.

            - Sizes between 24 Inches (600 mm) through 48 Inches (1200 mm) Tall: Three hinges.

            - Sizes Larger Than 48 Inches (1200 mm) Tall: Four hinges.

          - Corner-formed door, full size of enclosure face, supported using continuous piano hinge full length of door.

Retain first subparagraph below for upgraded door latching system.

          - Doors fitted with three-point (top, middle, and bottom) latch system with single, heavy-duty, liquidtight, [Type 304] [or] [Type 316L] stainless steel handle with integral locking mechanism.

          - Removable internal panel of 0.093-inch (2.36-mm) stainless steel.

          - Internal panel mounting studs and hardware, grounding hardware, and sealing washers.

          - Install corrosion-resistant polyester vent drain in a stainless steel sleeve at bottom of enclosure.

          - Include enclosure with stainless steel mounting brackets.

        - Freestanding, NEMA 250, Type 1:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - NRTL listed in accordance with UL 508A.

          - Seams and joints are continuously welded and ground smooth.

          - Externally formed body flange around perimeter of enclosure face.

          - Single-door enclosure sizes up to 84 inches tall by 36 inches wide (2100 mm tall by 900 mm wide).

          - Double-door enclosure sizes up to 84 inches tall by 72 inches wide (2100 mm tall by 900 mm wide).

          - Construct enclosure of steel, not less than 0.067 inch (1.7 mm) thick.

          - Finish enclosure with polyester powder coating that is electrostatically applied and then baked to bond to substrate.

            - Exterior Color: [White] [Gray] [Selected by Architect] [Manufacturer's standard] <Insert color>.

            - Interior Color: [White] [Gray] [Manufacturer's standard].

          - Corner-formed flush door, full size of enclosure face, supported using four concealed hinges with easily removable hinge pins.

          - Double-door enclosures with overlapping door design to include unobstructed full-width access.

          - Doors with three-point (top, middle, and bottom) latch system with single heavy-duty handle and integral locking mechanism.

          - Removable back covers.

          - Removable solid steel internal panel, 0.093 inch (2.36 mm) thick, with [white] [or] [gray] polyester powder coating that is electrostatically applied and then baked to bond to substrate.

          - Internal panel mounting studs with hardware, grounding hardware, and sealing washers.

          - Grounding stud on enclosure body.

          - Thermoplastic pocket on inside of door for record Drawings and Product Data.

          - Nominal 4-inch- (100-mm-) tall integral lifting base, not less than 0.123 inch (3.12 mm) thick, with predrilled holes for attachment to mounting surface.

          - Equip each top end of enclosure with lifting tabs, not less than 0.172 inch (4.37 mm) thick, or not less than two lifting eyes.

          - Internal rack-mount shelves and angles, as required by application.

        - Freestanding, NEMA 250, Types 4 and 12:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - NRTL listed in accordance with UL 508A.

          - Seams and joints are continuously welded and ground smooth.

          - Externally formed body flange around perimeter of enclosure face.

          - Type 12 Enclosure Sizes:

            - Single-door enclosure sizes up to 90 inches tall by 36 inches wide (2250 mm tall by 900 mm wide).

            - Double-door enclosure sizes up to 90 inches tall by 72 inches wide (2250 mm tall by 900 mm wide).

          - Type 4 Enclosure Sizes:

            - Single-door enclosure sizes up to 72 inches tall by 36 inches wide (1800 mm tall by 900 mm wide).

            - Double-door enclosure sizes larger than 36 inches (900 mm) wide.

          - Construct enclosure of steel, not less than 0.093 inch (2.36 mm) thick.

          - Finish enclosure with polyester powder coating that is electrostatically applied and then baked to bond to substrate.

            - Exterior Color: [White] [Gray] [Selected by Architect] [Manufacturer's standard] <Insert color>.

            - Interior Color: [White] [Gray] [Manufacturer's standard].

          - Corner-formed door with continuous perimeter oil-resistant gasket supported using continuous piano hinge full length of door.

          - Doors fitted with three-point (top, middle, and bottom) latch system with latching rod rollers and single, heavy-duty, oiltight handle with integral locking mechanism.

          - Removable solid steel internal panel, 0.093 inch (2.36 mm) thick, with [white] [or] [gray] polyester powder coating that is electrostatically applied and then baked to bond to substrate.

          - Internal panel mounting studs with hardware, grounding hardware, and sealing washers.

          - Grounding stud on enclosure body.

          - Thermoplastic pocket on inside of door for record Drawings and Product Data.

          - Equip top of enclosure with no fewer than two lifting eyes.

          - Internal rack-mount shelves and angles, as required by application.

        - Freestanding, NEMA 250, Type 4X-SS:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - NRTL listed in accordance with UL 508A.

          - Seams and joints are continuously welded and ground smooth.

          - Externally formed body flange around perimeter of enclosure face for continuous perimeter seamless gasket door seal.

          - Construct enclosure of [Type 304] [or] [Type 316L] stainless steel, not less than the following:

            - Size Less Than 24 Inches (600 mm): 0.053 inch (1.35 mm) thick.

            - Size 24 Inches (600 mm) and Larger: 0.067 inch (1.7 mm) thick.

          - Outside enclosure and door of enclosure with brushed No. 4 finish.

          - Doors:

            - Single-door enclosure sizes up to 36 inches (900 mm) wide.

            - Double-door enclosure sizes larger than 36 inches (900 mm) wide.

            - Corner-formed door(s) with continuous perimeter oil-resistant gasket, full size of enclosure face, supported using continuous piano hinge full length of door.

            - Doors fitted with three-point (top, middle, and bottom) latch system with single, heavy-duty, liquidtight, [Type 304] [or] [Type 316L] stainless steel handle with integral locking mechanism.

          - Removable internal panel of 0.093-inch (2.36-mm) stainless steel.

          - Internal panel mounting studs and hardware, grounding hardware, and sealing washers.

          - Install corrosion-resistant polyester vent drain in a stainless steel sleeve at bottom of enclosure.

          - Include enclosure with stainless steel mounting brackets.

          - Thermoplastic pocket on inside of door for record Drawings and Product Data.

          - Equip top of enclosure with no fewer than two lifting eyes.

          - Internal rack-mount shelves and angles, as required by application.

        - Accessories:

          - Electric Heater:

            - Aluminum housing with brushed finish.

            - Thermostatic control with adjustable set point from 0 to 100 deg F (minus 18 to 38 deg C).

            - Capacity: 100, 200, 400, and 800 W, as required by application.

            - Fan draws cool air from bottom of enclosure and passes air across thermostat and heating elements before being released into enclosure cavity. Heated air is discharged through the top of heater.

          - Ventilation Fans, Filtered Intake, and Exhaust Grilles:

            - Number and size of fans, filters, and grilles, as required by application.

            - Compact cooling fans engineered for 50,000 hours of continuous operation without lubrication or service.

            - Fans capable of being installed on any surface and in any position within enclosure for spot cooling or air circulation.

            - Thermostatic control with adjustable set point from 32 to 140 deg F (0 to 60 deg C).

            - Airflow Capacity at Zero Pressure:

              - 4-Inch (100-mm) Fan: 100 cfm (47 L/s).

              - 6-Inch (150-mm) Fan: 240 cfm (113 L/s).

              - 10-Inch (250-mm) Fan: 560 cfm (264 L/s).

            - Maximum operating temperature of 158 deg F (70 deg C).

            - 4-inch (100-mm) fan thermally protected and provided with permanently lubricated ball-bearings.

            - 6- and 10-inch (150- and 250-mm) fans with ball-bearing construction and split capacitor motors thermally protected to avoid premature failure.

            - Dynamically balanced impellers molded from polycarbonate material.

            - Fan furnished with power cord and polarized plug for power connection.

            - Fan brackets, finger guards, and mounting hardware provided with fans to complete installation.

            - Removable Intake and Exhaust Grilles: [ABS plastic] [or] [stainless steel], of size to match fan size and suitable for NEMA 250, Types 1 and 12 enclosures.

            - Filters for NEMA 250, Type 1 Enclosures: Washable [foam] [or] [aluminum], of size to match intake grille.

            - Filters for NEMA 250, Type 12 Enclosures: Disposable, of size to match intake grille.

          - Air Conditioner:

            - Electric-powered, self-contained, air-conditioning unit specially designed for electrical enclosures to maintain temperature inside enclosure below ambient temperature outside enclosure.

            - Thermostatic control with adjustable set point from 60 to 120 deg F (16 to 49 deg C).

            - Enclosure side or top mounting with unit capacity, as required by application.

            - Designed for closed-loop cooling with continuous operation in ambient environments up to 125 deg F (52 deg C).

            - HFC refrigerant.

            - Reusable and washable air filter.

            - High-performance, industrial-grade, and high-efficiency fans.

            - Furnished with power cord and polarized plug for power connection.

            - Condensate management system with base pan side drain.

            - Mounting hardware, gaskets, mounting template, and instruction manual furnished with unit.

            - Outdoor units equipped with head pressure control for low ambient operation, compressor heater, coated condenser coil, and thermostat.

          - Thermoelectric Humidifier:

            - ABS plastic enclosure.

            - Capacity of 8 oz. (0.24 L) of water per 24 hours.

            - Built-in drain captures moisture and plastic hose directs moisture to outside enclosure through a drain.

            - Controlled to maintain enclosure relative humidity at adjustable set point.

            - Unit power supply is internally wired to enclosure electrical power source.

          - Framed Fixed Window Kit for NEMA 250, Types 4, 4X, and 12 Enclosures:

            - 0.25-inch- (6-mm-) thick, scratch-resistant acrylic or polycarbonate window mounted in a metal frame matching adjacent door material.

            - Enclosure types, except NEMA 250 Type 1, to have continuous gasket material around perimeter of window and frame to provide watertight seal.

            - Window kit to be factory or shop installed before shipment to Project.

          - Frameless Fixed Window Kit for NEMA 250, Type 1 Enclosures:

            - 0.125-inch- (3-mm-) thick, polycarbonate window mounted in enclosure door material.

            - Window attached to door with screw fasteners and continuous strip of high-strength, double-sided tape around window perimeter.

            - Window kit is factory or shop installed before shipment to Project.

          - Frame Fixed or Hinged Window Kit for NEMA 250, Types 1 and 12 Enclosures:

            - 0.25-inch- (6-mm-) thick, scratch-resistant acrylic or polycarbonate window mounted in a metal frame matching adjacent door material.

            - Enclosure types, except NEMA 250 Type 1, to have continuous gasket material around perimeter of window and frame to provide watertight seal.

            - Window kit to be factory or shop installed before shipment to Project.

          - Bar handle with keyed cylinder lock set.

      - RELAYS

If more than one type of general-purpose relay is required, copy "General-Purpose Relays" Paragraph below and re-edit requirements for each different type. Include an applications article in Part 3 to describe applications for each different type of general-purpose relay specified.

        - General-Purpose Relays:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - NRTL listed.

          - Heavy-duty, electromechanical type; rated for at least [10] <Insert value> A at 250 V ac and 60 Hz.

          - SPDT, DPDT, or three-pole double-throw, as required by control application.

          - Plug-in-style relay with [8-pin octal] [or] [multiblade] plug for DPDT relays and [11-pin octal] [or] [multiblade] plug for three-pole double-throw relays.

          - Construct contacts of silver, silver alloy, or gold.

          - Enclose relay in a [clear transparent ]polycarbonate dust-tight cover.

          - Include LED indication[ and push-to-test button to test manual operation of relay without power on coil].

          - Performance:

            - Mechanical Life: At least [10] <Insert number> million cycles.

            - Electrical Life: At least [100,000] <Insert number> cycles at rated load.

            - Pickup Time: [15] [20] <Insert value> ms or less.

            - Dropout Time: [10] [20] <Insert value> ms or less.

            - Pull-in Voltage: [85] <Insert number> percent of rated voltage.

            - Dropout Voltage: [50] [10] <Insert number> percent of nominal rated voltage.

            - Power Consumption: [2] [5] VA or less.

            - Ambient Operating Temperatures: Minus 40 to 115 deg F (Minus 40 to 46 deg C).

          - Equip relays with coil transient suppression to limit transients to non-damaging levels.

          - Plug each relay into industry-standard, 35 mm DIN rail socket. Plug all relays located in control panels into sockets that are mounted on a DIN rail.

          - Include relay socket with screw terminals. Mold into socket the coincident screw terminal numbers.

If more than one type of multifunction time-delay relay is required, copy "Multifunction Time-Delay Relays" Paragraph below and re-edit requirements for each different type. Include an applications article in Part 3 to describe applications for each different type of multifunction time-delay relay specified.

        - Multifunction Time-Delay Relays:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - NRTL listed.

          - Continuous-duty type, rated for at least [10] <Insert value> A at 240 V ac and 60 Hz.

          - Relay with up to [4] [8] <Insert number> programmable functions to provide on/off delay, interval, and recycle timing functions.

          - Plug-in-style relay with either multi-pin or blade plug.

          - Construct contacts of silver, silver alloy, or gold.

          - Enclose relay in a dust-tight cover.

          - Include knob and dial scale for alternative digital interface for setting delay time.

          - Visual Status Indication: Power "On"[ and Output "On"] status.

          - Performance:

            - Mechanical Life: At least [10] <Insert number> million cycles.

            - Electrical Life: At least [100,000] <Insert number> cycles at rated load.

            - Timing Ranges: Multiple ranges from [0.1] <Insert number> seconds to [100] <Insert number> minutes.

            - Repeatability: Within [2] <Insert number> percent.

            - Recycle Time: [45] <Insert value> ms.

            - Minimum Pulse-Width Control: [50] <Insert value> ms.

            - Power Consumption: 5 VA or less.

            - Ambient Operating Temperatures: Minus 40 to 115 deg F (Minus 40 to 46 deg C).

          - Equip relays with transient suppression to limit transients to non-damaging levels.

          - Plug each relay into industry-standard, 35 mm DIN rail socket. Plug all relays located in control panels into sockets that are mounted on a DIN rail.

          - Include relay socket with screw terminals. Mold into socket the coincident screw terminal numbers.

If more than one type of latching relay is required, copy "Latching Relays" Paragraph below and re-edit requirements for each different type. Include an applications article in Part 3 to describe applications for each different type of latching relay specified.

        - Latching Relays:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - NRTL listed.

          - Continuous-duty type, rated for at least [10] <Insert value> A at 250 V ac and 60 Hz.

          - SPDT, DPDT, or three-pole double-throw, as required by control application.

          - Plug-in-style relay with either multi-pin or blade plug.

          - Construct contacts of silver, silver alloy, or gold.

          - Enclose relay in a [clear transparent ]polycarbonate dust-tight cover.

          - Performance:

            - Mechanical Life: At least [10] <Insert number> million cycles.

            - Electrical Life: At least [100,000] <Insert number> cycles at rated load.

            - Pickup Time: [15] [20] <Insert value> ms or less.

            - Dropout Time: [10] [20] <Insert value> ms or less.

            - Pull-in Voltage: [85] <Insert number> percent of rated voltage.

            - Dropout Voltage: [50] [10] <Insert number> percent of nominal rated voltage.

            - Power Consumption: [2] [5] <Insert value> VA or less.

            - Ambient Operating Temperatures: Minus 40 to 115 deg F (Minus 40 to 46 deg C).

          - Equip relays with coil transient suppression to limit transients to non-damaging levels.

          - Plug each relay into industry-standard, 35 mm DIN rail socket. Plug all relays located in control panels into sockets that are mounted on a DIN rail.

          - Relay socket with screw terminals. Mold into socket the coincident screw terminal numbers.

If more than one type of current sensing relay is required, copy "Current Sensing Relays" Paragraph below and re-edit requirements for each different type. Include an applications article in Part 3 to describe applications for each different type of current sensing relay specified.

        - Current Sensing Relays:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - NRTL listed.

          - Monitors ac current.

          - Independent adjustable controls for pickup and dropout current.

          - Energized when supply voltage is present and current is above pickup setting.

          - De-energizes when monitored current is below dropout current.

          - Dropout current is adjustable from [50] <Insert number> to [95] <Insert number> percent of pickup current.

          - Visual indication of contact status.

          - Include current transformer, if required for application.

          - House current sensing relay and current transformer if required in its own enclosure. Use NEMA 250, [Type 1] [or] [Type 12] enclosure for indoors applications and NEMA 250, [Type 4] [or] [Type 4X] for outdoor applications.

        - Combination On-Off Status Sensor and On-Off Control Relays:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description:

            - On-off control and on-off status indication in a single device.

            - LED status indication of activated relay and current trigger.

            - Closed-Open-Auto override switch located on the load side of relay.

          - Performance:

            - Ambient Temperature: Minus 30 to 140 deg F (Minus 34 to 60 deg C).

            - Voltage Rating: Single-phase loads rated for 300 V ac. Three-phase loads rated for 600 V ac.

          - Status Indication:

            - Current Sensor: Integral sensing for single-phase loads up to 20 A and external solid or split sensing ring for three-phase loads up to 150 A.

            - Current Sensor Range: As required by application.

            - Current Set Point: [Fixed] [Adjustable] [Fixed or adjustable, as required by application].

            - Current Sensor Output:

Retain any of first four subparagraphs below to suit Project.

              - Solid-state, SPDT contact rated for 30 V ac and dc and for 0.4 A.

              - Solid-state, SPDT contact rated for 120 V ac and 1.0 A.

              - Analog, 0 to 5 or 10 V dc.

              - Analog, 4 to 20 mA, loop powered.

          - Relay: SPDT, continuous-duty coil; rated for 10-million mechanical cycles.

          - Enclosure: NEMA 250, [Type 1] [Type 12] <Insert type> enclosure for indoor applications; NEMA 250, [Type 4] [Type 4X] <Insert type> enclosure for outdoor applications.

      - ELECTRICAL POWER DEVICES

        - Control Transformers:

          - Sizing Criteria: Size control transformers for total connected load, plus additional [25] [50] <Insert number> percent of connected load for future spare capacity.

          - Transformer Minimum Capacity: [40] [100] <Insert value> VA.

          - Protection: Provide transformers with both primary and secondary fuses.[ Integral circuit breaker is acceptable in lieu of fuses.]

          - Enclosure: House control transformers in NEMA 250 enclosures, type as indicated in "Performance Requirements" Article for application.

Retain "Power-Line Conditioners" Paragraph below if needed to protect HVAC control equipment and instruments not adequately protected through building electrical power distribution system, or other means, such as UPS. Consult Project electrical engineer.

If more than one type of power-line conditioner is required, copy "Power-Line Conditioners" Paragraph below and re-edit requirements for each different type. Include an applications article in Part 3 to describe applications for each different type of power-line conditioner specified.

        - Power-Line Conditioners:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - General Power-Line Conditioner Requirements:

            - Design to ensure maximum reliability, serviceability, and performance.

            - Overall function of power-line conditioner is to receive raw, polluted electrical power and purify it for use by electronic equipment. Power-line conditioner is to provide isolated, regulated, transient, and noise-free sinusoidal power to loads served.

          - Standards: NRTL listed per UL 1012.

          - Performance:

            - Single phase, continuous, 100 percent duty rated kVA/kW capacity. Design to supply power for linear or nonlinear, high crest factor, resistive and reactive loads.

            - Automatically regulate output voltage to within [2] <Insert number> percent or better with input voltage fluctuations of plus 10 to minus 20 percent of nominal when system is loaded 100 percent. Use Variable Range Regulation to obtain improved line voltage regulation when operating under less than full load conditions.

              - At 75 Percent Load: Output voltage automatically regulated to within [3] <Insert number> percent with input voltage fluctuations of plus 10 to minus 35 percent of nominal.

              - At 50 Percent Load: Output voltage automatically regulated to within [3] <Insert number> percent with input voltage fluctuations of plus 10 to minus 40 percent of nominal.

              - At 25 Percent Load: Output voltage automatically regulated to within [3] <Insert number> percent with input voltage fluctuations of plus 10 to minus 45 percent of nominal.

            - With input voltage distortion of up to 40 percent, limit the output voltage sine wave to maximum harmonic content of [5] <Insert number> percent.

            - Automatically regulate output voltage to within 2.5 percent when load (resistive) changes from zero to 100 to zero percent.

            - Output voltage returns to 95 percent of nominal level within two cycles and to 100 percent within three cycles when output is taken from no load to full-resistive load, or vice versa. Recovery from partial resistive load changes is corrected in a shorter period.

            - K Factor: [30] <Insert value>, designed to operate with nonlinear, non-sinusoidal, high crest factor loads without overheating.

            - Input power factor within 0.95 approaching unity with load power factor as poor as 0.6.

            - Attenuate load-generated odd current harmonics [23] <Insert value> dB at the input.

            - Electrically isolate the primary from the secondary. Meet isolation criteria as defined in NFPA 70, Article 250-5D.

            - Lighting and Surge Protection: Compares to UL 1449 rating of 330 V when subjected to Category B3 (6000 V/3000 A) combination waveform as established by IEEE C62.41.1 and IEEE C62.41.2.

            - Common-mode noise attenuation of [140] <Insert value> dB.

            - Transverse-mode noise attenuation of [120] <Insert value> dB.

            - With loss of input power for up to 16.6 ms, output sine wave remains at usable ac voltage levels.

            - Reliability of [200,000] <Insert number> hours' MTBF.

            - At full load, when measured at 1 m distance, audible noise is not to exceed [54] <Insert value> dB.

            - Approximately [92] <Insert number> percent efficient at full load.

          - Transformer Construction:

            - Ferroresonant, dry type, convection cooled, 600 V class. Transformer windings of Class H (220 deg C) insulated copper.

            - Use Class H installation system throughout with operating temperatures not to exceed 150 deg C over a 40 deg C ambient temperature.

            - Configure transformer primary for multi-input voltage. Include input terminals for source conductors and ground.

            - Manufacture transformer core using M-6 grade, grain-oriented, stress-relieved transformer steel.

            - Configure transformer secondary in 240/120 V split with 208 V tap or straight 120 V, depending on power output size.

            - Electrically isolate the transformer secondary windings from primary windings. Bond neutral conductor to cabinet enclosure and output neutral terminal.

            - Include interface terminals for output power hot, neutral, and ground conductors.

            - Label leads, wires, and terminals to correspond with circuit wiring diagram.

            - Vacuum impregnate transformer with epoxy resin.

          - Cabinet Construction:

            - Design for panel or floor mounting.

            - NEMA 250, [Type 1] [or] [Type 2] enclosure for indoor applications. NEMA 250, [Type 3R] <Insert type> for outdoor applications.

            - Manufacture the cabinet from heavy gauge steel complying with UL 50 or UL 508A.

            - Include textured baked-on paint finish.

If more than one type of DC power supply is required, copy "DC Power Supplies" Paragraph below and re-edit requirements for each different type. Include an applications article in Part 3 to describe applications for each different type of DC power supply specified.

        - DC Power Supplies:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Linear or switched, regulated power supplies with ac input to [one] [or] [multiple] dc output(s).

            - Include both line and load regulation to ensure stable output.

            - To protect both power supply and load, include power supply with an automatic current limiting circuit.

          - Features:

Retain any of first five subparagraphs below.

Retain "Connection" Subparagraph below to require plug-in connection for easy removal. Feature is not available from all listed manufacturers. Consult manufacturers for availability.

            - Connection: Plug-in style suitable for mating with standard [8-pin octal ]socket. Include power supply with mating mounting socket.

            - Housing: Enclose circuitry in a housing.

            - Local Adjustment: Include screw adjustment on exterior of housing for dc voltage output.

            - Mounting: DIN rail.

            - Visual status indicator.

            - <Insert feature>.

          - Performance:

            - Input Voltage: Nominally [120] <Insert value> V ac, 60 Hz.

            - Output Voltage: Nominally [24] <Insert value> V dc with plus or minus [1] <Insert value> V dc adjustment.

            - Output Current: Minimum [100] <Insert value> mA.

            - Load Regulation: Within [0.1] <Insert number> percent.

            - Line Regulation: Within [0.05] <Insert number> percent.

            - Stability: Within [0.1] <Insert number> percent of rated volts after warmup period.

            - Ripple: [1] <Insert value> mV rms.

      - UNINTERRUPTABLE POWER SUPPLY (UPS) UNITS

        - Furnish local UPS units, of type indicated, installed with DDC system.

        - DIN Rail Mounted UPS:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Provide continuous, regulated output power without using batteries during brown-out, surge, and spike conditions.

          - Performance:

            - Capacity: Load not to exceed [75] <Insert number> percent of rated capacity.

            - Efficiency: Minimum [94] <Insert number> percent.

            - Input Voltage: Single phase, 120 V ac, compatible with field power source.

            - Load Power Factor Range (Crest Factor): [0.65 to 1.0] <Insert range>.

            - Output Voltage: 101 to 132 V ac, while input voltage varies between 89 and 152 V ac.

            - On Battery Output Voltage: Sine wave.

            - Inverter Overload Capacity: Minimum [150] <Insert number> percent for 30 seconds.

            - Battery Backup: [Five] [10] [15] <Insert number> minutes of operation at [full] <Insert value> load with battery power.

            - Battery Recharge Time: Maximum of [four] [six] <Insert number> hours to 90 percent capacity after full discharge.

            - Transfer Time: [6] <Insert value> ms.

            - Surge Voltage Withstand Capacity: IEEE C62.41.1 and IEEE C62.41.2, Categories A and B.

          - Automatic bypass operation during fault or overload conditions.

          - Integral line-interactive, power condition topology to eliminate all power contaminants.

          - Include power switch and visual indication of power, battery, fault[, and temperature].

          - Include audible alarm of faults with silence feature.

          - Include dry contacts (digital output points) for low battery condition and battery-on (primary utility power failure)[ and connect points to DDC system].

          - Batteries: Sealed; maintenance free; replacement without dropping load.

        - Tower UPS Models through 1000 VA:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Provide continuous, regulated output power without using batteries during brown-out, surge, and spike conditions.

          - Performance:

            - Capacity: Load not to exceed [75] <Insert number> percent of rated capacity.

            - Efficiency: Complying with ENERGY STAR requirements; minimum [91] <Insert number> percent.

            - Input Voltage: Single phase, 120 V ac, compatible with field power source.

            - Load Power Factor Range (Crest Factor): [0.65 to 1.0] <Insert range>.

            - Output Voltage: 101 to 132 V ac, while input voltage varies between 89 and 152 V ac.

            - On Battery Output Voltage: Sine wave.

            - Inverter Overload Capacity: Minimum [150] <Insert number> percent for 30 seconds.

            - Battery Backup: [Five] [10] [15] <Insert number> minutes of operation at [full] <Insert value> load with battery power.

            - Battery Recharge Time: Maximum of [four] [six] <Insert number> hours to 90 percent capacity after full discharge to cutoff.

            - Transfer Time: [0] <Insert value> ms.

            - Surge Voltage Withstand Capacity: IEEE C62.41.1 and IEEE C62.41.2, Categories A and B; 6 kV/200 and 500 A; 100 kHz ring wave.

          - Automatic bypass operation during fault or overload conditions.

          - Integral line-interactive, power condition topology to eliminate all power contaminants.

          - Include power switch and visual indication of power, battery, fault, and temperature.

          - Include audible alarm of faults and front panel silence feature.

          - Receptacles: Minimum [four] <Insert number>, NEMA WD 1, NEMA WD 6 Configuration 5-15R receptacles.

          - Remote Alarms: Include dry contacts (digital output points) [or serial communication interface ]for low battery condition and battery-on (primary utility power failure)[ and connect points to DDC system].

          - Batteries: Sealed type; maintenance free. Battery replacement is to be front accessible by user without dropping load.

          - Install tower models in enclosures rated for location.

        - UPS Models through 3000 VA: [Tower] [and] [Rack].

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - NRTL Listing: UL 1778.

          - Provide continuous, regulated output power without using batteries during brown-out, surge, and spike conditions.

          - Performance:

            - Capacity: Load not to exceed [75] <Insert number> percent of UPS rated capacity.

            - Efficiency: Complying with ENERGY STAR requirements; minimum [91] <Insert number> percent.

            - Input Voltage: Single phase, 120 V ac, plus 20 to minus 30 percent.

            - Power Factor: Minimum [0.95] <Insert value> at full load.

            - Output Voltage: Single phase, 120 V ac, within [2] [3] percent.

            - Inverter overload capacity to be minimum [150] <Insert number> percent for 30 seconds.

            - Battery Backup: [Five] [10] [15] <Insert number> minutes of operation at [full] <Insert value> load with battery power.

            - Battery Recharge Time: Maximum of [6] [8] <Insert number> hours to 90 percent capacity.

            - Transfer Time: [0] <Insert value> ms.

            - <Insert additional performance requirement>.

          - LCD display with operator interface.

          - Receptacles: Minimum [6] <Insert number>, NEMA WD 1, NEMA WD 6 Configuration 5-15R or 5-20R receptacles.

          - Automatic bypass operation during fault or overload conditions.

          - Remote Alarms: Include dry contacts (digital output points) [or serial communication interface ]for low battery condition and battery-on (primary utility power failure)[ and connect points to DDC system].

          - Batteries: Sealed; maintenance free.

          - Enclosures: Install tower models in enclosures rated for location.[ Install rack models installed on matching racks, as applicable to particular installation location and space availability/configuration.]

      - PRESSURE INSTRUMENT SIGNAL AIR PIPING AND TUBING

        - Products in this article are intended for use with the following:

Retain first subparagraph below if Project includes pneumatic products.

          - Main air and signal air to pneumatically controlled instruments, actuators, and other control devices and accessories.

          - Signal air between pressure instruments, such as sensors, switches, transmitters, controllers, and accessories.

        - Copper Tubing:

          - Seamless phosphor deoxidized copper, drawn tempered[, or soft annealed], with chemical and physical properties in accordance with ASTM B75/B75M.

          - Performance, dimensions, weight, and tolerance in accordance with ASTM B280.

          - Diameter, as required by application, not less than nominal [1/4 inch (6 mm)] [3/8 inch (10 mm)] <Insert size>.

          - Wall thickness, as required by application, but not less than 0.030 inch (0.8 mm).

          - Copper Tubing Connectors and Fittings - Brass, Compression Type:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Single or double ferrule design creating a constant tension between fitting body and fitting nut for leak-free seal.

          - Copper Tubing Connectors and Fittings - Copper, Solder-Joint Type:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Copper Solder-Joint Fittings: Cast, ASME B16.18 or wrought, ASME B16.22.

Retain "Galvanized-Steel Piping" Paragraph if required by Project. Galvanized-steel pipe is not typically used on most projects.

        - Galvanized-Steel Piping (for Pneumatic/Pressure Instrument Signal Air):

          - Pipe: ASTM A53/A53M, Schedule 40.

          - Fittings: Galvanized malleable iron, ASME B16.3, Class 150.

        - Polyethylene Tubing: ([For Pneumatic/]Pressure Instrument Signal Air).

          - Fire-resistant, black virgin polyethylene in accordance with ASTM D1248, Type 1, Class C, and Grade 5.

          - Complying with stress crack test in accordance with ASTM D1693.

          - Diameter, as required by application, of not less than nominal 1/4 inch (6 mm).

          - Polyethylene Tubing Connectors and Fittings - Brass, Barb Fittings:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Tapered and beaded hose barbs of push-on design; intended for low-pressure applications only.

          - Polyethylene Tubing Connectors and Fittings - Brass, Compression Type:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Specially designed for jointing polyethylene tubing to provide leak-free seal without twisting or weakening polyethylene tubing.

      - PROCESS TUBING

        - Products in this article are intended for signals to instruments connected to liquid and steam systems.

Retain "Copper Tubing" or "Stainless Steel Tubing (for Process Tubing)" Paragraph below, or both, to suit Project.

        - Copper Tubing:

          - Seamless phosphor deoxidized copper, drawn tempered with chemical and physical properties in accordance with ASTM B75/B75M.

          - Performance, dimensions, weight, and tolerance in accordance with ASTM B280.

          - Diameter, as required by application, of not less than nominal [3/8 inch (10 mm)] [1/2 inch (13 mm)] <Insert size>.

          - Wall thickness, as required by application, but not less than 0.030 inch (0.8 mm).

          - Copper Tubing Connectors and Fittings (for Process Tubing) - Brass, Compression Type:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Single or double ferrule design creating a constant tension between fitting body and fitting nut for leak-free seal.

          - Copper Tubing Connectors and Fittings (for Process Tubing) - Brass, Solder-Joint Type:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Copper Solder-Joint Fittings: Cast, ASME B16.18 or wrought, ASME B16.22.

        - Stainless Steel Tubing (for Process Tubing):

          - Seamless Type 316 stainless steel, Grade TP, cold drawn, annealed and pickled, and free from scale.

          - Chemical and physical properties in accordance with ASTM A269/A269M.

          - Diameter, as required by application, of not less than nominal [3/8 inch (10 mm)] [1/2 inch (13 mm)] <Insert size>.

          - Wall thickness, as required by application, but not less than 0.035 inch (0.9 mm).

          - Furnish stainless steel tubing in [20 ft. (6 m)] straight random lengths.

        - Stainless Steel Tubing Connectors and Fittings (for Process Tubing) - Stainless Steel, Compression Type:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Connectors and fittings constructed from Type 316 stainless steel, with collets, flareless type.

          - Single or double ferrule design creating a constant tension between fitting body and fitting nut for leak-free seal.

          - Connect instruments to tubing with connectors having compression connector on one end and IPS or NPT thread on other end.

      - CONTROL WIRE AND CABLE

        - Wire: Single conductor control wiring above 24 V.

          - Wire Size: Minimum [18] [16] [14] <Insert value> AWG.

          - Conductors: 7/24 soft annealed copper strand with 2- to 2.5-inch (50- to 65-mm) lay.

          - Conductor Insulation: 600 V, Type THWN or Type THHN, and 90 deg C in accordance with UL 83.

          - Conductor Insulation Colors: Black (hot), white (neutral), and green (ground).

          - Furnish on spools.

        - Single, Twisted-Shielded, Instrumentation Cable above 24 V:

          - Wire Size: Minimum [18] [20] [22] <Insert value> AWG.

          - Conductors: Twisted, 7/24 soft annealed copper strand with a 2- to 2.5-inch (50- to 65-mm) lay.

          - Conductor Insulation: Type THHN/THWN or Type TFN rating.

          - Conductor Insulation Colors:

            - Twisted Pair: Black and white.

            - Twisted Triad: Black, red, and white.

          - Shielding: 100 percent type, 0.35/0.5-mil aluminum/Mylar tape, helically applied with 25 percent overlap, and aluminum side in with tinned copper drain wire.

          - Outer Jacket Insulation: 600 V, 90 deg C rating, and Type TC cable.

          - Furnish on spools.

        - Single, Twisted-Shielded, Instrumentation Cable 24 V and Less:

          - Wire Size: Minimum [18] [20] [22] <Insert value> AWG.

          - Conductors: Twisted, 7/24 soft annealed copper stranding with a 2- to 2.5-inch (50- to 65-mm) lay.

          - Conductor Insulation: Nominal 15-mil thickness, constructed from flame-retardant PVC.

          - Conductor Insulation Colors:

            - Twisted Pair: Black and white.

            - Twisted Triad: Black, red, and white.

          - Shielding: 100 percent type, 1.35-mil aluminum/polymer tape, helically applied with 25 percent overlap, and aluminum side in with tinned copper drain wire.

          - Outer Jacket Insulation: 300 V, 105 deg C rating, and Type PLTC cable.

          - Furnish on spools.

        - LAN and Communication Cable: Comply with DDC system manufacturer requirements for network being installed.

          - Comply with following requirements for balanced twisted pair cable described in [Section 260523 "Control-Voltage Electrical Power Cables."] [Section 271513 "Communications Copper Horizontal Cabling."]

            - Plenum rated.

            - Unique color that is different from other cables used on Project.

      - RACEWAYS

        - Comply with requirements in Section 260533.13 "Conduits for Electrical Systems" and Section 260533.16 "Boxes and Covers for Electrical Systems" for electrical power raceways and boxes.

        - Comply with requirements in Section 270528 "Pathways for Communications Systems" for raceways for balanced twisted pair cables and optical fiber cables.

      - OPTICAL FIBER CABLE AND CONNECTORS

        - Comply with requirements in Section 271323 "Communications Optical Fiber Backbone Cabling" for optical fiber backbone cabling and connectors.

        - Comply with requirements in Section 271523 "Communications Optical Fiber Horizontal Cabling" for optical fiber horizontal cabling and connectors.

      - ACCESSORIES

        - Pneumatic Pressure Gauges:

          - Face Size: 1.5-inch- (38-mm-) diameter face for pressures up through 30 psig (207 kPa) and 2.5-inch- (65-mm-) diameter face for greater pressures.

          - Face Markings: White dial face with black printing; 1 psig (6.9 kPa) increment for scale ranges through 30 psig (207 kPa) and 2 psig (13.8 kPa) increment for larger ranges.

          - Accuracy: Within [0.5] [1] <Insert number> percent of full-scale range.

          - Applications: Include separate gauges for branch pressure and main pressure tubing.

        - Pressure Electric Switches:

          - Description: Diaphragm-operated, snap-acting switch.

          - Performance:

            - Rating: Resistance loads at [120] <Insert value> V ac.

            - Set Point: Adjustable from [3 to 20 psig (21 to 138 kPa)] <Insert pressure range>.

            - Differential: Adjustable from [2 to 6 psig (14 to 41 kPa)] <Insert pressure range>.

          - Body and Switch Housing: Metal.

        - Control Damper Blade Limit Switches:

          - Application: Sense positive open and/or closed position of damper blades.

          - NEMA 250, [Type 13] <Insert type>, oiltight construction. Install in instrument enclosure where required for additional environmental protection.

          - Arrange for mounting application, and to prevent "over-center" operation.

        - I/P and E/P Transducers:

          - Commercial Grade:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Description: Transducer converting an electronic current (I) or voltage (E) AO signal to a proportional [or stepped ]pneumatic signal. Unless otherwise required by operating sequence, use 3 to 15 psig (21 to 103 kPa) pneumatic signal for pneumatic actuation.

            - Features:

              - Auto/manual output switch, manual output control, and output pressure gauge.

              - Separate zero and span calibration adjustments.

            - Performance:

              - Accuracy: Within [1.0] <Insert number> percent of output span.

              - Linearity: Within [0.5] [1.0] <Insert number> percent of output span.

              - Output Capacity: Not less than [550 scim (0.54 cu. m/h)] <Insert value> at 15 psig (103 kPa).

              - Maximum Pressure: [30 psig (206 kPa)] [40 psig (276 kPa)] <Insert value> of supply pressure without damage.

              - Vibration: Construct entire assembly so that shock and vibration will not harm transducer or affect accuracy.

            - Applications:

              - Terminal Units: Fan-coil units, VAV units, unit heaters, and <Insert equipment>.

              - <Insert applications>.

          - Industrial Grade:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Description: Transducer converting an electronic current (I) or voltage (E) AO signal to a proportional pneumatic signal (P). Unless otherwise required by operating sequence, use 3 to 15 psig (21 to 103 kPa) pneumatic signal for pneumatic actuation. Stepped pneumatic signal is unacceptable.

            - Features:

              - Adjustments: Separate zero and span calibration adjustments.

              - Conduit Connections: Nominal 1/2 inch (13 mm).

              - Enclosure: NEMA 250, [Type 4X] <Insert type>.

              - Pressure Gauge: Integral output pressure gauge.

            - Performance:

              - Accuracy: Within [0.5] [1.0] <Insert number> percent of output span.

              - Hysteresis: Within [0.5] <Insert number> percent of output span.

              - Linearity: Within [0.5] [0.75] <Insert number> percent of output span.

              - Repeatability: Within [0.5] <Insert number> percent of output span.

              - Output Capacity: Not less than [5] <Insert value> scfm at 15 psig (103 kPa).

              - Air Consumption: Maximum of [5] <Insert value> scfh at 15 psig (103 kPa).

              - Ambient Temperature: Suitable for operation in ambient temperature range of minus 20 to 150 deg F (minus 40 to 66 deg C).

              - Pressure: Up to [50 psig (345 kPa)] <Insert value> without damage.

              - Vibration: Construct entire assembly so shock and vibration will not harm transducer or affect accuracy.

            - Applications:

              - All applications, except for terminal units and other applications with commercial-grade transducers.

              - <Insert applications>.

        - E/P Switch:

          - Body: Cast aluminum or brass; three pipe body (common, normally open, and normally closed).

          - Internal Components: Brass, copper, steel, or stainless steel.

          - Connections: Barb, or threaded for mating to compression fittings.

          - Rating: 30 psig (207 kPa) when installed in systems below 25 psig (172 kPa); 150 psig (1034 kPa) when installed in systems above 25 psig (172 kPa).

          - Features: Include coil transient suppression.

        - Instrument Enclosures:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Application: Include instrument enclosure for secondary protection to comply with requirements indicated in "Performance Requirements" Article.

          - Certification: NRTL listed and labeled to UL 50 or UL 508A as applicable.

          - Subpanel:

            - Size enclosure with least 25 percent spare area on subpanel.

            - Mount instrument(s) within enclosure on internal subpanel(s).

          - Identification: Include on face of enclosure an engraved, laminated phenolic nameplate for each instrument installed within enclosure.

Retain first subparagraph below for pneumatic control devices.

          - Pneumatic Pressure Gauges: Include main pressure gauge and a branch pressure gauge for each pneumatic device installed inside enclosure.

          - Raceways: For enclosures housing multiple instruments, route tubing, cable, and wiring within enclosure in a raceway having continuous removable cover.

          - Access: Provide enclosures larger than [12 inches (300 mm)] <Insert dimension> with hinged full-size face cover.

Retain subparagraph below for applications requiring additional security.

          - Security: Equip enclosures with lock and common key.

        - Manual Valves:

          - Brass Needle Valves:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Pressure Rating: 150 psig (1030 kPa).

            - Temperature Rating: 250 deg F (121 deg C).

            - Body: Brass.

            - Seat: Brass.

            - Handle: Aluminum, brass, or stainless steel T-bar handle.

            - Connections: Include tubing connections.

            - Applications: Copper and polyethylene pneumatic tubing.

          - Stainless Steel Needle Valves:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Pressure Rating: 5000 psig (34 474 kPa).

            - Temperature Rating: 450 deg F (232 deg C).

            - Body: Type 316 stainless steel.

            - Seat: Type 316 stainless steel.

            - Packing: [PTFE] <Insert material>.

            - Handle: Aluminum or stainless steel T-bar handle.

            - Connections: Include tubing connections.

            - Applications: Copper pneumatic tubing; copper and stainless steel process tubing.

          - Bronze Body Ball Valves:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: MSS SP-110.

            - SWP Rating: 150 psig (1035 kPa).

            - CWP Rating: 600 psig (4140 kPa).

            - Body Design: Two piece.

            - Body Material: Bronze.

            - Ends: Threaded.

            - Seats: PTFE.

            - Stem: Stainless steel.

            - Ball: Stainless steel, vented.

            - Handle: Stainless steel with vinyl grip.

            - Port: Full.

Retain "Retractable, Wall-Mounted Cabinet for Portable Workstations" Paragraph below for use with portable operator workstations. Consult Owner to determine need.

        - Retractable, Wall-Mounted Cabinet for Portable Workstations:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Surface-mounted or recessed wall cabinet for tilt-out operation of laptop computers and large-format mobile devices.

          - Cabinet Load Limit: [50 lb (23 kg)] <Insert value>.

          - Cabinet Material: Carbon steel.

          - Cabinet Finish: Powder-coat epoxy; manufacturer's standard color.

          - Features include the following:

Retain any of first seven subparagraphs below. Not all features listed below are available from all listed manufacturers.

            - Oil-filled dampers for controlled lowering of equipment to operational position.

            - 3RU EIA mounting rails.

            - Removable laptop shelf.

            - Separate top compartment with mounting area, hinged rail.

            - Front ventilation slots.

            - Security key lock access.

            - Knockouts for conduit connections on top and bottom of cabinet.

            - <Insert additional features>.

          - Field Coordination: Provide inside center of backbox with provision to mount a field-furnished and -installed, single-gang electrical outlet box.

      - IDENTIFICATION

        - Instrument Air Pipe and Tubing:

          - Engraved tag bearing the following information:

            - Service (Example): "Instrument Air."

            - Pressure Range (Example): 0 to 30 psig (0 to 200 kPa).

          - Letter size minimum of [0.25 inch (6 mm)] <Insert dimension> high.

          - Engraved phenolic consisting of three layers of rigid laminate. Top and bottom layers color-coded blue with contrasting white center exposed by engraving through outer layer.

          - Include tag with brass grommet, chain, and S-hook.

        - Control Equipment, Instruments, and Control Devices:

          - [Self-adhesive label] [Laminated acrylic or melamine plastic sign] bearing unique identification.

            - Include instruments with unique identification identified by equipment being controlled or monitored, followed by point identification.

          - Letter size as follows:

First 10 subparagraphs below are examples only.

            - Servers: Minimum of [0.5 inch (13 mm)] <Insert dimension> high.

            - DDC Controllers: Minimum of [0.5 inch (13 mm)] <Insert dimension> high.

            - Gateways: Minimum of [0.5 inch (13 mm)] <Insert dimension> high.

            - Repeaters: Minimum of [0.5 inch (13 mm)] <Insert dimension> high.

            - Enclosures: Minimum of [0.5 inch (13 mm)] <Insert dimension> high.

            - Electrical Power Devices: Minimum of [0.25 inch (6 mm)] <Insert dimension> high.

            - UPS units: Minimum of [0.5 inch (13 mm)] <Insert dimension> high.

            - Accessories: Minimum of [0.25 inch (6 mm)] <Insert dimension> high.

            - Instruments: Minimum of [0.25 inch (6 mm)] <Insert dimension> high.

            - Control Damper and Valve Actuators: Minimum of [0.25 inch (6 mm)] <Insert dimension> high.

          - Engraved phenolic consisting of three layers of rigid laminate. Top and bottom layers color-coded black with contrasting white center exposed by engraving through outer layer.

          - Fastened with drive pins.

          - Instruments, control devices, and actuators with Project-specific identification tags having unique identification numbers following requirements indicated and provided by original manufacturer do not require additional identification.

        - Valve Tags:

          - Brass tags and brass chains attached to valve.

          - Tag Size: Minimum [1.5 inches (38 mm)] <Insert dimension> in diameter.

          - Include tag with unique valve identification indicating control influence such as flow, level, pressure, or temperature; followed by location of valve, and followed by three-digit sequential number. For example: TV-1.001.

          - Valves with Project-specific identification tags having unique identification numbers following requirements indicated and provided by original manufacturer do not require an additional tag.

        - Raceway and Boxes:

          - Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

          - Paint cover plates on junction boxes and conduit same color as tape banding for conduits. After painting, label cover plate "HVAC Controls"[ using engraved phenolic tag].

Retain first subparagraph below if Project includes pneumatic products.

          - For raceways housing pneumatic tubing, add phenolic tag labeled "HVAC Instrument Air Tubing."

          - For raceways housing air signal tubing, add phenolic tag labeled "HVAC Air Signal Tubing."

        - Equipment Warning Labels:

          - Self-adhesive label with pressure-sensitive adhesive back and peel-off protective jacket.

          - Lettering size at least 14-point type with white lettering on red background.

          - Warning label to read "CAUTION-Equipment operated under remote automatic control and may start or stop at any time without warning. Switch electric power disconnecting means to OFF position before servicing."

          - Lettering to be enclosed in a white line border. Edge of label is to extend at least [0.25 inch (6 mm)] <Insert dimension>beyond white border.

      - SOURCE QUALITY CONTROL

This article covers tests and inspections performed at the source to verify that products and materials comply with requirements specified.

Retain "Testing Agency" Paragraph below if retaining "DDC System Reliability" Paragraph in "Performance Requirements" Article and to require independent evaluation. Independent evaluation may be required whether DDC system reliability is required. Independent certification may be acceptable to authorities having jurisdiction without further monitoring of plant's quality-control and testing program by Owner.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to evaluate the following in accordance with industry standards for each product, and to verify DDC system reliability specified in performance requirements:

First three subparagraphs below are examples only.

          - DDC controllers.

          - Gateways.

          - Routers.

          - <Insert product>.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Product(s) [and] [material(s)] will be considered defective if [it does] [they do] not pass tests and inspections.

        - Prepare test and inspection reports.

- EXECUTION

      - EXAMINATION

        - Examine substrates and conditions for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

          - Verify compatibility with and suitability of substrates.

        - Examine roughing-in for instruments installed in piping to verify actual locations of connections before installation.

        - Examine roughing-in for instruments installed in duct systems to verify actual locations of connections before installation.

        - Examine walls, floors, roofs, and ceilings for suitable conditions where product will be installed.

        - Prepare written report, endorsed by Installer, listing conditions detrimental to performance of the Work.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - DDC SYSTEM INTERFACE WITH OTHER SYSTEMS AND EQUIPMENT

Retain "Communication Interface to Equipment with Integral Controls" Paragraph below to require DDC system to monitor or control equipment through a communication link.

        - Communication Interface to Equipment with Integral Controls:

          - DDC system has communication interface with equipment having integral controls and having communication interface for remote monitoring or control.

Retain "Equipment to Be Connected" Subparagraph below to require equipment to be connected to DDC system through a communication interface; delete if equipment to be connected is indicated on Drawings. Coordinate with Drawings.

          - Equipment to Be Connected:

Retain applicable subparagraphs below. Coordinate specific interface requirements in Sections specifying equipment.

            - Domestic water booster pumps specified in Section 221123.13 "Domestic-Water Packaged Booster Pumps."

            - Sewage pump stations specified in Section 221343 "Facility Packaged Sewage Pumping Stations."

            - Sump pumps specified in Section 221429 "Sump Pumps."

            - Air-compressors and air driers specified in Section 221519 "General-Service Packaged Air Compressors and Receivers" and Section 226119 "Compressed-Air Equipment for Laboratory and Healthcare Facilities."

            - Domestic water softeners specified in Section 223100 "Domestic Water Softeners."

            - Domestic water heaters specified in Section 223300 "Electric, Domestic-Water Heaters" and Section 223400 "Fuel-Fired, Domestic-Water Heaters."

            - Vacuum equipment specified in Section 226219 "Vacuum Equipment for Laboratory and Healthcare Facilities."

            - Processed water equipment specified in Section 226719 "Processed Water Equipment for Laboratory and Healthcare Facilities."

            - Air curtains specified in Section 233433.16 "Industrial Air Curtains."

            - Air-terminal units specified in Section 233600 "Air Terminal Units."

            - Kitchen hoods specified in Section 233813 "Commercial-Kitchen Hoods."

            - Boilers specified in Section 235213 "Electric Boilers."

            - Boilers specified in Section 235216 "Condensing Boilers."

            - Boilers specified in Section 235223 "Cast-Iron Boilers."

            - Boilers specified in Section 235233 "Water-Tube Boilers."

            - Boilers specified in Section 235239 "Fire-Tube Boilers."

            - Feedwater equipment specified in Section 235313 "Boiler Feedwater Pumps."

            - Deaerators specified in Section 235316 "Deaerators."

            - Chillers specified in Section 236413.13 "Direct-Fired Absorption Water Chillers."

            - Chillers specified in Section 236413.16 "Indirect-Fired Absorption Water Chillers."

            - Chillers specified in Section 236416 "Centrifugal Water Chillers."

            - Chillers specified in Section 236423.13 "Air-Cooled, Scroll Water Chillers."

            - Chillers specified in Section 236423.16 "Water-Cooled, Scroll Water Chillers."

            - Chillers specified in Section 236426.13 "Air-Cooled, Rotary-Screw Water Chillers."

            - Chillers specified in Section 236426.16 "Water-Cooled, Rotary-Screw Water Chillers."

            - Cooling towers specified in Section 236513.13 "Open-Circuit, Forced-Draft Cooling Towers."

            - Cooling towers specified in Section 236513.16 "Closed-Circuit, Forced-Draft Cooling Towers."

            - Cooling towers specified in Section 236514.13 "Open-Circuit, Induced-Draft, Counterflow Cooling Towers."

            - Cooling towers specified in Section 236514.14 "Open-Circuit, Induced-Draft, Crossflow Cooling Towers."

            - Cooling towers specified in Section 236514.16 "Closed-Circuit, Induced-Draft, Counterflow Cooling Towers."

            - Cooling towers specified in Section 236514.17 "Closed-Circuit, Induced-Draft, Combined-Flow Cooling Towers."

            - Heat wheels specified in Section 237223.13 "Packaged Indoor Heat Wheel Energy Recovery Units" and Section 237223.23 "Packaged, Outdoor, Heat Wheel Energy Recovery Units."

            - Heat exchangers specified in Section 237223.19 "Packaged Indoor Fixed Plate Energy Recovery Units" and Section 237223.29 "Packaged, Outdoor, Fixed Plate Energy Recovery Units"

            - Air-handling units specified in Section 237313.13 "Indoor, Basic Air-Handling Units."

            - Air-handling units specified in Section 237313.16 "Indoor, Semi-Custom Air-Handling Units."

            - Air-handling units specified in Section 237313.19 "Indoor, Custom Air-Handling Units."

            - Heating and ventilating units specified in Section 237333.16 "Indoor, Indirect, Gas-Fired Heating and Ventilating Units."

            - Heating and ventilating units specified in Section 237339 "Indoor, Direct-Fired Heating and Ventilating Units."

            - Air-handling units specified in Section 237343.16 "Outdoor, Semi-Custom Air-Handling Units."

            - Air-handling units specified in Section 237343.19 "Outdoor, Custom Air-Handling Units."

            - Roof-top units specified in Section 237416.11 "Packaged, Small-Capacity, Rooftop Air-Conditioning Units."

            - Roof-top units specified in Section 237416.13 "Packaged, Large-Capacity, Rooftop Air-Conditioning Units."

            - Make-up air units specified in Section 237423.13 "Packaged, Direct-Fired, Outdoor, Heating-Only Makeup-Air Units."

            - Make-up air units specified in Section 237423.16 "Packaged, Indirect-Fired, Outdoor, Heating-Only Makeup-Air Units."

            - Dedicated outdoor-air units specified in Section 237433 "Dedicated Outdoor-Air Units."

            - Packaged terminal air-conditioners specified in Section 238113.11 "Packaged Terminal Air-Conditioners, Through-Wall Units."

            - Packaged terminal air-conditioners specified in Section 238113.12 "Packaged Terminal Air-Conditioners, Freestanding Units."

            - Packaged terminal air-conditioners specified in Section 238113.13 "Packaged Terminal Air-Conditioners, Outdoor, Wall-Mounted Units."

            - Computer-room air-conditioning units specified in Section 238123.11 "Small Capacity (6 Tons (21 kW) and Smaller), Computer-Room Air-Conditioners, Floor-Mounted Units."

            - Computer-room air-conditioning units specified in Section 238123.12 "Large Capacity (7 Tons (25 kW) and Larger), Computer-Room Air-Conditioners, Floor-Mounted Units."

            - Computer-room air-conditioning units specified in Section 238123.13 "Computer-Room Air Conditioners, Ceiling-Mounted Units."

            - Computer-room air-conditioning units specified in Section 238123.14 "Computer-Room Air Conditioners, Console Units."

            - Computer-room, rack-mounted cooling equipment specified in Section 238123.18 "Computer-Room, Rack-Cooling Equipment."

            - Variable refrigerant flow units specified in Section 238129 "Variable-Refrigerant-Flow HVAC Systems."

            - Fan-coil units specified in Section 238219 "Fan Coil Units."

            - Unit ventilators specified in Section 238223 "Unit Ventilators."

            - Wetted-element humidifiers specified in Section 238413.16 "Wetted-Element Humidifiers."

            - Atomizing humidifiers specified in Section 238413.19 "Atomizing Humidifiers."

            - Direct-steam-injection humidifiers specified in Section 238413.23 "Direct-Steam-Injection Humidifiers."

            - Self-contained steam humidifiers specified in Section 238413.29 "Self-Contained Steam Humidifiers."

            - Heat exchanger humidifiers specified in Section 238413.36 "Heat Exchanger Humidifiers."

            - Dehumidification units specified in Section 238416.13 "Outdoor, Mechanical Dehumidification Units" and in Section 238416.16 "Indoor, Mechanical Dehumidification Units."

            - Switchboards specified in Section 262300 "Low-Voltage Switchgear."

            - Motor-control centers specified in Section 262419 "Motor-Control Centers."

            - Variable-frequency controllers specified in Section 262923 "Variable-Frequency Motor Controllers."

            - Diesel emergency engine generators specified in Section 263213.13 "Diesel-Engine-Driven Generator Sets."

            - Gaseous emergency engine generators specified in Section 263213.16 "Gas-Engine-Driven Generator Sets."

            - Bi-fuel emergency engine generators specified in Section 263213.19 "Bi-Fuel-Engine-Driven Generator Sets."

            - UPS specified in Section 263353 "Static Uninterruptible Power Supply."

            - Refrigerant monitoring specified in Section 284400 "Refrigerant Detection and Alarm."

            - <Insert equipment and Section number and title>.

Retain "Communication Interface to Other Building Systems" Paragraph below to require DDC system to interface with systems through a communication link.

        - Communication Interface to Other Building Systems:

          - DDC system communicates with systems having communication interface.

Retain "Systems to Be Connected" Subparagraph below to indicate systems to be connected; delete if systems to be connected are indicated on Drawings. Coordinate with Drawings.

          - Systems to Be Connected:

Coordinate specific interface requirements in Sections retained in remaining subparagraphs below.

            - Elevators specified in Section 142100 "Electric Traction Elevators."

            - Elevators specified in Section 142113 "Electric Traction Freight Elevators."

            - Elevators specified in Section 142400 "Hydraulic Elevators."

            - Elevators specified in Section 142413 "Hydraulic Freight Elevators."

            - Escalators specified in Section 143100 "Escalators."

            - Automated water treatment systems specified in Section 232500 "HVAC Water Treatment."

            - Automated water treatment systems specified in Section 232516 "Water Treatment for Open-Loop Hydronic Systems."

            - Automated water treatment systems specified in Section 232519 "Water Treatment for Steam System Feedwater."

            - Power monitoring specified in Section 260913 "Electrical Power Monitoring."

            - Lighting controls specified in Section 260936 "Modular Dimming Controls."

            - Lighting controls specified in Section 260943.16 "Addressable Luminaire Lighting Controls."

            - Lighting controls specified in Section 260943.23 "Relay-Based Lighting Controls."

            - Fire-alarm system specified in Section 284621.11 "Addressable Fire-Alarm Systems."

            - Fire-alarm system specified in Section 284621.13 "Conventional Fire-Alarm Systems."

            - Access controls specified in Section 281300 "Access Control System Software and Database Management."

            - Intrusion detection specified in Section 283100 "Intrusion Detection."

            - Perimeter security specified in Section 283121 "Area and Perimeter Intrusion Detection."

            - <Insert system and Section number and title>.

      - PREINSTALLATION INTEGRATION TESTING

Retain this article to require integration testing before field installation to reduce time required for field startup and checkout.

        - Perform the following pretesting of other systems and equipment integration with DDC system before field installation:

          - Test all communications in a controlled environment to ensure connectivity.

          - Load software and demonstrate functional compliance with each control sequence of operation indicated.

          - Using simulation, demonstrate compliance with sequences of operation and other requirements indicated including, but not limited to, the following:

            - HVAC equipment controlled through DDC system, such as boilers, chillers, pumps, and air-handling units.

            - Equipment faults and system recovery with fault annunciation.

            - Analog and Boolean value alarming and annunciation.

          - Develop a method for testing interfaces before deployment.

          - Submit documentation supporting compliance upon request.

      - DDC SYSTEM INTERFACE WITH EXISTING SYSTEMS

Retain "Interface with Existing Systems" Paragraph below to require DDC system to be connected to existing systems. Include special instructions in Document 002213 "Supplementary Instructions to Bidders" to instruct bidders to visit Project to become familiar with systems to be connected and available interface requirements and to report findings with bids.

        - Interface with Existing Systems:

          - Interface DDC systems with existing systems to achieve integration indicated.

Retain "Monitoring and Control of DDC System by Existing Control System" Subparagraph below when DDC system being installed is to integrate with existing system.

          - Monitoring and Control of DDC System by Existing Control System:

            - Satisfy DDC system performance requirements when monitoring and controlling DDC system by existing control system.

            - Operator of existing system to upload, download, monitor, trend, control, and program every I/O point in DDC system from existing control system using existing control system software and operator workstations.

            - Make interface so operator of existing system is not required to learn new software for remote monitoring and control from existing control system.

            - Make interface of DDC system into existing control system transparent to operators of existing control system and allow operators to [program, monitor, and control] [monitor and control] DDC system from any operator workstation connected to existing control system.

            - <Insert requirements>.

Retain "Integration of Existing Control System into DDC System" Subparagraph below to require existing system to be integrated into DDC system.

          - Integration of Existing Control System into DDC System:

            - Satisfy existing control system performance requirements when monitoring and controlling existing control system through DDC system.

            - Operator to upload, download, monitor, alarm, report, trend, control, and program every I/O point in existing system from DDC system using operator workstations and software provided. Combined systems to share one database.

            - Make interface of existing control system I/O points into DDC system transparent to operators. Make all operational capabilities identical regardless of whether I/O already exists, or I/O is being installed.

            - <Insert requirements>.

Retain "Integration with Existing Enterprise System" Paragraph below where required to connect to existing enterprise system.

        - Integration with Existing Enterprise System:

          - Interface DDC system with an existing enterprise system to adhere to Owner standards already in-place and to achieve integration.

Retain one of first two subparagraphs below where required to connect to existing enterprise system that requires services of Owner's existing control system integrator.

          - Owner's control system integrator to provide the following services:

            - Enterprise system expansion and development of graphics, logs, reports, trends, and other operational capabilities of enterprise system for I/O being added to DDC control system for use by enterprise system operators.

            - Limited assistance during commissioning to extent of DDC system integration with existing enterprise system.

            - Prepare on-site demonstration mockup of integration of DDC system to be installed with existing system before installing DDC system.

          - Engage Owner's control system integrator to provide the following services:

            - Enterprise system expansion and development of graphics, logs, reports, trends, and other operational capabilities of enterprise system for I/O being added to DDC control system for use by enterprise system operators.

            - Limited assistance during commissioning to extent of DDC system integration with existing enterprise system.

            - Prepare on-site demonstration mockup of integration of DDC system to be installed with existing system before installing DDC system.

          - Control System Integrator Contact Information:

            - Company: <Insert name>.

            - Company Street Address: <Insert address>.

            - Company Contact: <Insert name>.

            - Phone Number: <Insert phone number>.

            - Email Address: <Insert email address>.

          - Attend meetings with control system integrator to integrate DDC system.

      - CONTROL DEVICES FOR INSTALLATION BY INSTALLERS

Coordinate requirements in this article with requirements in Sections specifying the identified equipment and systems. This article includes examples of requirements but is not all-inclusive. Requirements must be revised to comply with specific Project requirements.

        - Deliver selected control devices, specified in indicated HVAC instrumentation and control device Sections, to identified equipment and systems manufacturers for factory installation and to identified installers for field installation.

Both paragraphs below are examples only. Retain and revise as applicable.

        - Deliver the following to duct fabricator and Installer for installation in ductwork. Include installation instructions to Installer and supervise installation for compliance with requirements.

          - Control dampers, which are specified in Section 230923.12 "Control Dampers."

          - Airflow sensors and switches, which are specified in Section 230923.14 "Flow Instruments."

          - Pressure sensors, which are specified in Section 230923.23 "Pressure Instruments."

          - <Insert additional control devices>.

        - Deliver the following to plumbing and HVAC piping installers for installation in piping. Include installation instructions to Installer and supervise installation for compliance with requirements.

          - Control valves, which are specified in Section 230923.11 "Control Valves."

          - Pipe-mounted flow meters, which are specified in Section 230923.14 "Flow Instruments."

          - Pipe-mounted sensors, switches, and transmitters. Flow meters are specified in Section 230923.14 "Flow Instruments."

          - Tank-mounted sensors, switches, and transmitters. Pressure sensors, switches, and transmitters are specified in Section 230923.23 "Pressure Instruments."

          - Liquid[ and steam] temperature sensors, switches, and transmitters are specified in Section 230923.27 "Temperature Instruments."

          - Pipe- and tank-mounted thermowells. Liquid[ and steam] thermowells are specified in Section 230923.27 "Temperature Instruments."

          - <Insert additional control devices>.

      - CONTROL DEVICES FOR EQUIPMENT MANUFACTURER FACTORY INSTALLATION

Paragraphs in this article are examples only. Retain and revise as applicable.

        - Deliver the following to air-handling unit manufacturer for factory installation. Include installation instructions to air-handling unit manufacturer[ and supervise installation for compliance with requirements].

          - [Programmable application] [or] [application-specific] controller.

          - Unit-mounted DDC control dampers and actuators, which are specified in Section 230923.12 "Control Dampers."

          - Unit-mounted airflow sensors, switches, and transmitters, which are specified in Section 230923.14 "Flow Instruments."

          - Unit-mounted gas sensors, and transmitters, which are specified in Section 230923.16 "Gas Instruments."

          - Unit-mounted leak-detection switches, which are specified in Section 230923.18 "Leak Detection Instruments."

          - Unit-mounted pressure sensors, switches, and transmitters, which are specified in Section 230923.23 "Pressure Instruments."

          - Unit-mounted speed sensors, switches, and transmitters, which are specified in Section 230923.24 "Speed Instruments."

          - Unit-mounted temperature sensors, switches, and transmitters. Air-temperature sensors, switches, and transmitters are specified in Section 230923.27 "Temperature Instruments."

          - Relays.

          - <Insert additional control devices>.

        - Deliver the following to terminal unit manufacturer for factory installation. Include installation instructions to terminal unit manufacturer.

          - [Programmable application] [or] [application-specific] controller.

          - Electric damper actuator. Damper actuators are specified in Section 230923.12 "Control Dampers."

          - Unit-mounted flow and pressure sensors, transmitters, and transducers. Flow sensors, transmitters, and transducers are specified in Section 230923.14 "Flow Instruments." Pressure sensors, switches, and transmitters are specified in Section 230923.23 "Pressure Instruments."

          - Unit-mounted temperature sensors. Air-temperature sensors, switches, and transmitters are specified in Section 230923.27 "Temperature Instruments."

          - Relays.

          - <Insert additional control devices>.

        - Deliver the following to fan-coil unit manufacturer for factory installation. Include installation instructions to fan-coil unit manufacturer.

          - [Programmable application] [or] [application-specific] controller.

          - Unit-mounted temperature sensors. Air-temperature sensors, switches, and transmitters are specified in Section 230923.27 "Temperature Instruments."

          - Flow and pressure switches. Air and liquid flow sensors, transmitters, and transducers are specified in Section 230923.14 "Flow Instruments." Pressure sensors, switches, and transmitters are specified in Section 230923.23 "Pressure Instruments."

          - Leak-detection switches, which are specified in Section 230923.18 "Leak Detection Instruments."

          - Relays.

          - <Insert control devices>.

      - GENERAL INSTALLATION REQUIREMENTS

        - Install products to satisfy more stringent of all requirements indicated.

        - Install products level, plumb, parallel, and perpendicular with building construction.

        - Support products, tubing, piping wiring, and raceways. Brace products to prevent lateral movement and sway or a break in attachment when subjected to <Insert value> force.

        - If codes and referenced standards are more stringent than requirements indicated, comply with requirements in codes and referenced standards.

        - Fabricate openings and install sleeves in ceilings, floors, roof, and walls required by installation of products. Before proceeding with drilling, punching, and cutting, check for concealed work to avoid damage. Patch, flash, grout, seal, and refinish openings to match adjacent condition.

        - Firestop Penetrations Made in Fire-Rated Assemblies: Comply with requirements in Section 078413 "Penetration Firestopping."

        - Seal penetrations made in acoustically rated assemblies. Comply with requirements in Section 079200 "Joint Sealants."

        - Welding Requirements:

          - Restrict welding and burning to supports and bracing.

          - No equipment is cut or welded without approval. Welding or cutting will not be approved if there is risk of damage to adjacent Work.

          - Welding, where approved, is to be by inert-gas electric arc process and is to be performed by qualified welders in accordance with applicable welding codes.

          - If requested on-site, show satisfactory evidence of welder certificates indicating ability to perform welding work intended.

        - Fastening Hardware:

          - Wrenches, pliers, and other tools that damage surfaces of rods, nuts, and other parts are prohibited for work of assembling and tightening fasteners.

          - Tighten bolts and nuts firmly and uniformly. Do not overstress threads by excessive force or by oversized wrenches.

          - Lubricate threads of bolts, nuts, and screws with graphite and oil before assembly.

        - If product locations are not indicated, install products in locations that are accessible and that will permit service and maintenance from floor, equipment platforms, or catwalks without removal of permanently installed furniture and equipment.

        - Corrosive Environments:

          - Avoid or limit use of materials in corrosive airstreams and environments including, but not limited to, the following:

            - Laboratory exhaust-air streams.

            - Process exhaust-air streams.

            - <Insert conditions>.

          - When conduit is in contact with a corrosive airstream and environment, use Type 316 stainless steel conduit and fittings or conduit and fittings that are coated with a corrosive-resistant coating that is suitable for environment. Comply with requirements for installation of raceways and boxes specified in Section 260533.13 "Conduits for Electrical Systems," Section 260533.16 "Boxes and Covers for Electrical Systems," and Section 260533.23 "Surface Raceways for Electrical Systems."

          - Where instruments are located in a corrosive airstream and are not already corrosive resistant from instrument manufacturer, field install products in NEMA 250, Type 4X instrument enclosure constructed of Type 316L stainless steel.

      - INSTALLATION OF WORKSTATIONS

        - Desktop Workstation Installation:

Retain option in first subparagraph below if workstations are not furnished with DDC system but are furnished by Owner. Consult Owner.

          - Install [Owner-furnished ]workstation(s) at location(s) indicated on Drawings.

          - Install multiple-receptacle power strip with cord for use in connecting multiple workstation components to a single, duplex, electrical power receptacle.

          - Install DDC system software on workstation(s) and verify that software functions properly.

          - Develop Project-specific graphics, trends, reports, logs, and historical database.

          - Power [each ]workstation through a [dedicated ]UPS unit. Locate UPS adjacent to workstation.

        - Portable Workstation Installation:

Retain option in subparagraph below if workstations are not furnished with DDC system but are furnished by Owner. Consult Owner.

          - Install DDC system software on [Owner-furnished ]workstation(s) and verify that software functions properly.

        - Color Graphics Application:

          - Use system schematics indicated on Drawings as starting point to create graphics.

          - Develop Project-specific library of symbols for representing system equipment and products.

          - Incorporate digital images of Project-completed installation into graphics where beneficial to enhance effect.

          - Submit sketch of graphic layout with description of all text for each graphic for Owner's[ and Architect's] review before creating graphic using graphics software.

          - Seek Owner input in graphics development once using graphics software.

          - Make final editing on-site with Owner's[ and Architect's] review and feedback.

          - Refine graphics as necessary for Owner acceptance.

          - On receiving Owner acceptance, print a PDF file of each graphic and include with softcopy of DDC system operation and maintenance manual.

Retain "Retractable, Wall-Mounted Cabinet for Portable Operator's Workstation Installation" Paragraph below for applications requiring a cabinet to house and support portable operator workstations. Consult Owner for need.

        - Retractable, Wall-Mounted Cabinet for Portable Operator's Workstation Installation:

Retain one of first two subparagraphs below.

          - Install retractable, wall-mounted portable operator's workstation cabinet(s) at location(s) indicated on Drawings.

          - Install retractable, wall-mounted portable operator's workstation cabinet(s) at following location(s) and at additional locations indicated on Drawings:

Retain any of first three subparagraphs below.

            - Each mechanical room.

            - Chiller room.

            - Boiler room.

            - <Insert location>.

          - Connect each cabinet to [120 V, single-phase, 60 Hz] <Insert power requirements> field power source and install single gang electrical box with [NEMA WD 6, Type 20R duplex] <Insert receptacle type> receptacle and metal cover plate in cabinet. Comply with requirements in Section 262726 "Wiring Devices."

          - Connect each cabinet to Ethernet network and install an Ethernet network port for connection to portable operator workstation Ethernet cable. Comply with requirements in Section 271513 "Communications Copper Horizontal Cabling."

      - INSTALLATION OF POT

Retain this article if operator access is provided at multiple locations and a portable operator workstation is not provided. Portable operator workstation is preferred because it provides operator with more capabilities.

Retain first paragraph below unless indicated on Drawings.

        - Install [one] [two] <Insert quantity> POT(s).

        - Turn over POTs to Owner at Substantial Completion.

        - Install software on each POT and verify that software functions properly.

      - INSTALLATION OF SERVERS

Retain one of first two paragraphs below if servers are not indicated on Drawings.

        - Install server(s) at location(s) indicated on Drawings.

        - Install number of servers required to suit requirements indicated. Review Project requirements and indicate layout of proposed server location in Shop Drawings.

        - Install software indicated on server(s) and verify that software functions properly.

        - Develop Project-specific graphics, trends, reports, logs, and historical database.

        - Power servers through [dedicated ]UPS unit. Locate UPS adjacent to server. Install rack-mounted UPS units for powering rack-mounted servers and tower UPS units for tower servers.

      - INSTALLATION OF PRINTERS

Retain option in first paragraph below if printers are not furnished with DDC system but furnished by Owner. Consult Owner.

        - Install [Owner-furnished ]printers at location(s) indicated on Drawings.

Retain option in paragraph below if workstations are not furnished with DDC system but furnished by Owner. Consult Owner.

        - Install applicable printer software on [Owner-furnished ]workstations and verify that software functions properly.

      - INSTALLATION OF GATEWAYS

Design of each gateway should include an interoperability schedule showing each point or event with interface requirements defined for each.

For BACnet DDC systems, include an interoperability schedule showing each point or event on non-BACnet side that BACnet "client" will read, and each parameter that BACnet network will write to for BACnet services, or BIBBs, defined in ASHRAE 135, Annex K.

        - Install gateways if required for DDC system communication interface requirements indicated.

          - Install gateway(s) required to suit indicated requirements.

            - <Insert requirements>.

        - Test gateways to verify that communication interface functions properly.

      - INSTALLATION OF ROUTERS

        - Install routers if required for DDC system communication interface requirements indicated.

          - Install router(s) required to suit indicated requirements.

            - <Insert requirements>.

        - Test routers to verify that communication interface functions properly.

      - INSTALLATION OF CONTROLLERS

        - Install controllers in enclosures to comply with indicated requirements.

        - Connect controllers to field power supply[ and to UPS units where indicated].

        - Install controllers with latest version of applicable software and configure to execute requirements indicated.

        - Test and adjust controllers to verify operation of connected I/O to achieve performance indicated requirements while executing sequences of operation.

        - Installation of Network Controllers:

          - DDC system provider and DDC system manufacturer to determine quantity and location of network controllers to satisfy requirements indicated.[ Provide minimum quantity indicated.]

          - Install controllers in a protected location that is easily accessible by operators.

          - Locate top of controller within [72 inches (1800 mm)] [84 inches (2100 mm)] <Insert dimension> of finished floor.

        - Installation of Programmable Application Controllers:

          - DDC system provider and DDC system manufacturer to determine quantity and location of programmable application controllers to satisfy requirements indicated.[ Provide minimum quantity indicated.]

          - Install controllers in a protected location that is easily accessible by operators.

          - Locate top of controller within [72 inches (1800 mm)] [84 inches (2100 mm)] <Insert dimension> of finished floor, except where dedicated controllers are installed at terminal units.

        - Application-Specific Controllers:

          - DDC system provider and DDC system manufacturer to determine quantity and location of application-specific controllers to satisfy requirements indicated.[ Provide minimum quantity indicated.]

          - For controllers not mounted directly on equipment being controlled, install controllers in a [protected ]location that is easily accessible by operators.

      - INSTALLATION OF WIRELESS ROUTERS FOR OPERATOR INTERFACE

        - Install wireless routers to achieve optimum performance and best possible coverage.

        - Mount wireless routers in a protected location that is within [60 inches (1500 mm)] <Insert requirement> of floor and easily accessible by operators.

        - Connect wireless routers to field power supply and to UPS units if network controllers are powered through UPS units.

        - Install wireless router with latest version of applicable software and configure wireless router with security and password protection. Create access password with not less than 12 characters consisting of letters and numbers and at least one special character. Document password in operations and maintenance manuals for reference by operators.

        - Test and adjust wireless routers for proper operation with all types (such as, laptops, smartphones, and tablets) of wireless devices intended for use by operators.

      - INSTALLATION OF ENCLOSURES

        - Install the following items in enclosures, to comply with indicated requirements:

Retain any of first nine subparagraphs below.

          - Gateways.

          - Routers.

          - Controllers.

          - Electrical power devices.

          - UPS units.

          - Relays.

          - Accessories.

          - Instruments.

          - Actuators.

          - <Insert devices>.

        - Attach wall-mounted enclosures to wall using the following types of steel struts:

          - For NEMA 250, [Type 1] <Insert type> Enclosures: Use [painted steel] [galvanized-steel] [corrosion-resistant-coated steel] strut and hardware.

          - For NEMA 250, [Type 4] [Type 4X] <Insert type> Enclosures and Enclosures Located Outdoors: Use stainless steel strut and hardware.

          - Install plastic caps on exposed cut edges of strut.

        - Align [top] [or] [bottom] of adjacent enclosures[ of like size].

        - Install floor-mounted enclosures located [in mechanical equipment rooms ]on concrete housekeeping pads. Attach enclosure legs using [galvanized-steel] [or] [stainless steel] anchors.

Retain paragraph below to require wireways to connect between adjacent enclosures. Wireways provide a neat and easily accessible alternative to conduit, but they may come at a higher cost for specific installation.

        - Install continuous and fully accessible wireways to connect conduit, wire, and cable to multiple adjacent enclosures. Wireways used for application are to have protection equal to NEMA 250 rating of connected enclosures.

      - ELECTRIC POWER CONNECTIONS

        - Connect electrical power to DDC system products requiring electrical power connections.

        - Design of electrical power to products not indicated with electric power is delegated to DDC system provider and installing trade to provide a fully functioning DDC system. Work is to comply with NFPA 70 and other requirements indicated.

        - Comply with requirements in Section 262816 "Enclosed Switches and Circuit Breakers" for electrical power circuit breakers.

        - Comply with requirements in Section 260519 "Low-Voltage Electrical Power Conductors and Cables" for electrical power conductors and cables.

        - Comply with requirements in Section 260533.13 "Conduits for Electrical Systems," Section 260533.16 "Boxes and Covers for Electrical Systems," and Section 260533.23 "Surface Raceways for Electrical Systems" for electrical power raceways and boxes.

      - INSTALLATION OF IDENTIFICATION

        - Identify system components, wiring, cabling, and terminals. Comply with requirements in Section 260553 "Identification for Electrical Systems" for identification products and installation.

Products in first paragraph below are described in Section 260553 "Identification for Electrical Systems."

        - Install [self-adhesive labels] [laminated acrylic or melamine plastic signs] with unique identification on face for each of the following:

          - Server.

          - Gateway.

          - Router.

          - Protocol analyzer.

          - DDC controller.

          - Enclosure.

          - Electrical power device.

          - UPS unit.

          - Accessory.

        - Install unique instrument identification for each instrument connected to DDC controller.

        - Install unique identification for each control [damper] [and] [valve] actuator connected to DDC controller.

Retain first two paragraphs below to enhance locating products installed above ceilings.

        - Where product is installed above accessible tile ceiling, also install matching identification on face of ceiling grid located directly below.

        - Where product is installed above an inaccessible ceiling, also install identification on face of access door directly below.

        - Warning Labels and Signs:

          - Permanently attach to equipment that can be automatically started by DDC control system.

          - Locate where highly visible near power service entry points.

      - INSTALLATION OF NETWORKS

Retain first paragraph below to require optical fiber cable when connecting networks across large distance.

        - Install optical fiber cable when connecting between the following network devices and when located in different buildings on campus, or when distance between devices exceeds <Insert distance>:

          - Operator workstations.

          - Operator workstations and network controllers.

          - Network controllers.

          - <Insert network device>.

        - Install balanced twisted pair [or optical fiber ]cable when connecting between the following network devices[ located in same building]:

          - Operator workstations.

          - Operator workstations and network controllers.

          - Network controllers.

          - <Insert network device>.

        - Install balanced twisted pair or copper cable (as required by equipment) when connecting between the following:

          - Gateways.

          - Gateways and network controllers or programmable application controllers.

          - Routers.

          - Routers and network controllers or programmable application controllers.

          - Network controllers and programmable application controllers.

          - Programmable application controllers.

          - Programmable application controllers and application-specific controllers.

          - Application-specific controllers.

          - <Insert network device>.

        - Install cable in continuous raceway.

          - Where indicated on Drawings, cable trays may be used for copper cable in lieu of conduit.

      - NETWORK NAMING AND NUMBERING

        - Coordinate with Owner and provide unique naming and addressing for networks and devices.

Retain "ASHRAE 135 Networks" Paragraph below for unique requirements to ASHRAE 135 networks.

        - ASHRAE 135 Networks:

          - MAC Address:

            - Assign and document a MAC address unique to its network for every network device.

            - Ethernet Networks: Document MAC address assigned at its creation.

            - MS/TP Networks: Assign from 00 to 64.

          - Network Numbering:

            - Assign unique numbers to each new network.

            - Provide ability for changing network number through device switches or operator interface.

            - DDC system, with all possible connected LANs, can contain up to 65,534 unique networks.

          - Device Object Identifier Property Number:

            - Assign unique device object identifier property numbers or device instances for each device network.

            - Provide for future modification of device instance number by device switches or operator interface.

            - LAN is to support up to 4,194,302 unique devices.

          - Device Object Name Property Text:

            - Device object name property field to support 32 minimum printable characters.

            - Assign unique device "Object Name" property names with plain-English descriptive names for each device.

              - Example 1: Device object name for device controlling heating water boiler plant at Building 1000 would be "Heating Water System Bldg. 1000."

              - Example 2: Device object name for VAV terminal unit controller could be "VAV Unit 102."

          - Object Name Property Text for Other Than Device Objects:

            - Object name property field is to support 32 minimum printable characters.

            - Assign object name properties with plain-English names descriptive of application.

              - Example 1: "Zone 1 Temperature."

              - Example 2 "Fan Start and Stop."

          - Object Identifier Property Number for Other Than Device Objects:

            - Assign object identifier property numbers according to [Drawings] [or] [tables] indicated.

            - If not indicated, object identifier property numbers may be assigned at Installer's discretion but must be approved by Owner in advance, be documented, and be unique for like object types within device.

      - INSTALLATION OF AIR SIGNAL PIPING AND TUBING

        - Above-Grade Air Signal Piping and Tubing Installation:

          - Material Application:

Retain one of first two subparagraphs below. Retain first subparagraph for projects not requiring galvanized-steel pipe.

            - Install copper tubing, except as follows:

              - Tubing Exposed to View: Polyethylene tubing installed in raceways may be used in lieu of copper tubing.

              - Concealed Tubing: Polyethylene tubing may be used in lieu of copper tubing when [concealed behind accessible ceilings] [and] [concealed in walls and connecting wall-mounted instruments with recessed connections].

            - Install copper tubing for sizes up through [NTS 1 (DN 25)] <Insert size> and install galvanized-steel pipe for larger sizes, except as follows:

              - Tubing Exposed to View: Polyethylene tubing installed in raceways may be used in lieu of copper tubing where exposed to view.

              - Concealed Tubing: Polyethylene tubing may be used in lieu of copper tubing when [concealed behind accessible ceilings] [and] [concealed in walls and connecting wall-mounted instruments with recessed connections].

Retain "Pneumatic Tubing" Subparagraph below where DDC system interfaces with pneumatic instruments, actuators, and accessories.

            - Pneumatic Tubing: Install copper tubing[, unless other accessible materials are indicated,] for pneumatic main and control signals to instruments including, but not limited to, the following:

              - Pneumatic actuators.

              - I/P transducers.

              - Sensors.

              - Switches.

              - Transmitters.

              - <Insert instrument>.

            - Install copper tubing[, unless other accessible materials are indicated,] for air signals to instruments including, but not limited to, the following:

              - Sensors.

              - Switches.

              - Transmitters.

              - <Insert instrument>.

            - Install drawn-temper copper tubing, except within 36 inches (900 mm) of device terminations tubing is to be annealed-tempered copper tubing.

            - Install compression fittings to connect copper tubing to instruments, control devices, and accessories.

            - Install [barbed] [or] [compression] fittings to connect polyethylene tubing to instruments, control devices, and accessories.

          - Routing:

            - Do not expose tubing in finished spaces, such as spaces with ceilings; occupied spaces, offices, and conference rooms, unless expressly approved in writing by Architect. Tubing may be exposed in areas without ceilings.

            - Where tubing is installed in finished occupied spaces, install the tubing in surface metal raceway with appropriate fittings only where not feasible to conceal in wall, above ceiling, or behind architectural enclosures or covers.

            - Install piping and tubing plumb and parallel to and at right angles with building construction.

            - Install multiple runs of tubing or piping in equally spaced parallel lines.

            - Install piping and tubing not to interfere with access to valves, equipment, duct, and equipment access doors, or obstruct personnel access and passageways of any kind.

            - Coordinate with other trades before installation to prevent proposed piping and tubing from interfering with pipe, duct, terminal equipment, light fixtures, conduit, and cable tray space. If changes to Shop Drawings are necessary due to field coordination, document changes on Record Drawings.

            - Install vibration loops in copper tubing when connecting to instruments and actuators that vibrate.

          - Support:

            - Space supports in accordance with MSS SP-58, except support spacing not to exceed 60 inches (1500 mm).

            - Support copper tubing with copper hangers, clips, and tube trays.

            - Do not use tape for support or dielectric isolation.

            - Install supports at each change in direction and at each branch take-off.

            - Attached supports to building structure independent of work of other trades. Support from ducts, pipes, cable trays, and conduits is prohibited.

            - Attached support from building structure with threaded rods, structural shapes, or channel strut.

            - Install and brace supports to carry static load plus a safety margin, which will allow tubing to be serviced.

            - Brace supports to prevent lateral movement.

            - Paint steel support members that are not galvanized or zinc coated.

            - Support polyethylene tubing same as copper tubing.

          - Do not attach piping and tubing to equipment that may be removed frequently for maintenance or that may impart vibration and expansion from temperature change.

Retain first subparagraph below for additional protection.

          - Protect exposed tubing in mechanical equipment rooms [and similar utility spaces ]from mechanical damage within [76 inches (1800 mm)] [84 inches (2100 mm)] [96 inches (2400 mm)] <Insert dimension> above floor. Use aluminum channel reversed and secured over tubing to protect tubing from damage.

          - Joining and Makeup:

            - Where joining and mating dissimilar metals where galvanic action could occur, install dielectric isolation.

            - Install dirt leg with an isolation valve and threaded plug at each main air, connection to panel, pneumatic pilot positioner, and PRV station.

            - Make threaded joints for connecting to instrument equipment with connectors with a compression tubing connector on one end and threaded connection on the other end.

            - Make tubing bends with tube-bending tool. Hard-bends or wrinkled or flattened bends are unacceptable.

            - Install tube fittings in accordance with manufacturer's written instructions.

            - Do not make tubing connections to a fitting before completing makeup of the connection.

            - Align tubing with fitting. Avoid springing tube into position; this may result in excessive stress on both tubing and fitting with possible resulting leaks.

            - Do not install fittings close to a bend. A length of straight tubing, not deformed by bending, is required for proper connection.

            - Check tubing for correct diameter and wall thickness.

            - Cut tube ends square and deburr. Exercise care during cutting to keep tubing round.

            - Thread pipe on a threading machine. Ream inner edges of pipe ends, and file and grind to remove burrs.

            - Wrap pipe threads with single wrap of PTFE tape.

            - Protect piping and tubing from entrance of foreign matter.

          - Do not exceed 50 percent fill capacity where tubing is installed in conduit. Support conduit in accordance with NFPA 70 unless otherwise indicated.

Retain "Below-Grade Signal Piping and Tubing Installation" Paragraph below for below-grade applications.

        - Below-Grade Air Signal Piping and Tubing Installation:

          - Install tubing below-grade in a continuous Schedule 80, PVC conduit.

          - Do not exceed 50 percent fill capacity; minimum size [2 inches (50 mm)] [4 inches (100 mm)] <Insert size>.

          - Install top of conduit at depth of at least [24 inches (600 mm)] [36 inches (900 mm)] <Insert distance> below finished grade.

          - Install tubing in raceways dedicated to only tubing. Do not combine electrical conductors and tubing in raceways.

        - Identify above-grade piping and tubing as follows:

          - Every 50 ft. (15 m) of straight run.

          - At least once for each branch within 36 inches (900 mm) of main tee.

          - At each change in direction.

          - Within 36 inches (900 mm) of each ceiling, floor, roof, and wall penetration.

          - Where exposed to and where concealed from view, including above ceiling plenums, shafts, and chases.

          - At each valve.

          - Mark each instrument tube connection with a number-coded identification. Each unique tube is to have same unique number at instrument connection and termination at opposite end of tube.

Retain "Valve Installation for Pneumatic Tubing" Paragraph below where DDC system interfaces with pneumatic instruments, actuators, and accessories.

        - Valve Installation for Pneumatic Tubing:

          - Install valves full size of piping and tubing.

          - Install at the following locations:

            - At each branch.

            - Before and after each PRV.

            - Before and after each air dryer.

            - At each control device.

          - Locate valves to be readily accessible from floor.

          - Install needle valves for isolation and throttling applications.[ Option to install ball valves in lieu of needle valves for isolation only applications.]

      - INSTALLATION OF PROCESS TUBING

        - Install process tubing for signal to instruments in liquid and steam systems. Instruments include, but are not limited to, the following:

          - Meters.

          - Sensors.

          - Switches.

          - Transmitters.

        - Support tubing in accordance with MSS SP-58, but at intervals no more than 60 inches (1500 mm) apart.

        - Install minimum NPS 1/2 (DN 15) process tubing for industrial-grade sensors, transmitters, and switches. Install bushings where required.

        - Make smooth tubing bends with a bending tool. Flattened or wrinkled bends are unacceptable.

        - Support tubing independent of other trades.

        - Route tubing parallel to and at right angles to building construction.

        - Install tubing concealed in areas with ceilings.

        - Install dirt leg with an isolation valve and threaded plug in drain valve at each connection to a transmitter and switch.

        - Insulate process piping and tubing connected to hot water and steam systems for personnel protection if surface temperature exceeds 120 deg F (49 deg C). Only insulate piping and tubing within maintenance personnel reach from floor, platform, or catwalk.

        - Wrap pipe threads of fitting in process tubing with service temperatures below 350 deg F (177 deg C) with single wrap of PTFE tape.

        - Coat pipe threads of fittings on process tubing in services with temperatures exceeding 350 deg F (177 deg C) with pipe compound before being made up to reduce possibility of galling.

        - Do not make tubing connections to a fitting before completing makeup of connection.

        - Check tubing for correct diameter and wall thickness. Cut the tube ends square and deburred. Exercise care during cutting to keep tubing round.

        - Do not install fittings close to a bend. Straight length of tubing, not deformed by bending, is required for proper connection.

        - Align tubing with fitting when installed. Avoid springing tube into position.

        - Install tubing with extreme care to keep foreign matter out of system. Plug open tubing ends to keep out dust, dirt, and moisture.

        - Do not attach tubing to equipment that may be removed frequently for maintenance or may impart vibration and expansion from temperature change.

Retain first paragraph below for additional protection.

        - Protect exposed tubing in mechanical equipment rooms from inadvertent mechanical damage within [76 inches (1800 mm)] [84 inches (2100 mm)] [96 inches (2400 mm)] <Insert dimension> above floor. Use aluminum channel reversed and secured over tubing to protect tubing from damage.

Retain "Below-Grade Process Tubing Installation" Paragraph below for below-grade applications.

        - Below-Grade Process Tubing Installation:

          - Install tubing below-grade in a continuous Schedule 80, PVC conduit.

          - Do not exceed 50 percent fill capacity; minimum size [2 inches (50 mm)] [4 inches (100 mm)] <Insert size>.

          - Install top of conduit at depth of at least [24 inches (600 mm)] [36 inches (900 mm)] <Insert distance> below finished grade.

          - Install tubing in raceways dedicated to only process tubing. Do not combine electrical conductors and tubing in raceways.

        - Identify above-grade process tubing as follows:

          - Every 50 ft. (15 m) of straight run.

          - At least once for each branch within 36 inches (900 mm) of main tee.

          - Near each change in direction.

          - Within 36 inches (900 mm) of each ceiling, floor, roof, and wall penetration.

          - Where exposed to and where concealed from view, including above ceiling plenums, shafts, and chases.

          - Near each isolation valve.

          - Mark each instrument tube connection with a number-coded identification. Each unique tube is to have same unique number at instrument connection and termination at opposite end of tube.

        - Process Tubing Isolation Valves Installation:

          - Install valves full size of piping and tubing.

          - Install isolation valves at the following locations:

            - Process connection.

            - Inlet to each instrument including, sensors, transmitters, switches, gauges, and other control devices.

          - Locate valves to be readily accessible from floor.

          - Install needle valves for isolation and throttling applications.[ Option to install ball valves in lieu of needle valves for isolation only applications.]

      - INSTALLATION OF CONTROL WIRE, CABLE, AND RACEWAY

        - Comply with NECA 1.

        - Wire and Cable Installation:

          - Comply with installation requirements in Section 260523 "Control-Voltage Electrical Power Cables."

          - Comply with installation requirements in Section 271313 "Communications Copper Backbone Cabling."

          - Comply with installation requirements in Section 271513 "Communications Copper Horizontal Cabling."

Requirements in first subparagraph below are in addition to those specified in Divisions 26 and 27 cabling Sections.

          - Install cables with protective sheathing that is waterproof and capable of withstanding continuous temperatures of 90 deg C with no measurable effect on physical and electrical properties of cable.

            - Provide shielding to prevent interference and distortion from adjacent cables and equipment.

          - Terminate wiring in a junction box.

            - Clamp cable over jacket in a junction box.

            - Individual conductors in the stripped section of cable is to be slack between the clamping point and terminal block.

          - Terminate field wiring and cable not directly connected to instruments and control devices having integral wiring terminals using terminal blocks.

          - Install signal transmission components in accordance with IEEE C2, REA Form 511a, NFPA 70, and as indicated.

          - Use shielded cable to transmitters.

          - Use shielded cable to temperature sensors.

          - Perform continuity and meager testing on wire and cable after installation.

        - Conduit Installation:

          - Comply with Section 260533.13 "Conduits for Electrical Systems," Section 260533.16 "Boxes and Covers for Electrical Systems," and Section 260533.23 "Surface Raceways for Electrical Systems" for control-voltage conductors.

          - Comply with Section 270528 "Pathways for Communications Systems" for balanced twisted pair cabling and optical fiber installation.

      - INSTALLATION OF OPTICAL FIBER CABLE SYSTEMS

        - Comply with installation requirements in Section 271323 "Communications Optical Fiber Backbone Cabling."

        - Comply with installation requirements in Section 271523 "Communications Optical Fiber Horizontal Cabling."

      - FIELD QUALITY CONTROL

Retain first option in "Testing Agency" Paragraph below if Owner hires an independent testing agency.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain "Manufacturer's Field Service" Paragraph below to require a factory-authorized service representative to perform tests and inspections.

        - Manufacturer's Field Service: Engage a factory-authorized service representative to test and inspect components, assemblies, and installations, including connections.

Retain "Tests and Inspections" Paragraph below to require Contractor to perform tests and inspections.

        - Tests and Inspections: Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

          - Perform each visual and mechanical inspection and electrical test stated in NETA ATS. Certify compliance with test parameters.

          - Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

        - Testing of Air-Signal Tubing:

          - Test for leaks and obstructions.

          - Disconnect each pipe and tubing line before test is performed, and blowout dust, dirt, trash, condensate, and other foreign materials with compressed air. Use commercially pure compressed air or nitrogen as distributed in gas cylinders. Use of compressed air from oil-free compressor with air dryer is an acceptable alternative for test.

          - After foreign matter is expelled and line is free from obstructions, plug far end of tubing run.

          - Connect pressure source to near end of tubing run with needle valve between air supply and tubing run.

          - Connect pressure gauge accurate to within 0.5 percent of test between shutoff needle valve and tubing run under test.

          - For air signal tubing, apply test pressure of [1.5] [2.0] <Insert value> times instrument operating pressure range. Record pressure in tubing run every 10 minutes for one hour. Allowable drop in pressure in one-hour period to not exceed [0.1] <Insert number> percent of test pressure.

Retain one of two subparagraphs below, or both, for pneumatic systems as applicable.

          - For pneumatic system pressures above 30 psig (207 kPa), apply pressure of [1.1] [1.5] <Insert value> times operating pressure to tubing run. Record pressure in tubing run every 10 minutes for one hour. Allowable drop in pressure in one-hour period to not exceed [1 psig (6.9 kPa)] <Insert value>.

          - For pneumatic system pressures 30 psig (207 kPa) and below, apply pressure of [1.5] [2.0] <Insert value> times operating pressure to tubing run. Record pressure in tubing run every five minutes for one hour. Allowable drop in pressure in one-hour period to not exceed [0.5 psig (3.5 kPa)] <Insert value>.

        - Optical Fiber Cable Testing:

          - Perform preinstallation, in-progress, and final tests, supplemented by additional tests, as necessary.

          - Preinstallation Cable Verification: Verify integrity and serviceability for new cable lengths before installation. This assurance may be provided by using vendor verification documents, testing, or other methods. At a minimum, furnish evidence of verification for cable attenuation and bandwidth parameters.

          - In-Progress Testing: Perform standard tests for correct pair identification and termination during installation to ensure proper installation and cable placement. Perform tests in addition to those specified if there is any reason to question condition of material furnished and installed. Testing accomplished is to be documented by agency conducting tests. Submit test results for Project record.

          - Final Testing: Perform final test of installed system to demonstrate acceptability as installed. Perform testing according to test plan supplied by DDC system manufacturer. Correct defective Work or material and retest. At a minimum, final testing for cable system, including spare cable, to verify compliance of attenuation, length, and bandwidth parameters with performance indicated.

          - Test Equipment: Use optical fiber time-domain reflectometer for testing of length and optical connectivity.

          - Test Results: Record test results and submit copy of test results for Project record.

      - DDC SYSTEM I/O CHECKOUT PROCEDURES

        - Check installed products before continuity tests, leak tests, and calibration.

        - Check instruments for proper location and accessibility.

        - Check instruments for proper installation on direction of flow, elevation, orientation, insertion depth, or other applicable considerations that will impact performance.

        - Check instrument tubing for proper isolation, fittings, slope, dirt legs, drains, material, and support.

Retain first paragraph below for pneumatic products.

        - For pneumatic products, verify that air supply for each product is properly installed.

        - Control Damper Checkout:

Retain first subparagraph below for pneumatic control dampers.

          - For pneumatic control dampers, verify that pressure gauges are provided in each air line connected to the damper actuator and positioner.

          - Verify that control dampers are installed correctly for flow direction.

          - Verify that proper blade alignment, either parallel or opposed, has been provided.

          - Verify that damper frame attachment is properly secured and sealed.

          - Verify that damper actuator and linkage attachment are secure.

          - Verify that actuator wiring is complete, enclosed, and connected to correct power source.

          - Verify that damper blade travel is unobstructed.

        - Control Valve Checkout:

Retain first subparagraph below for pneumatic control valves.

          - For pneumatic control valves, verify that pressure gauges are provided in each air line connected to the valve actuator and positioner.

          - Verify that control valves are installed correctly for flow direction.

          - Verify that valve body attachment is properly secured and sealed.

          - Verify that valve actuator and linkage attachment are secure.

          - Verify that actuator wiring is complete, enclosed, and connected to correct power source.

          - Verify that valve ball, disc, or plug travel is unobstructed.

          - After piping systems have been tested and put into service, but before insulating and balancing, inspect each valve for leaks. Adjust or replace packing to stop leaks. Replace valve if leaks persist.

        - Instrument Checkout:

          - Verify that instrument is correctly installed for location, orientation, direction, and operating clearances.

          - Verify that attachment is properly secured and sealed.

          - Verify that conduit connections are properly secured and sealed.

          - Verify that wiring is properly labeled with unique identification, correct type, and size and is securely attached to proper terminals.

          - Inspect instrument tag against approved submittal.

          - For instruments with tubing connections, verify that tubing attachment is secure and isolation valves have been provided.

          - For flow instruments, verify that recommended upstream and downstream distances have been maintained.

          - For temperature instruments, verify the following:

            - Sensing element type and proper material.

            - Length and insertion.

      - DDC SYSTEM I/O ADJUSTMENT, CALIBRATION, AND TESTING

        - Calibrate each instrument installed that is not factory calibrated and provided with calibration documentation.

        - Provide written description of proposed field procedures and equipment for calibrating each type of instrument. Submit procedures before calibration and adjustment.

        - For each analog instrument, make three-point test of calibration for both linearity and accuracy.

        - Equipment and procedures used for calibration to comply with instrument manufacturer's written instructions.

        - Provide diagnostic and test equipment for calibration and adjustment.

          - Use field testing and diagnostic instruments and equipment with an accuracy at least twice the instrument accuracy of instrument to be calibrated. For example, test and calibrate an installed instrument with accuracy of 1 percent using field testing and diagnostic instrument with accuracy of 0.5 percent or better.

        - Calibrate each instrument in accordance with instruction manual supplied by instrument manufacturer.

        - If after calibration the indicated performance cannot be achieved, replace out-of-tolerance instruments.

        - Comply with field testing requirements and procedures indicated by ASHRAE's Guideline 11, "Field Testing of HVAC Controls Components," in the absence of specific requirements, and to supplement requirements indicated.

        - Analog Signals:

          - Check analog voltage signals using a precision voltage meter at zero, 50, and 100 percent.

          - Check analog current signals using a precision current meter at zero, 50, and 100 percent.

          - Check resistance signals for temperature sensors at zero, 50, and 100 percent of operating span using a precision-resistant source.

        - Digital Signals:

          - Check digital signals using a jumper wire.

          - Check digital signals using an ohmmeter to test for contact making or breaking.

        - Control Dampers:

          - Stroke and adjust control dampers following manufacturer's recommended procedure, from 100 percent open to 100 percent closed and back to 100 percent open.

Retain first subparagraph below for pneumatic control dampers.

          - Stroke pneumatic control dampers with pilot positioners. Adjust damper and positioner following manufacturer's recommended procedure, so damper is 100 percent closed, 50 percent closed, and 100 percent open at proper air pressures.

          - Check and document open and close cycle times for applications with cycle time less than [30] <Insert number> seconds.

          - For control dampers equipped with positive position indication, check feedback signal at multiple positions to confirm proper position indication.

        - Control Valves:

          - Stroke and adjust control valves following manufacturer's recommended procedure, from 100 percent open to 100 percent closed and back to 100 percent open.

Retain first subparagraph below for pneumatic control valves.

          - Stroke pneumatic control valves with pilot positioners. Adjust valve and positioner following manufacturer's recommended procedure, so valve is 100 percent closed, 50 percent closed, and 100 percent open at proper air pressures.

          - Check and document open and close cycle times for applications with cycle time less than [30] <Insert number> seconds.

          - For control valves equipped with positive position indication, check feedback signal at multiple positions to confirm proper position indication.

        - Meters: Check meters at zero, 50, and 100 percent of Project design values.

        - Sensors: Check sensors at zero, 50, and 100 percent of Project design values.

        - Switches: Calibrate switches to make or break contact at set points indicated.

        - Transmitters:

          - Check and calibrate transmitters at zero, 50, and 100 percent of Project design values.

          - Calibrate resistance temperature transmitters at zero, 50, and 100 percent of span using a precision-resistant source.

      - DDC SYSTEM CONTROLLER CHECKOUT

        - Verify power supply.

          - Verify voltage, phase, and hertz.

          - Verify that protection from power surges is installed and functioning.

          - Verify that ground fault protection is installed.

          - If applicable, verify if connected to UPS unit.

          - If applicable, verify if connected to backup power source.

          - If applicable, verify that power conditioning units are installed.

        - Verify that wire and cabling are properly secured to terminals and labeled with unique identification.

        - Verify that spare I/O capacity is provided.

      - DDC CONTROLLER I/O CONTROL LOOP TESTS

        - Testing:

          - Test every I/O point connected to DDC controller to verify that safety and operating control set points are as indicated and as required to operate controlled system safely and at optimum performance.

          - Test every I/O point throughout its full operating range.

          - Test every control loop to verify that operation is stable and accurate.

          - Adjust control loop proportional, integral, and derivative settings to achieve optimum performance while complying with performance requirements indicated. Document testing of each control loop's precision and stability via trend logs.

          - Test and adjust every control loop for proper operation according to sequence of operation.

          - Test software and hardware interlocks for proper operation. Correct deficiencies.

          - Operate each analog point at the following:

            - Upper quarter of range.

            - Lower quarter of range.

            - At midpoint of range.

          - Exercise each binary point.

          - For every I/O point in DDC system, read and record each value at operator workstation, at DDC controller, and at field instrument simultaneously. Value displayed at operator workstation, at DDC controller, and at field instrument must match.

          - Prepare and submit report documenting results for each I/O point in DDC system and include in each I/O point a description of corrective measures and adjustments made to achieve desire results.

      - DDC SYSTEM VALIDATION TESTS

        - Perform validation tests before requesting final review of system. Before beginning testing, first submit Pretest Checklist and Test Plan.

        - After [review] [approval] of Pretest Checklist and Test Plan, execute all tests and procedures indicated in plan.

        - After testing is complete, submit completed Pretest Checklist.

        - Pretest Checklist: Submit the following list with items checked off once verified:

          - Detailed explanation for any items that are not completed or verified.

          - Required mechanical installation work is successfully completed and HVAC equipment is working correctly.

          - HVAC equipment motors operate below full-load amperage ratings.

          - Required DDC system components, wiring, and accessories are installed.

          - Installed DDC system architecture matches approved Drawings.

          - Control electric power circuits operate at proper voltage and are free from faults.

          - Required surge protection is installed.

          - DDC system network communications function properly, including uploading and downloading programming changes.

Retain first subparagraph below if applicable to Project.

          - Using BACnet protocol analyzer, verify that communications are error free.

          - Each controller's programming is backed up.

          - Equipment, products, tubing, wiring cable, and conduits are properly labeled.

          - All I/O points are programmed into controllers.

          - Testing, adjusting, and balancing work affecting controls is complete.

          - Dampers and actuators zero and span adjustments are set properly.

          - Each control damper and actuator goes to failed position on loss of power[ and loss of signal].

          - Valves and actuators zero and span adjustments are set properly.

          - Each control valve and actuator goes to failed position on loss of power[ and loss of signal].

          - Meter, sensor, and transmitter readings are accurate and calibrated.

          - Control loops are tuned for smooth and stable operation.

          - View trend data where applicable.

          - Each controller works properly in standalone mode.

          - Safety controls and devices function properly.

          - Interfaces with fire-alarm system function properly.

          - Electrical interlocks function properly.

          - Operator workstations and other interfaces are delivered, all system and database software is installed, and graphics are created.

          - Record Drawings are completed.

          - <Insert additional requirements>.

        - Test Plan:

          - Prepare and submit validation Test Plan including test procedures for performance validation tests.

          - Address all specified functions of DDC system and sequences of operation in Test Plan.

          - Explain detailed actions and expected results to demonstrate compliance with requirements indicated.

          - Explain method for simulating necessary conditions of operation used to demonstrate performance.

          - Include Test Checklist to be used to check and initial that each test has been successfully completed.

          - Submit Test Plan documentation [10] [20] <Insert number> business days before start of tests.

        - Validation Test:

          - Verify operating performance of each I/O point in DDC system.

            - Verify analog I/O points at operating value.

            - Make adjustments to out-of-tolerance I/O points.

              - Identify I/O points for future reference.

              - Simulate abnormal conditions to demonstrate proper function of safety devices.

              - Replace instruments and controllers that cannot maintain performance indicated after adjustments.

          - Simulate conditions to demonstrate proper sequence of control.

          - Readjust settings to design values and observe ability of DDC system to establish desired conditions.

          - 24 hours after initial validation test, do as follows:

            - Re-check I/O points that required corrections during initial test.

            - Identify I/O points that still require additional correction and make corrections necessary to achieve desired results.

          - 24 Hours after second validation test, do as follows:

            - Re-check I/O points that required corrections during second test.

            - Continue validation testing until I/O point is normal on two consecutive tests.

          - Completely check out, calibrate, and test all connected hardware and software to ensure that DDC system performs according to requirements indicated.

          - After validation testing is complete, prepare and submit report indicating results of testing. For all I/O points that required correction, indicate how many validation re-tests it took to pass. Identify adjustments made for each test and indicate instruments that were replaced.

Retain "DDC System Response Time Test" Paragraph below for Projects requiring more elaborate testing of system speed.

        - DDC System Response Time Test:

          - Simulate HLC.

            - Heavy load to be occurrence of [50] <Insert number> percent of total connected binary COV, one-half of which represents "alarm" condition, and [50] <Insert number> percent of total connected analog COV, one-half of which represents "alarm" condition, that are initiated simultaneously on a one-time basis.

          - Initiate 10 successive occurrences of HLC and measure response time to typical alarms and status changes.

          - Measure with timer having at least 0.1-second resolution and 0.01 percent accuracy.

          - Purpose of test is to demonstrate DDC system, as follows:

            - Reaction to COV and alarm conditions during HLC.

            - Ability to update DDC system database during HLC.

          - Passing test is contingent on the following:

            - Alarm reporting at printer beginning no more than [two] <Insert number> seconds after initiation (time zero) of HLC.

            - All alarms, both binary and analog, are reported and printed; none are lost.

            - Compliance with response times specified.

          - Prepare and submit report documenting HLC tested and results of test including time stamp and print out of all alarms.

Retain "DDC System Network Bandwidth Test" Paragraph below for projects requiring more elaborate testing of system speed.

        - DDC System Network Bandwidth Test:

          - Test network bandwidth usage on all DDC system networks to demonstrate bandwidth usage under DDC system normal operating conditions and under simulated HLC.

          - To pass, none of DDC system networks are to use more than 70 percent of available bandwidth under normal and HLC operation.

      - VERIFICATION OF DDC SYSTEM WIRELESS NETWORK

        - DDC system Installer is to design wireless DDC system networks to comply with performance requirements indicated.

        - Verify wireless network performance through field testing and document results in a field test report.

        - Testing and verification of all wireless devices to include, but not be limited to, the following:

          - Speed.

          - Online status.

          - Signal strength.

      - FINAL REVIEW

        - Submit written request to Architect [Owner] [Commissioning Agent] [and] [Construction Manager] when DDC system is ready for final review. State the following:

          - DDC system has been thoroughly inspected for compliance with Contract Documents and found to be in full compliance.

          - DDC system has been calibrated, adjusted, and tested and found to comply with requirements of operational stability, accuracy, speed, and other performance requirements indicated.

          - DDC system monitoring and control of HVAC systems results in operation according to sequences of operation indicated.

          - DDC system is complete and ready for final review.

          - <Insert additional requirements>.

        - Upon receipt of written request for final review, [Architect] [Owner] [Commissioning Agent] [and] [Construction Manager] to start review within [xx business days] [reasonable period] and upon completion issue field report(s) documenting observations and deficiencies.

        - Take prompt action to remedy deficiencies indicated in reviewer's field report(s) and submit second written request after all deficiencies have been corrected. Repeat process until no deficiencies are reported.

Retain first paragraph below to address additional compensation for additional reviews of deficient work. Consult Owner.

        - Compensation for Subsequent Reviews: Should more than [two] <Insert number> reviews be required, DDC system manufacturer and Installer to compensate entity/entities performing reviews for total costs (labor and expenses) associated with subsequent reviews. Estimated cost of each subsequent review to be submitted and approved by DDC system manufacturer and Installer before review.

        - Prepare and submit closeout submittals[ and begin procedures indicated in "Extended Operation Test" Article] when no deficiencies are reported.

        - Part of DDC system final review to include demonstration to parties participating in final review.

          - Provide staff familiar with DDC system installed to demonstrate operation of DDC system during final review.

          - Provide testing equipment to demonstrate accuracy and other performance requirements of DDC system that is requested by reviewers during final review.

          - Demonstration to include, but not be limited to, the following:

Subparagraphs below are examples only and must be revised to suit Project.

            - Accuracy and calibration of [10] [20] <Insert number> I/O points randomly selected by reviewers. If review finds that some I/O points are not properly calibrated and not satisfying performance requirements indicated, additional I/O points may be selected by reviewers until total I/O points being reviewed that satisfy requirements equals quantity indicated.

            - HVAC equipment and system hardwired and software safeties and life-safety functions are operating according to sequence of operation. Up to [10] [20] <Insert number> I/O points to be randomly selected by reviewers. Additional I/O points may be selected by reviewers to discover problems with operation.

            - Correct sequence of operation after electrical power interruption and resumption after electrical power is restored for randomly selected HVAC systems.

            - Operation of randomly selected dampers and valves in normal-on, normal-off, and failed positions.

            - Reporting of alarm conditions for randomly selected alarms, including different classes of alarms, to ensure that alarms are properly received by operators and operator workstations.

            - Trends, summaries, logs, and reports set up for Project.

            - For up to [three] <Insert number> HVAC systems randomly selected by reviewers, use graph trends to show that sequence of operation is executed in correct manner and that HVAC systems operate properly through complete sequence of operation including different modes of operations indicated. Show that control loops are stable and operating at set points and respond to changes in set point of 20 percent or more.

            - Software's ability to communicate with controllers, operator workstations, and uploading and downloading of control programs.

            - Software's ability to edit control programs offline.

            - Data entry to show Project-specific customizing capability including parameter changes.

            - Step through penetration tree, display all graphics, demonstrate dynamic update, and direct access to graphics.

            - Execution of digital and analog commands in graphic mode.

            - Spreadsheet and curve plot software and its integration with database.

            - Online user guide and help functions.

            - Multitasking by showing different operations occurring simultaneously on four quadrants of split screen.

            - System speed of response compared to requirements indicated.

            - For Each Controller: Applies to [network] [and] [programmable application] controllers.

              - Memory: Programmed data, parameters, trend, and alarm history collected during normal operation are not to be lost during power failure.

              - Operator Interface: Ability to connect directly to each type of digital controller with portable workstation and mobile device. Show that maintenance personnel interface tools perform as indicated in manufacturer's technical literature.

              - Standalone Ability: Demonstrate that controllers provide stable and reliable standalone operation using default values or other method for values normally read over network.

              - Electric Power: Ability to disconnect any controller safely from its power source.

              - Wiring Labels: Match control drawings.

              - Network Communication: Ability to locate controller's location on network and communication architecture matches Shop Drawings.

              - Nameplates and Tags: Accurate and permanently attached to control panel doors, instrument, actuators, and devices.

            - For Each Operator Workstation:

              - I/O points lists agree with naming conventions.

              - Graphics are complete.

              - UPS unit, if applicable, operates.

            - Communications and Interoperability: Demonstrate proper interoperability of data sharing, alarm and event management, trending, scheduling, and device and network management.[ Use ASHRAE 135 protocol analyzer to help identify devices, view network traffic, and verify interoperability.] Requirements must be met even if only one manufacturer's equipment is installed.

              - Data Presentation: On each operator workstation, demonstrate graphic display capabilities.

              - Reading of Any Property: Demonstrate ability to read and display any used readable object property of any device on network.

              - Set-Point and Parameter Modifications: Show ability to modify set points and tuning parameters indicated.[ Modifications are made with messages and write services initiated by operator using workstation graphics, or by completing a field in menu with instructional text.]

              - Peer-to-Peer Data Exchange: Network devices are installed and configured to perform without need for operator intervention to implement Project sequence of operation and to share global data.

              - Alarm and Event Management: Alarms and events are installed and prioritized according to Owner. Demonstrate that time delays and other logic are set up to avoid nuisance tripping. Show that operators with sufficient privileges are permitted.

              - Schedule Lists: Schedules are configured for start and stop, mode change, occupant overrides, and night setback as defined in sequence of operations.

              - Schedule Display and Modification: Ability to display any schedule with start and stop times for calendar year. Show that all calendar entries and schedules are modifiable from any connected operator workstation by an operator with sufficient privilege.

              - Archival Storage of Data: Data archiving is handled by operator workstation and server and local trend archiving and display is accomplished.

              - Modification of Trend Log Object Parameters: Operator with sufficient privilege can change logged data points, sampling rate, and trend duration.

              - Device and Network Management:

                - Display of network device status.

                - Display of BACnet object information.

                - Silencing devices transmitting erroneous data.

                - Time synchronization.

                - Remote device re-initialization.

                - Backup and restore network device programming and master database(s).

                - Configuration management of routers.

            - <Insert additional requirements>.

      - EXTENDED OPERATION TEST

Retain this article when documentation of proper DDC system operation over an extended operating period is required. Extended operation test is intended to simulate normal operation of DDC system by Owner. Consult Owner to confirm if test is desired due to added cost.

        - Operate DDC system for operating period of [14] [21] [28] <Insert number> consecutive calendar days following Substantial Completion. Coordinate exact start date of testing with Owner.

        - Provide operator familiar with DDC system installed to man an operator workstation [while on-site ]during eight hours of each normal business day occurring during operating period.

        - During operating period, DDC system to demonstrate correct operation and accuracy of monitored and controlled points as well as operation capabilities of sequences, logs, trends, reports, specialized control algorithms, diagnostics, and other software indicated.

          - Correct defects of hardware and software when they occur.

        - Definition of Failures and Downtime during Operating Period:

          - Failed I/O point constituting downtime is I/O point failing to perform its intended function consistently and a point physically failed due to hardware and software.

          - Downtime is when any I/O point in DDC system is unable to fulfill its required function.

          - Calculate downtime as elapsed time between detected point failure as confirmed by operator, and time point is restored to service.

          - Maximum time interval allowed between DDC system detection of failure occurrence and operator confirmation is to be 0.5 hours.

          - Log downtime in hours to nearest 0.1 hour.

          - Power outages do not count as downtime, but do suspend test hours unless systems are provided with UPS and served through a backup power source.

          - Hardware or software failures caused by power outages do count as downtime.

        - During operating period, log downtime and operational problems are encountered.

          - Identify source of problem.

          - Provide written description of corrective action taken.

          - Record duration of downtime.

          - Maintain log showing the following:

            - Time of occurrence.

            - Description of each occurrence and pertinent written comments for reviewer to understand scope and extent of occurrence.

            - Downtime for each failed I/O point.

            - Running total of downtime and total time of I/O point after each problem has been restored.

          - Make log available to Owner for review at any time.

        - For DDC system to pass extended operation test, total downtime is limited to [1] [2] <Insert number> percent of total point-hours during operating period.

          - If DDC system testing results fail to comply with minimum requirements of passing at end of operating period indicated, extend operating period one consecutive day at a time until DDC system passes requirement.

        - Base evaluation of DDC system passing test on the following calculation:

          - Count downtime on point-hour basis where total number of DDC system point-hours is equal to total number of I/O points in DDC system multiplied by total number of hours during operating period.

          - One point-hour of downtime is one I/O point down for one hour. For example, three I/O points down for five hours is total of 15 point-hours of downtime. Four points down for one-half hour is two point-hours of downtime.

          - Example Calculation: Maximum allowable downtime for 30-day test for DDC system with 1000 total I/O points (combined analog and binary) and passing score of 1 percent downtime is computed by 30 days x 24 h/day x 1000 points x 1 percent equals 7200 point-hours of maximum allowable downtime.

        - Prepare test and inspection reports.

      - ADJUSTING

        - Occupancy Adjustments: When requested within [12] <Insert number> months from date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions. Provide up to [two] <Insert number> visits to Project during other-than-normal occupancy hours for this purpose.

      - MAINTENANCE SERVICE

Verify, with Owner, that maintenance service is required for Project.

        - Beginning at Substantial Completion, verify that maintenance service includes [three] [six] [nine] [12] <Insert number> months' full maintenance by DDC system manufacturer's authorized service representative. Include [monthly] [quarterly] [semiannual] [annual] preventive maintenance, repair or replacement of worn or defective components, cleaning, calibration, and adjusting as required for proper operation. Use only manufacturer's authorized replacement parts and supplies.

      - SOFTWARE SERVICE AGREEMENT

Services in this article may not be allowed for publicly funded projects.

        - Technical Support: Beginning at Substantial Completion, verify that service agreement includes software support for [one] [two] <Insert number> year(s).

        - Upgrade Service: At Substantial Completion, update software to latest version. Install and program software upgrades that become available within [one] [two] <Insert number> year(s) from date of Substantial Completion. Verify that upgrading software includes operating system and new or revised licenses for using software.

          - Upgrade Notice: No fewer than [30] <Insert number> days to allow Owner to schedule and access system and to upgrade computer equipment if necessary.

      - DEMONSTRATION

Revise this article to suit scope of DDC system for Project. Not all requirements indicated may be applicable.

        - Engage a factory-authorized service representative with complete knowledge of Project-specific system installed to train Owner's maintenance personnel to adjust, operate, and maintain DDC system.

        - Extent of Training:

          - Base extent of training on scope and complexity of DDC system indicated and training requirements indicated. Provide extent of training required to satisfy requirements indicated even if more than minimum training requirements are indicated.

          - Inform Owner of anticipated training requirements if more than minimum training requirements are indicated.

          - Minimum Training Requirements:

Revise subparagraphs below to suit unique requirements of DDC system and other Project requirements. Consult Owner for assistance in establishing minimum requirements.

            - Provide not less than [five] [10] [15] <Insert number> days of training total.

            - Stagger training over multiple training classes to accommodate Owner's requirements. All training to occur before end of warranty period.

            - Break down total days of training into not more than [two] [three] [four] <Insert number> separate training classes.

            - Schedule training so each training class is not less than [one] [two] [three] <Insert number> consecutive day(s).

        - Training Schedule:

          - Schedule training with Owner [20] <Insert number> business days before expected Substantial Completion.

          - Schedule training to provide Owner with at least [10] [15] [20] <Insert number> business days of notice in advance of training.

          - Training to occur within normal business hours at mutually agreed on time. Unless otherwise agreed to, training to occur Monday through Friday, except on U.S. Federal holidays, with two morning sessions and two afternoon sessions. Each morning session and afternoon session to be split in half with [15] [30] <Insert number>-minute break between sessions. Morning and afternoon sessions to be separated by [30] [60] <Insert number>-minute lunch period. Training, including breaks and excluding lunch period, are not to exceed [eight] <Insert number> hours per day.

          - Provide staggered training schedule as requested by Owner.

        - Training Attendee List and Sign-in Sheet:

          - Request from Owner in advance of training a proposed attendee list with name, phone number, and email address.

          - Provide preprinted sign-in sheet for each training session with proposed attendees listed and no fewer than six blank spaces to add additional attendees.

          - Include preprinted sign-in sheet with training session number, date and time, instructor name, phone number, email address, and brief description of content to be covered during session. List attendees with columns for name, phone number, and email address and a column for attendee signature or initials.

          - Circulate sign-in sheet at beginning of each session and solicit attendees to sign or initial in applicable location.

          - At end of each training day, send Owner an email with attachment of scanned copy (PDF) of circulated sign-in sheet for each session.[ Indicate which attendees, if any, joined for only part of training sessions].

        - Training Attendee Headcount:

          - Plan in advance of training for [two] [three] [five] <Insert number> attendees.

          - Make allowance for Owner to add up to [one] [two] <Insert number> attendee(s) at time of training.

          - Headcount may vary depending on training content covered in session. Attendee access may be restricted to some training content for purposes of maintaining system security.

        - Training Attendee Prior Knowledge: For guidance in planning required training and instruction, assume attendees have the following:

Revise subparagraphs below to suit Owner personnel being trained. Consult Owner for assistance.

          - [High school] [High school and technical school] [High school and four-year college] <Insert level> education and degree.

          - [Basic] [Intermediate] [Advanced] user knowledge of computers and office applications.

          - [Basic] [Intermediate] [Advanced] knowledge of HVAC systems.

          - [Basic] [Intermediate] [Advanced] knowledge of DDC systems.

          - [Basic] [Intermediate] [Advanced] knowledge of DDC system and products installed.

        - Attendee Training Manuals:

          - Provide each attendee with color hard copy of all training materials and visual presentations.

          - Organize hard-copy materials in three-ring binder with table of contents and individual divider tabs marked for each logical grouping of subject matter. Organize material to provide space for attendees to take handwritten notes within training manuals.

          - In addition to hard-copy materials included in training manual, provide each binder with a sleeve or pocket that includes DVD or flash drive with PDF copy of all hard-copy materials.

        - Instructor Requirements:

          - One or multiple qualified instructors, as required, to provide training.

          - Use instructors who have provided not less than [five] <Insert number> years of instructional training on not less than [five] <Insert number> past projects with similar DDC system scope and complexity to DDC system installed.

        - Organization of Training Sessions:

          - Organize training sessions into logical groupings of technical content and to reflect different levels of operators having access to system. Plan training sessions to accommodate the following three levels of operators:

            - Daily operators.

            - Advanced operators.

            - System managers and administrators.

          - Plan and organize training sessions to group training content to protect DDC system security. Some attendees may be restricted to some training sessions to ensure DDC system security.

        - Training Outline:

          - Submit training outline for Owner review at least [10] <Insert number> business day before scheduling training.

          - Include in outline a detailed agenda for each training day that is broken down into each of four training sessions that day, training objectives for each training session, and synopses for each lesson planned.

        - On-Site Training:

          - Owner will provide conditioned classroom or workspace with ample desks or tables, chairs, power, and data connectivity for instructor and each attendee.

          - Provide training materials, projector, and other audiovisual equipment used in training.

          - Provide as much of training located on-site as deemed feasible and practical by Owner.

          - Include on-site training with regular walk-through tours, as required, to observe each unique product type installed with hands-on review of operation, calibration, and service requirements.

          - Use operator workstation that is to be used with DDC system in the training. If operator workstations are unavailable, provide temporary workstation to convey training content.

        - Off-Site Training:

          - Provide conditioned training rooms and workspace with ample tables desks or tables, chairs, power, and data connectivity for each attendee.

Retain first subparagraph below if DDC system is capable of remote access.

          - Provide capability to remotely access to Project DDC system for use in training.

          - Provide operator workstation for use by each attendee.

        - Training Content for Daily Operators:

Subparagraphs below are examples only and must be revised to suit Project.

          - Basic operation of system.

          - Understanding DDC system architecture and configuration.

          - Understanding each unique product type installed including performance and service requirements for each.

          - Understanding operation of each system and equipment controlled by DDC system including sequences of operation, each unique control algorithm, and each unique optimization routine.

          - Operating operator workstations, printers, and other peripherals.

          - Logging on and off system.

          - Accessing graphics, reports, and alarms.

          - Adjusting and changing set points and time schedules.

          - Recognizing DDC system malfunctions.

          - Understanding content of operation and maintenance manuals including control drawings.

          - Understanding physical location and placement of DDC controllers and I/O hardware.

          - Accessing data from DDC controllers.

          - Operating portable operator workstations.

          - Review of DDC testing results to establish basic understanding of DDC system operating performance and HVAC system limitations as of Substantial Completion.

          - Running each specified report and log.

          - Displaying and demonstrating each data entry to show Project-specific customizing capability. Demonstrating parameter changes.

          - Stepping through graphics penetration tree, displaying all graphics, demonstrating dynamic updating, and direct access to graphics.

          - Executing digital and analog commands in graphic mode.

          - Demonstrating control loop precision and stability via trend logs of I/O for not less than 10 percent of I/O installed.

          - Demonstrating DDC system performance through trend logs and command tracing.

          - Demonstrating scan, update, and alarm responsiveness.

          - Demonstrating spreadsheet and curve plot software, and its integration with database.

          - Demonstrating on-line user guide, and help function and mail facility.

          - Demonstrating multitasking by showing dynamic curve plot, and graphic construction operating simultaneously via split screen.

          - Demonstrating the following for HVAC systems and equipment controlled by DDC system:

            - Operation of HVAC equipment in normal-off, normal-on, and failed conditions while observing individual equipment, dampers, and valves for correct position under each condition.

            - For HVAC equipment with factory-installed software, show that integration into DDC system is able to communicate with DDC controllers or gateways, as applicable.

            - Using graphed trends, show that sequence of operation is executed in correct manner, and HVAC systems operate properly through complete sequence of operation including seasonal change, occupied and unoccupied modes, warm-up and cool-down cycles, and other modes of operation indicated.

            - Hardware interlocks and safeties function properly and DDC system performs correct sequence of operation after electrical power interruption and resumption after power is restored.

            - Reporting of alarm conditions for each alarm, and confirm that alarms are received at assigned locations, including operator workstations.

            - Each control loop responds to set-point adjustment and stabilizes within time period indicated.

            - Sharing of previously graphed trends of all control loops to demonstrate that each control loop is stable and set points are being maintained.

            - <Insert requirement>.

        - Training Content for Advanced Operators:

Subparagraphs below are examples only and must be revised to suit Project.

          - Making and changing workstation graphics.

          - Creating, deleting, and modifying alarms including annunciation and routing.

          - Creating, deleting, and modifying point trend logs including graphing and printing on an ad-hoc basis and operator-defined time intervals.

          - Creating, deleting, and modifying reports.

          - Creating, deleting, and modifying points.

          - Creating, deleting, and modifying programming including ability to edit control programs offline.

          - Creating, deleting, and modifying system graphics and other types of displays.

          - Adding DDC controllers and other network communication devices such as gateways and routers.

          - Adding operator workstations.

          - Performing DDC system checkout and diagnostic procedures.

          - Performing DDC controllers operation and maintenance procedures.

          - Performing operator workstation operation and maintenance procedures.

          - Configuring DDC system hardware including controllers, workstations, communication devices, and I/O points.

          - Maintaining, calibrating, troubleshooting, diagnosing, and repairing hardware.

          - Adjusting, calibrating, and replacing DDC system components.

          - <Insert requirement>.

        - Training Content for System Managers and Administrators:

Subparagraphs below are examples only.

          - DDC system software maintenance and backups.

          - Uploading, downloading, and offline archiving of all DDC system software and databases.

          - Interface with Project-specific, third-party operator software.

          - Understanding password and security procedures.

          - Adding new operators and making modifications to existing operators.

          - Operator password assignments and modification.

          - Operator authority assignment and modification.

          - Workstation data segregation and modification.

          - <Insert requirement>.

        - Video of Training Sessions:

          - Provide digital video and audio recording of each training session. Create separate recording file for each session.

          - Stamp each recording file with training session number, session name, and date.

          - Provide Owner with [two] <Insert number> copies of digital files on cloud and flash drives for later reference and for use in future training.

          - Owner retains right to make additional copies for intended training purposes without having to pay royalties.

END OF SECTION 230923