Copyright 2022 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 230923.12 - CONTROL DAMPERS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Rectangular control dampers with airfoil blades.

          - Rectangular control dampers with flat blades.

          - Rectangular control dampers with insulated blades.

          - Rectangular control dampers with integral airflow monitoring.

          - Rectangular control dampers with integral airflow control.

          - Rectangular industrial-duty control dampers.

          - Round control dampers.

          - Round industrial-duty control dampers.

          - Electric and electronic control-damper actuators.

          - Pneumatic control-damper actuators.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 230923 "Direct Digital Control (DDC) System for HVAC" for control equipment and software, relays, electrical power devices, uninterruptible power supply units, wire, and cable.

          - Section 230993.11 "Sequence of Operations for HVAC DDC" for requirements that relate to this Section.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - DDC: Direct digital control.

        - RMS: Root-mean-square value of alternating voltage, which is the square root of the mean value of the square of the voltage values during a complete cycle.

        - Thermal Efficiency Ratio (E): Comparison of a tested damper's thermal performance against a v-groove blade reference damper. A damper with the same thermal efficiency as the reference damper would have an E value of 0 percent, while a damper that is 4 times as efficient would have an E value of 200 percent.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

          - Rectangular control dampers with airfoil blades.

          - Rectangular control dampers with flat blades.

          - Rectangular control dampers with insulated blades.

          - Rectangular control dampers with integral airflow monitoring.

          - Rectangular control dampers with integral airflow control.

          - Rectangular industrial-duty control dampers.

          - Round control dampers.

          - Round industrial-duty control dampers.

          - Electric and electronic control-damper actuators.

          - Pneumatic control-damper actuators.

        - Product Data Submittals: For each damper and actuator.

          - Construction details, material descriptions, dimensions of individual components and profiles, and finishes.

          - Operating characteristics, electrical characteristics, and furnished accessories indicating process operating range, accuracy over range, control signal over range, default control signal with loss of power, calibration data specific to each unique application, electrical power requirements, and limitations of ambient operating environment, including temperature and humidity.

          - Product description with complete technical data, performance curves, and product specification sheets.

          - Installation instructions, including factors affecting performance.

        - Shop Drawings:

          - Include plans, elevations, sections, and[ mounting] details.

          - Include details of product assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

          - Include diagrams for power, signal, and control wiring.

Retain subparagraph below for dampers with pneumatic actuators.

          - Include diagrams for pneumatic signal and main air tubing.

Retain "Delegated Design Submittals" Paragraph below if design services have been delegated to Contractor.

        - Delegated Design Submittals:

          - Schedule and design calculations for control dampers and actuators, including the following:

            - Unique designation for each damper/actuator assembly.

            - Service/application.

            - Damper assembly size.

            - Damper assembly weight, including actuator(s).

            - Damper and actuator action (modulating or two position).

            - Flow at project design and minimum flow conditions.

            - Face velocity at project design and minimum airflow conditions.

            - Pressure drop across damper at project design and minimum airflow conditions.

            - AMCA 500D damper installation arrangement used to calculate and schedule pressure drop, as applicable to installation.

            - Maximum close-off pressure.

            - Leakage airflow at maximum system pressure differential (fan close-off pressure).

            - Damper torque required at worst-case condition for sizing actuator.

            - Actuator selection indicating torque provided.

            - Actuator fail-safe position on loss of power and loss of signal.

            - Remarks listing special requirements.

      - INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Coordinate paragraph with other Sections specifying products listed below. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

        - Coordination Drawings: Plan drawings and corresponding product installation details, drawn to scale, on which the following items are indicated and coordinated with each other, using input from installers of the items involved:

          - Product installation location indicated in relationship to room, duct, and equipment.

          - Size and location of wall access panels for control dampers and actuators installed behind walls.

          - Size and location of ceiling access panels for control dampers and actuators installed above inaccessible ceilings.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For control dampers.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - PERFORMANCE REQUIREMENTS

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

"ASHRAE 62.1 Compliance" Paragraph below may be required to comply with Project requirements or authorities having jurisdiction. Sustainable design may require compliance with requirements in ASHRAE 62.1, including requirements for airflow controls. Verify, with manufacturers, the availability of product components and features that comply with these requirements.

        - ASHRAE 62.1 Compliance: Applicable outdoor ventilation requirements in ASHRAE 62.1, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

"ASHRAE/IES 90.1 Compliance" Paragraph below may be required to comply with Project requirements or authorities having jurisdiction. Sustainable design may require minimum efficiency equal to requirements in ASHRAE/IES 90.1. Insert a specific version of the standard if required to satisfy a Project sustainability requirement.

        - ASHRAE/IES 90.1 Compliance: Applicable requirements in ASHRAE/IES 90.1, Section 6 - "Heating, Ventilating, and Air-Conditioning."

        - Code Compliance: Comply with governing energy code.

Retain "Delegated Design" Paragraph below if Contractor is required to assume responsibility for design.

        - Delegated Design: Engage a qualified professional[ engineer], as defined in Section 014000 "Quality Requirements," to size products where indicated as delegated design.

        - Ground Fault: Properly ground products to prevent failing due to ground fault conditions.

        - Backup Power Source: Serve control-damper actuators from a backup power source where associated with systems and equipment served by a backup power source.

        - Environmental Conditions: For actuators not available with integral enclosures complying with requirements indicated, house in protective secondary enclosures complying with requirements.

        - Selection Criteria:

For projects with varying requirements for each different application, indicate requirements on Drawings.

          - Multi-Blade Damper Configuration: [See Drawings] [As follows unless otherwise indicated on Drawings]:

Retain any of first six subparagraphs below if blade configuration is not indicated on Drawings.

            - Two-Position Control: [Opposed] [or] [parallel].

            - Equipment Isolation Applications: [Opposed] [or] [parallel].

            - Face and Bypass Applications: [Opposed] [or] [parallel].

            - Outdoor/Return Air-Mixing Applications: [Opposed] [or] [parallel].

            - All Other Applications: [Opposed] [or] [parallel].

            - <Insert application>.

          - Pressure and Temperature: Control dampers suitable for operating conditions encountered by the application[ and following conditions unless otherwise indicated on Drawings]:

Retain any of first six subparagraphs below if operating conditions are not indicated on Drawings.

            - Supply Air: <Insert pressure and coincident temperature requirements>.

            - Return Air: <Insert pressure and coincident temperature requirements>.

            - Outdoor Air: <Insert pressure and coincident temperature requirements>.

            - Mixed Air: <Insert pressure and coincident temperature requirements>.

            - Exhaust Air: <Insert pressure and coincident temperature requirements>.

            - <Insert system and requirements>.

For projects with varying requirements for each different application, indicate requirements on Drawings.

          - Fail-Safe Positions: [See Drawings] [As follows unless otherwise indicated on Drawings]:

            - Supply Air: [Close] [Last position] [Open].

            - Return Air: [Close] [Last position] [Open].

            - Outdoor Air: [Close] [Last position] [Open].

            - Mixed Air: [Close] [Last position] [Open].

            - Exhaust Air: [Close] [Last position] [Open].

            - <Insert system and requirements>.

          - Select dampers with smooth and stable operation throughout full range of operation over varying pressures and temperatures encountered.

Retain second option in "Sizing" Subparagraph below if control-damper size is not indicated on Drawings.

          - Sizing: [See Drawings] [As follows unless otherwise indicated on Drawings]

            - Modulating Dampers: Select damper size for a pressure drop of <Insert number> percent of fan total static pressure unless otherwise indicated.

            - Two-Position Dampers: Full size of duct or equipment connection unless otherwise indicated.

Retain "Pneumatic, Two-Position Control-Damper Opening and Closing Characteristic" Subparagraph below for pneumatic two-position control dampers with special installation requirements.

          - Pneumatic, Two-Position Control-Damper Opening and Closing Characteristic:

            - Provide a smooth opening and closing characteristic slow enough to avoid an excessive rapid change in system pressure.

            - Provide an adjustable opening time (full closed to full open) and an adjustable closing time (full open to full closed) ranging from zero to [10] [15] [30] <Insert value> seconds. Make opening and closing times independently adjustable.

Retain "Pneumatic Control Signal Distance Limitation" Subparagraph below to restrict installation requirements.

          - Pneumatic Control Signal Distance Limitation: Not to exceed [100 ft. (30 m)] [200 ft. (60 m)] <Insert distance> from controller. For longer distances, provide an electric/electronic control signal to the damper/actuator and an electric solenoid valve or electro-pneumatic transducer locally at the damper/actuator to convert the control signal to pneumatic.

      - RECTANGULAR CONTROL DAMPERS WITH AIRFOIL BLADES

        - General Requirements:

          - Factory assemble multiple damper sections to provide a single damper assembly of size required by the application.

            - Include multisection damper assemblies with intermediate reinforcing where required between individual sections being joined together. Construct reinforcing of same material (aluminum, galvanized steel, stainless steel) as damper frame.

Retain subparagraph below for damper manufacturer to have single-source responsibility for damper assembly with actuators.

          - Factory install actuator(s) as integral part of damper assembly. Coordinate, with damper manufacturer, field requirements for actuators, such as type, fail-safe position, power supply, location, and mounting requirements.

        - Rectangular Control Dampers with Aluminum Airfoil Blades and Frames:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

All listed manufacturers may not offer products that comply with all requirements and options indicated; consult manufacturers.

          - Source Limitations: Obtain rectangular control dampers, with aluminum airfoil blades and frames, from single manufacturer.

"AMCA Certification" Subparagraph below requires test results to be verified by AMCA staff and the manufacturer to have obtained the proper license from AMCA, in order for the products to bear AMCA's Certified Ratings Seal for air performance, air leakage, or both. Consult manufacturers.

          - [AMCA Certification: Test, rate, and seal, in accordance with AMCA 511 for air performance and air leakage.]

          - Performance:

            - Leakage:

              - AMCA 511, Class 1A, at 1 in. wg (250 Pa) Differential Static Pressure: Leakage not to exceed 3 cfm/sq. ft. (15.2 L/s per sq. m) against 1 in. wg (250 Pa) differential static pressure when tested in accordance with AMCA 500D.

              - AMCA 511, Class 1, at 4 in. wg (1000 Pa) Differential Static Pressure: Leakage not to exceed 8 cfm/sq. ft. (40.6 L/s per sq. m) against 4 in. wg (1000 Pa) differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop: [0.05 in. wg (12.5 Pa)] <Insert pressure drop> at [1500 fpm (7.6 m/s)] <Insert velocity> across a [24-by-24-inch (600-by-600-mm)] <Insert size> damper when tested in accordance with AMCA 500D, figure [5.3] <Insert figure no.>.

            - Pressure Rating: Damper close-off pressure equal to [fan shutoff pressure] <Insert requirement> with a maximum blade deflection of [1/180] <Insert deflection> of blade length.

            - Temperature: [Minus 40 to plus 250 deg F (Minus 40 to plus 121 deg C)] <Insert temperature range>.

            - Velocity: Up to [4000 fpm (20 m/s)] [6000 fpm (30 m/s)] <Insert velocity>.

          - Construction:

            - Frame:

              - Material: ASTM B211/B211M, Alloy 6063 T5 extruded-aluminum profiles, minimum [0.125 inch (3 mm)] <Insert thickness> thick.

              - Arrangement: Hat-shaped channel with integral extended face flange(s) having mating face of minimum [1 inch (25 mm)] [1-1/2 inches (38 mm)] [2 inches (50 mm)] <Insert size> for attachment to duct flanges, plenum walls, and equipment.

              - Width: Not less than [5 inches (125 mm)] <Insert width>.

            - Blades:

              - Configuration: Parallel or opposed blade configuration as required by application.

              - Material: ASTM B211/B211M, Alloy 6063 T5 extruded-aluminum profiles, [0.07 inch (1.8 mm)] <Insert thickness> thick.

              - Shape: Hollow, airfoil.

              - Length: As required by close-off pressure rating, not to exceed [48 inches (1200 mm)] <Insert length>.

              - Width: Not to exceed [6 inches (150 mm)] <Insert width>.

            - Seals:

              - Blades: Replaceable; extruded Santoprene, silicone, [or damper manufacturer-offered equivalent, ]as required by performance requirements. Seals are mechanically attached in extruded blade slots.

Retaining option in "Jambs" Subparagraph below is less restrictive. Not all listed manufacturers offer stainless steel compression-type jamb seals. Some use silicone seals.

              - Jambs: Replaceable; stainless steel, compression type[ or mechanically attached extruded silicone].

            - Axles:

              - Diameter: Minimum [0.375 inch (10 mm)] [0.5 inch (13 mm)] <Insert diameter>.

              - Material: [Aluminum,] [plated steel] [or] [stainless steel] [, specific to application indicated].

              - Mechanically attached to blades.

            - Bearings:

              - Material: Molded [acetal] [Celcon/polycarbonate] [nylon] [synthetic] [or] stainless steel sleeve, as required by operating conditions, mounted in frame.

              - Where blade axles are installed in vertical position, provide thrust bearings.

            - Linkage:

              - Hardware: [Plated] [or] [stainless] steel.

              - Material: [Aluminum,] [plated steel] [or] [stainless steel] [, specific to application indicated].

              - Mounting: Concealed in frame.

Retain "Transitions with Sleeve" Subparagraph below for manufacturer to include close transitions as integral part of factory damper assembly for field connection to round and flat oval ducts.

            - Transitions with Sleeve:

              - For round and flat oval duct applications, provide damper assembly with integral transitions to mate to adjoining field connections.

              - Factory mount damper in a sleeve with a close transition to mate to field connection.

                - Sleeve length not less than [12 inches (300 mm)] <Insert length> for dampers without jackshafts and not less than [16 inches (450 mm)] <Insert length> for dampers with jackshafts.

                - Oversize damper and sleeve for duct connection size plus minimum [4 inches (100 mm)] <Insert dimension>.

              - Fabricate sleeve and transitions of materials (aluminum, galvanized steel or stainless steel) to match damper frame[ or adjoining duct].

              - Match end connections (flange or sleeve) to field connections.

Retain "Additional Corrosion Protection for Corrosive Environments" Subparagraph below for applications requiring additional protection against corrosion.

            - Additional Corrosion Protection for Corrosive Environments:

Retain one of first two subparagraphs below, or both. Consult damper manufacturer for finish options best suited for a specific application. First subparagraph is sometimes used where dampers are exposed to coastal climates. If requirements differ by damper application, indicate requirements for each different application on Drawings.

              - Provide anodized finish, minimum of 0.0007 inch (0.018 mm) thick, for aluminum surfaces in contact with airstream.

              - Paint surfaces exposed to airstream with an [enamel] [or] [epoxy] <Insert finish> finish. Prepare surfaces to be painted according to paint manufacturer's instructions.

              - Construct axles, damper linkage, and hardware of Type 316L stainless steel.

        - Rectangular Control Dampers with Galvanized-Steel Airfoil Blades and Frames:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain rectangular control dampers, with galvanized-steel airfoil blades and frames, from single manufacturer.

All listed manufacturers may not offer products that comply with all requirements and options indicated; consult manufacturers.

"AMCA Certification" Subparagraph below requires test results to be verified by AMCA staff and the manufacturer to have obtained the proper license from AMCA, in order for the products to bear AMCA's Certified Ratings Seal for air performance, air leakage, or both. Consult manufacturers.

          - [AMCA Certification: Test, rate, and seal, in accordance with AMCA 511 for air performance and air leakage.]

          - Performance:

            - Leakage:

              - AMCA 511, Class 1A, at 1 in. wg (250 Pa) Differential Static Pressure: Leakage not to exceed 3 cfm/sq. ft. (15.2 L/s per sq. m) against 1 in. wg (250 Pa) differential static pressure when tested in accordance with AMCA 500D.

              - AMCA 511, Class 1, at 4 in. wg (1000 Pa) Differential Static Pressure: Leakage not to exceed 8 cfm/sq. ft. (40.6 L/s per sq. m) against 4 in. wg (1000 Pa) differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop: [0.06 in. wg (15 Pa)] <Insert pressure drop> at [1500 fpm (7.6 m/s)] <Insert velocity> across a [24-by-24-inch (600-by-600-mm)] <Insert size> damper when tested in accordance with AMCA 500D, figure [5.3] <Insert figure no.>.

            - Pressure Rating: Damper close-off pressure equal to [fan shutoff pressure] <Insert requirement> with a maximum blade deflection of [1/180] <Insert deflection> of blade length.

            - Temperature: [Minus 40 to plus 250 deg F (Minus 40 to plus 121 deg C)] <Insert temperature range>.

            - Velocity: Up to [4000 fpm (20 m/s)] [6000 fpm (30 m/s)] <Insert velocity>.

          - Construction:

            - Frame:

              - Material: ASTM A653/A653M galvanized steel, minimum [0.06 inch (1.6 mm)] <Insert thickness> thick.

              - Arrangement: Hat-shaped channel with integral extended face flange(s) having mating face of minimum [1 inch (25 mm)] [1-1/2 inches (38 mm)] [2 inches (50 mm)] <Insert size> for attachment to duct flanges, plenum walls, and equipment.

              - Width: Not less than [5 inches (125 mm)] <Insert width>.

            - Blades:

              - Configuration: Parallel or opposed blade configuration as required by application.

              - Material: ASTM A653/A653M galvanized steel, [0.05 inch (1.3 mm)] <Insert thickness> thick.

              - Shape: Hollow, airfoil.

              - Length: As required by close-off pressure rating, not to exceed [48 inches (1200 mm)] <Insert length>.

              - Width: Not to exceed [8 inches (200 mm)] <Insert width>.

            - Seals:

              - Blades: Replaceable; extruded silicone, vinyl, [or damper manufacturer-offered equivalent, ]as required by performance requirements. Seals are to be mechanically attached in extruded blade slots.

              - Jambs: Stainless steel, compression type.

            - Axles:

              - Diameter: Minimum [0.375 inch (10 mm)] [0.5 inch (13 mm)] <Insert diameter>.

              - Material: [Plated steel] [or] [stainless steel] [, specific to application indicated].

              - Mechanically attached to blades.

            - Bearings:

              - Material: Molded [acetal] [nylon] [or] stainless steel sleeve, as required by operating conditions, mounted in frame.

              - Where blade axles are installed in vertical position, provide thrust bearings.

            - Linkage:

              - Hardware: [Plated] [or] [stainless] steel.

              - Material: [Plated steel] [or] [stainless steel] [, specific to application indicated].

              - Mounting: Concealed in frame.

Retain "Transitions with Sleeve" Subparagraph below for manufacturer to include close transitions as integral part of factory damper assembly for field connection to round and flat oval ducts.

            - Transitions with Sleeve:

              - For round and flat oval duct applications, provide damper assembly with integral transitions to mate to adjoining field connections.

              - Factory mount damper in a sleeve with a close transition to mate to field connection.

                - Sleeve length not less than [12 inches (300 mm)] <Insert length> for dampers without jackshafts and not less than [16 inches (450 mm)] <Insert length> for dampers with jackshafts.

                - Oversize damper and sleeve for duct connection size plus minimum [4 inches (100 mm)] <Insert dimension>.

              - Fabricate sleeve and transitions of galvanized steel.

              - Match end connections (flange or sleeve) to field connections.

Retain "Additional Corrosion Protection for Corrosive Environments" Subparagraph below for applications requiring additional protection against corrosion. If requirements differ by damper application, indicate requirements for each different application on Drawings.

            - Additional Corrosion Protection for Corrosive Environments:

              - Paint surfaces exposed to airstream with an [enamel] [or] [epoxy] <Insert finish> finish. Prepare surfaces to be painted according to paint manufacturer's instructions.

        - Rectangular Control Dampers with Stainless Steel Airfoil Blades and Frames:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain rectangular control dampers, with stainless steel airfoil blades and frames, from single manufacturer.

All listed manufacturers may not offer products that comply with all requirements and options indicated; consult manufacturers.

"AMCA Certification" Subparagraph below requires test results to be verified by AMCA staff and the manufacturer to have obtained the proper license from AMCA, in order for the products to bear AMCA's Certified Ratings Seal for air performance, air leakage, or both. Consult manufacturers.

          - [AMCA Certification: Test, rate, and seal, in accordance with AMCA 511 for air performance and air leakage.]

          - Performance:

            - Leakage:

              - AMCA 511, Class 1A, at 1 in. wg (250 Pa) Differential Static Pressure: Leakage not to exceed 3 cfm/sq. ft. (15.2 L/s per sq. m) against 1 in. wg (250 Pa) differential static pressure when tested in accordance with AMCA 500D.

              - AMCA 511, Class 1, at 4 in. wg (1000 Pa) Differential Static Pressure: Leakage not to exceed 8 cfm/sq. ft. (40.6 L/s per sq. m) against 4 in. wg (1000 Pa) differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop: [0.06 in. wg (15 Pa)] <Insert pressure drop> at [1500 fpm (7.6 m/s)] <Insert velocity> across a [24-by-24-inch (600-by-600-mm)] <Insert size> damper when tested in accordance with AMCA 500D, figure [5.3] <Insert figure no.>.

            - Pressure Rating: Damper close-off pressure equal to [fan shutoff pressure] <Insert requirement> with a maximum blade deflection of [1/180] <Insert deflection> of blade length.

            - Temperature: [Minus 40 to plus 250 deg F (Minus 40 to plus 121 deg C)] <Insert temperature range>.

            - Velocity: Up to [4000 fpm (20 m/s)] <Insert velocity>.

          - Construction:

            - Frame:

              - Material: Type 304 stainless steel, minimum [0.06 inch (1.6 mm)] <Insert thickness> thick.

              - Arrangement: Hat-shaped channel with integral extended face flange(s) having mating face of minimum [1 inch (25 mm)] [1-1/2 inches (38 mm)] [2 inches (50 mm)] <Insert size> for attachment to duct flanges, plenum walls, and equipment.

              - Width: Not less than [5 inches (125 mm)] <Insert width>.

            - Blades:

              - Configuration: Parallel or opposed blade configuration as required by application.

              - Material: Type 304 stainless steel, [0.05 inch (1.3 mm)] <Insert thickness> thick.

              - Shape: Hollow, airfoil.

              - Length: As required by close-off pressure rating, not to exceed [48 inches (1200 mm)] <Insert length>.

              - Width: Not to exceed [8 inches (200 mm)] <Insert width>.

            - Seals:

              - Blades: Replaceable; extruded silicone as required by performance requirements. Seals are to be mechanically attached in extruded blade slots.

              - Jambs: Stainless steel, compression type.

            - Axles:

              - Diameter: Minimum [0.375 inch (10 mm)] [0.5 inch (13 mm)] <Insert diameter>.

              - Material: Type 303 or 304 stainless steel.

              - Mechanically attached to blades.

            - Bearings:

              - Material: [Molded nylon or ]stainless steel sleeve, as required by operating conditions, mounted in frame.

              - Where blade axles are installed in vertical position, provide thrust bearings.

            - Linkage:

              - Hardware: Stainless steel.

              - Material: Type 304 or 316 stainless steel.

              - Mounting: Concealed in frame.

Retain "Transitions with Sleeve" Subparagraph below for manufacturer to include close transitions as integral part of factory damper assembly for field connection to round and flat oval ducts.

            - Transitions with Sleeve:

              - For round and flat oval duct applications, provide damper assembly with integral transitions to mate to adjoining field connections.

              - Factory mount damper in a sleeve with a close transition to mate to field connection.

                - Sleeve length not less than [12 inches (300 mm)] <Insert length> for dampers without jackshafts and not less than [16 inches (450 mm)] <Insert length> for dampers with jackshafts.

                - Oversize damper and sleeve for duct connection size plus minimum [4 inches (100 mm)] <Insert dimension>.

              - Fabricate sleeve and transitions of materials to match damper frame.

              - Match end connections (flange or sleeve) to field connections.

      - RECTANGULAR CONTROL DAMPERS WITH FLAT BLADES

        - General Requirements:

          - Factory assemble multiple damper sections to provide a single damper assembly of size required by the application.

            - Include multisection damper assemblies with intermediate reinforcing where required between individual sections being joined together. Construct reinforcing of same material (aluminum, galvanized steel, stainless steel) as damper frame.

Retain subparagraph below for damper manufacturer to have single-source responsibility for damper assembly with actuators.

          - Factory install actuator(s) as integral part of damper assembly. Coordinate, with damper manufacturer, field requirements for actuators, such as type, fail-safe position, power supply, location, and mounting requirements.

        - Rectangular Control Dampers with Aluminum Flat Blades and Frames:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain rectangular control dampers, with aluminum flat blades and frames, from single manufacturer.

All listed manufacturers may not offer products that comply with all requirements and options indicated; consult manufacturers.

"AMCA Certification" Subparagraph below requires test results to be verified by AMCA staff and the manufacturer to have obtained the proper license from AMCA, in order for the products to bear AMCA's Certified Ratings Seal for air performance, air leakage, or both. Consult manufacturers.

          - [AMCA Certification: Test, rate, and seal, in accordance with AMCA 511 for air performance and air leakage.]

          - Performance:

            - Leakage:

              - AMCA 511, Class 1, at 1 in. wg (250 Pa) Differential Static Pressure: Leakage not to exceed 3.2 cfm/sq. ft. (16.2 L/s per sq. m) against 1 in. wg (250 Pa) differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop: [0.08 in. wg (20 Pa)] <Insert pressure drop> at [1500 fpm (7.6 m/s)] <Insert velocity> across a [24-by-24-inch (600-by-600-mm)] <Insert size> damper when tested in accordance with AMCA 500D, figure [5.3] <Insert figure no.>.

            - Pressure Rating: [2.0 in. wg (500 Pa)] <Insert pressure>.

            - Temperature: [Minus 40 to plus 250 deg F (Minus 40 to plus 121 deg C)] <Insert temperature range>.

            - Velocity: Up to [2000 fpm (10 m/s)] <Insert velocity>.

          - Construction:

            - Frame:

              - Material: ASTM B211/B211M, Alloy 6063 T5 extruded-aluminum profiles, minimum [0.08 inch (2 mm)] [0.125 inch (3 mm)] thick.

              - Arrangement: Hat-shaped channel with integral extended face flange(s) having mating face of minimum [1 inch (25 mm)] [1-1/2 inches (38 mm)] [2 inches (50 mm)] <Insert size> for attachment to duct flanges, plenum walls and equipment.

              - Width: Not less than 5 inches (125 mm).

            - Blades:

              - Configuration: Parallel or opposed blade configuration as required by application.

              - Material: ASTM B211/B211M, Alloy 6063 T5 extruded-aluminum profiles, 0.125 inch (3 mm) thick.

              - Shape: Single thickness.

              - Length: As required by pressure rating, not to exceed [48 inches (1200 mm)] <Insert length>.

              - Width: Not to exceed 6 inches (150 mm).

            - Seals:

              - Blades: Replaceable; extruded silicone or vinyl, as required by performance requirements. Mechanically attached in extruded blade slots.

              - Jambs: Stainless steel, compression type.

            - Axles:

              - Diameter: Minimum 0.5 inch (13 mm).

              - Material: Aluminum or plated steel.

              - Mechanically attached to blades.

            - Bearings:

              - Material: Celcon, polycarbonate or synthetic, mounted in frame.

            - Linkage:

              - Hardware: Plated or stainless steel.

              - Material: Aluminum or plated steel.

              - Mounting: Concealed in frame.

Retain "Additional Corrosion Protection for Corrosive Environments" Subparagraph below for applications requiring additional protection against corrosion. Consult damper manufacturer for finish options best suited for a specific application. If requirements differ by damper application, indicate requirements for each different application on Drawings.

            - Additional Corrosion Protection for Corrosive Environments:

              - Provide anodized finish for aluminum surfaces in contact with airstream.

        - Rectangular Control Dampers with Galvanized-Steel Flat Blades and Frames:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain rectangular control dampers, with galvanized-steel flat blades and frames, from single manufacturer.

All listed manufacturers may not offer products that comply with all requirements and options indicated; consult manufacturers.

"AMCA Certification" Subparagraph below requires test results to be verified by AMCA staff and the manufacturer to have obtained the proper license from AMCA, in order for the products to bear AMCA's Certified Ratings Seal for air performance, air leakage, or both. Consult manufacturers.

          - [AMCA Certification: Test, rate, and seal, in accordance with AMCA 511 for air performance and air leakage.]

          - Performance:

            - Leakage:

              - AMCA 511, Class II, at 1 in. wg (250 Pa) Differential Static Pressure: Leakage not to exceed 5.4 cfm/sq. ft. (27.4 L/s per sq. m) against 1 in. wg (250 Pa) differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop: [0.1 in. wg (25 Pa)] <Insert pressure drop> at [1500 fpm (7.6 m/s)] <Insert velocity> across a [24-by-24-inch (600-by-600-mm)] <Insert size> damper when tested in accordance with AMCA 500D, figure [5.3] <Insert figure no.>.

            - Pressure Rating: [2.0 in. wg (500 Pa)] [3.0 in. wg (750 Pa)] [4.0 in. wg (1000 Pa)] <Insert pressure>.

            - Temperature: [Minus 20 to plus 185 deg F (Minus 29 to plus 85 deg C)] <Insert temperature range>.

            - Velocity: Up to [2000 fpm (10 m/s)] <Insert velocity>.

          - Construction:

            - Frame:

              - Material: ASTM A653/A653M galvanized steel, minimum [0.06 inch (1.6 mm)] <Insert thickness> thick.

              - Arrangement: Hat-shaped channel with integral extended face flange(s) having mating face of minimum [1 inch (25 mm)] [1-1/2 inches (38 mm)] [2 inches (50 mm)] <Insert size> for attachment to duct flanges, plenum walls, and equipment.

              - Width: Not less than [5 inches (125 mm)] <Insert width>.

            - Blades:

              - Configuration: Parallel or opposed blade configuration as required by application.

              - Material: ASTM A653/A653M galvanized steel, [0.06 inch (1.6 mm)] <Insert thickness> thick.

              - Shape: Single thickness with bends for reinforcing.

              - Length: As required by pressure rating, not to exceed [48 inches (1200 mm)] <Insert length>.

              - Width: Not to exceed [8 inches (200 mm)] <Insert width>.

            - Seals:

              - Blades: Replaceable; extruded silicone, vinyl, [or damper manufacturer-offered equivalent, ]as required by performance requirements. Seals are to be mechanically attached in extruded blade slots.

              - Jambs: Stainless steel, compression type.

            - Axles:

              - Diameter: Minimum [0.375 inch (10 mm)] [0.5 inch (13 mm)] <Insert diameter>.

              - Material: [Plated steel] [or] [stainless steel] [, specific to application indicated].

              - Mechanically attached to blades.

            - Bearings:

              - Material: Molded [nylon] [or] [synthetic], or stainless steel sleeve, as required by operating conditions, mounted in frame.

              - Where blade axles are installed in vertical position, provide thrust bearings.

            - Linkage:

              - Hardware: [Plated] [or] [stainless] steel.

              - Material: [Plated steel] [or] [stainless steel] [, specific to application indicated].

              - Mounting: Concealed in frame.

Retain "Transitions with Sleeve" Subparagraph below for manufacturer to include close transitions as integral part of factory damper assembly for field connection to round and flat oval ducts.

            - Transitions with Sleeve:

              - For round and flat oval duct applications, provide damper assembly with integral transitions to mate to adjoining field connections.

              - Factory mount damper in a sleeve with a close transition to mate to field connection.

                - Sleeve length not less than [12 inches (300 mm)] <Insert length> for dampers without jackshafts and not less than [16 inches (450 mm)] <Insert length> for dampers with jackshafts.

                - Oversize damper and sleeve for duct connection size plus minimum [4 inches (100 mm)] <Insert dimension>.

              - Fabricate sleeve and transitions of galvanized steel.

              - Match end connections (flange or sleeve) to field connections.

Retain "Additional Corrosion Protection for Corrosive Environments" Subparagraph below for applications requiring additional protection against corrosion. If requirements differ by damper application, indicate requirements for each different application on Drawings.

            - Additional Corrosion Protection for Corrosive Environments:

              - Paint surfaces exposed to airstream with an [enamel] [or] [epoxy] <Insert finish> finish. Prepare surfaces to be painted according to paint manufacturer's instructions.

        - Rectangular Control Dampers with Stainless Steel Flat Blades and Frames:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain rectangular control dampers, with stainless steel flat blades and frames, from single manufacturer.

All listed manufacturers may not offer products that comply with all requirements and options indicated; consult manufacturers.

"AMCA Certification" Subparagraph below requires test results to be verified by AMCA staff and the manufacturer to have obtained the proper license from AMCA, in order for the products to bear AMCA's Certified Ratings Seal for air performance, air leakage, or both. Consult manufacturers.

          - [AMCA Certification: Test, rate, and seal, in accordance with AMCA 511 for air performance and air leakage.]

          - Performance:

            - Leakage:

              - AMCA 511, Class II, at 1 in. wg (250 Pa) Differential Static Pressure: Leakage not to exceed 5.4 cfm/sq. ft. (27.4 L/s per sq. m) against 1 in. wg (250 Pa) differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop: [0.1 in. wg (25 Pa)] <Insert pressure drop> at [1500 fpm (7.6 m/s)] <Insert velocity> across a [24-by-24-inch (600-by-600-mm)] <Insert size> damper when tested in accordance with AMCA 500D, figure [5.3] <Insert figure no.>.

            - Pressure Rating: [2.0 in. wg (500 Pa)] [3.0 in. wg (750 Pa)] [4.0 in. wg (1000 Pa)] <Insert pressure>.

            - Temperature: [Minus 20 to plus 185 deg F (Minus 29 to plus 85 deg C)] <Insert temperature range>.

            - Velocity: Up to [2000 fpm (10 m/s)] <Insert velocity>.

          - Construction:

            - Frame:

              - Material: Type 304 stainless steel, minimum [0.06 inch (1.6 mm)] <Insert thickness> thick.

              - Arrangement: Hat-shaped channel with integral extended face flange(s) having mating face of minimum [1 inch (25 mm)] [1-1/2 inches (38 mm)] [2 inches (50 mm)] <Insert size> for attachment to duct flanges, plenum walls, and equipment.

              - Width: Not less than [5 inches (125 mm)] <Insert width>.

            - Blades:

              - Configuration: Parallel or opposed blade configuration as required by application.

              - Material: Type 304 stainless steel, [0.06 inch (1.6 mm)] <Insert thickness> thick.

              - Shape: Single thickness with bends for reinforcing.

              - Length: As required by pressure rating, not to exceed [48 inches (1200 mm)] <Insert length>.

              - Width: Not to exceed [8 inches (200 mm)] <Insert width>.

            - Seals:

              - Blades: Replaceable; extruded silicone, vinyl, [or damper manufacturer-offered equivalent, ]as required by performance requirements. Seals are to be mechanically attached in extruded blade slots.

              - Jambs: Stainless steel, compression type.

            - Axles:

              - Diameter: Minimum [0.375 inch (10 mm)] [0.5 inch (13 mm)] <Insert diameter>.

              - Material: Type 304 or 316 stainless steel.

              - Mechanically attached to blades.

            - Bearings:

              - Material: Molded [nylon] [or] [synthetic], or stainless steel sleeve, as required by operating conditions, mounted in frame.

              - Where blade axles are installed in vertical position, provide thrust bearings.

            - Linkage:

              - Hardware: Stainless steel.

              - Material: Type 304 or 316 stainless steel.

              - Mounting: Concealed in frame.

Retain "Transitions with Sleeve" Subparagraph below for manufacturer to include close transitions as integral part of factory damper assembly for field connection to round and flat oval ducts.

            - Transitions with Sleeve:

              - For round and flat oval duct applications, provide damper assembly with integral transitions to mate to adjoining field connections.

              - Factory mount damper in a sleeve with a close transition to mate to field connection.

                - Sleeve length not less than [12 inches (300 mm)] <Insert length> for dampers without jackshafts and not less than [16 inches (450 mm)] <Insert length> for dampers with jackshafts.

                - Oversize damper and sleeve for duct connection size plus minimum [4 inches (100 mm)] <Insert dimension>.

              - Fabricate sleeve and transitions of Type 304 stainless steel.

              - Match end connections (flange or sleeve) to field connections.

      - RECTANGULAR CONTROL DAMPERS WITH INSULATED BLADES

        - General Requirements:

          - Factory assemble multiple damper sections to provide a single damper assembly of size required by the application.

            - Include multisection damper assemblies with intermediate reinforcing where required between individual sections being joined together. Construct reinforcing of same material (aluminum) as damper frame.

Retain subparagraph below for damper manufacturer to have single-source responsibility for damper assembly with actuators.

          - Factory install actuator(s) as integral part of damper assembly. Coordinate field requirements for actuators, such as type, fail-safe position, power supply, location, and mounting requirements with damper manufacturer.

        - Rectangular Control Dampers with Insulated Aluminum Airfoil Blades:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain rectangular control dampers, with insulated aluminum airfoil blades, from single manufacturer.

All listed manufacturers may not offer products that comply with all requirements and options indicated; consult manufacturers.

"AMCA Certification" Subparagraph below requires test results to be verified by AMCA staff and the manufacturer to have obtained the proper license from AMCA, in order for the products to bear AMCA's Certified Ratings Seal for air performance, air leakage and thermal performance. Consult manufacturers.

          - [AMCA Certification: Test, rate, and seal, in accordance with AMCA 511 for air performance, air leakage, and thermal performance.]

          - Performance:

            - Leakage:

              - AMCA 511, Class 1A, at 1 in. wg (250 Pa) Differential Static Pressure: Leakage not to exceed 3 cfm/sq. ft. (15.2 L/s per sq. m) against 1 in. wg (250 Pa) differential static pressure when tested in accordance with AMCA 500D.

              - AMCA 511, Class 1, at 4 in. wg (1000 Pa) Differential Static Pressure: Leakage not to exceed 8 cfm/sq. ft. (40.6 L/s per sq. m) against 4 in. wg (1000 Pa) differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop: [0.05 in. wg (12.5 Pa)] <Insert pressure drop> at [1500 fpm (7.6 m/s)] <Insert velocity> across a [24-by-24-inch (600-by-600-mm)] <Insert size> damper when tested in accordance with AMCA 500D, figure [5.3] <Insert figure no.>.

            - Pressure Rating: Damper close-off pressure equal to [fan shutoff pressure] <Insert requirement>, not less than [8.0 in. wg (2000 Pa)] <Insert pressure>.

            - Temperature: [Minus 40 to plus 185 deg F (Minus 40 to plus 85 deg C)] <Insert temperature range>.

            - Thermal Performance:

              - R-Value: [2.2] <Insert value> or higher.

              - Thermal Efficiency Ratio (E): [345] <Insert value> or higher when tested in accordance with AMCA 500D.

            - Velocity: Up to [4000 fpm (20 m/s)] <Insert velocity>.

          - Construction:

            - Frame:

              - Material: ASTM B211/B211M, Alloy 6063 T5 extruded-aluminum profiles, minimum [0.08 inch (2 mm)] [0.125 inch (3 mm)] <Insert thickness> thick.

              - Arrangement: Hat-shaped channel with integral extended face flange(s) having mating face of minimum [1 inch (25 mm)] [1-1/2 inches (38 mm)] [2 inches (50 mm)] <Insert size> for attachment to duct flanges, plenum walls, and equipment.

              - Width: Not less than [5 inches (125 mm)] <Insert width>.

            - Blades:

              - Configuration: Parallel or opposed blade configuration as required by application.

              - Material: ASTM B211/B211M, Alloy 6063 T5 extruded-aluminum profiles, [0.07 inch (1.8 mm)] <Insert thickness> thick.

              - Shape: Airfoil.

              - Length: As required by close-off pressure rating, not to exceed [48 inches (1200 mm)] <Insert length>.

              - Width: Not to exceed [6 inches (150 mm)] <Insert width>.

              - Insulation: Hollow airfoil blade internally insulated with expanded polyurethane foam for thermal performance indicated.

              - Thermal Break: Complete thermal break with blades in full closed position.

            - Seals:

              - Blades: Replaceable; extruded EPDM, Santoprene or silicone, [or damper manufacturer-offered equivalent, ]as required by performance requirements. Seals are to be mechanically attached in extruded blade slots.

Retaining optional text in "Jambs" Subparagraph below is less restrictive. Not all listed manufacturers offer compression-type jamb seals. Some use silicone seals.

              - Jambs: Replaceable; polycarbonate, compression type[ or mechanically attached extruded silicone].

            - Axles:

              - Diameter: Minimum [0.44 inch (11 mm)] [0.5 inch (13 mm)] <Insert diameter>.

              - Material: Aluminum or plated steel.

              - Mechanically attached to blades.

            - Bearings:

              - Material: Molded inner and outer bearings of [acetal] [Celcon] [or] [polycarbonate], as required by operating conditions.

              - Mounting: Inner bearing fixed to axle, rotating within an outer bearing inserted in the frame, resulting in no metal-to-metal contact.

              - Where blade axles are installed in vertical position, provide thrust bearings.

            - Linkage:

              - Hardware: [Plated] [or] [stainless] steel.

              - Material: [Aluminum,] [plated steel] [or] [stainless steel].

              - Mounting: Concealed in frame.

Retain "Transitions with Sleeve" Subparagraph below for manufacturer to include close transitions as integral part of factory damper assembly for field connection to round and flat oval ducts.

            - Transitions with Sleeve:

              - For round and flat oval duct applications, provide damper assembly with integral transitions to mate to adjoining field connections.

              - Factory mount damper in a sleeve with a close transition to mate to field connection.

                - Sleeve length not less than [12 inches (300 mm)] <Insert length> for dampers without jackshafts and not less than [16 inches (450 mm)] <Insert length> for dampers with jackshafts.

                - Oversize damper and sleeve for duct connection size plus minimum [4 inches (100 mm)] <Insert dimension>.

              - Fabricate sleeve and transitions of materials (aluminum, galvanized steel, or stainless steel) to match damper frame[ or adjoining duct].

              - Match end connections (flange or sleeve) to field connections.

Retain "Additional Corrosion Protection for Corrosive Environments" Subparagraph below for applications requiring additional protection against corrosion.

            - Additional Corrosion Protection for Corrosive Environments:

Retain one of first two subparagraphs below, or both. Consult damper manufacturer for finish options best suited for a specific application. First subparagraph is sometimes used where dampers are exposed to coastal climates. If requirements differ by damper application, indicate requirements for each different application on Drawings.

              - Provide anodized finish, minimum of 0.0007 inch (0.018 mm) thick, for aluminum surfaces in contact with airstream.

              - Paint surfaces exposed to airstream with an [enamel] [or] [epoxy] <Insert finish> finish. Prepare surfaces to be painted according to paint manufacturer's instructions.

              - Construct axles, damper linkage, and hardware of Type 316L stainless steel.

        - Rectangular Control Dampers with Insulated Aluminum Airfoil Blades and Thermal Break Frames:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain rectangular control dampers, with insulated aluminum airfoil blades and thermal break, from single manufacturer.

All listed manufacturers may not offer products that comply with all requirements and options indicated; consult manufacturers.

"AMCA Certification" Subparagraph below requires test results to be verified by AMCA staff and the manufacturer to have obtained the proper license from AMCA, in order for the products to bear AMCA's Certified Ratings Seal for air performance, air leakage and thermal performance. Consult manufacturers.

          - [AMCA Certification: Test, rate, and seal, in accordance with AMCA 511 for air performance, air leakage, and thermal performance.]

          - Performance:

            - Leakage:

              - AMCA 511, Class 1A, at 1 in. wg (250 Pa) Differential Static Pressure: Leakage not to exceed 3 cfm/sq. ft. (15.2 L/s per sq. m) against 1 in. wg (250 Pa) differential static pressure when tested in accordance with AMCA 500D.

              - AMCA 511, Class 1, at 4 in. wg (1000 Pa) Differential Static Pressure: Leakage not to exceed 8 cfm/sq. ft. (40.6 L/s per sq. m) against 4 in. wg (1000 Pa) differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop: [0.05 in. wg (12.5 Pa)] <Insert pressure drop> at [1500 fpm (7.6 m/s)] <Insert velocity> across a [24-by-24-inch (600-by-600-mm)] <Insert size> damper when tested in accordance with AMCA 500D, figure [5.3] <Insert figure no.>.

            - Pressure Rating: Damper close-off pressure equal to [fan shutoff pressure] <Insert requirement>, not less than [8.0 in. wg (2000 Pa)] <Insert pressure>.

            - Temperature: [Minus 40 to plus 185 deg F (Minus 40 to plus 85 deg C)] <Insert temperature range>.

            - Thermal Performance:

              - R-Value: [2.2] <Insert value> or higher.

              - Thermal Efficiency Ratio (E): [345] <Insert value> or higher when tested in accordance with AMCA 500D.

            - Velocity: Up to [4000 fpm (20 m/s)] <Insert velocity>.

          - Construction:

            - Frame:

              - Material: ASTM B211/B211M, Alloy 6063 T5 extruded-aluminum profiles, minimum [0.08 inch (2 mm)] [0.125 inch (3 mm)] <Insert thickness> thick.

              - Arrangement: Hat-shaped channel with integral extended face flange(s) having mating face of minimum [1 inch (25 mm)] [1-1/2 inches (38 mm)] [2 inches (50 mm)] <Insert size> for attachment to duct flanges, plenum walls, and equipment.

              - Thermal Break: Continuous extruded pocket at two locations, one on each side of closed damper blade, with polyurethane resin fill to achieve frame with no through metal.

              - Width: Not less than [5 inches (125 mm)] <Insert width>.

            - Blades:

              - Configuration: Parallel or opposed blade configuration as required by application.

              - Material: ASTM B211/B211M, Alloy 6063 T5 extruded-aluminum profiles, [0.07 inch (1.8 mm)] <Insert thickness> thick.

              - Shape: Airfoil.

              - Length: As required by close-off pressure rating, not to exceed [48 inches (1200 mm)] <Insert length>.

              - Width: Not to exceed [6 inches (150 mm)] <Insert width>.

              - Insulation: Hollow airfoil blade internally insulated with expanded polyurethane foam for thermal performance indicated.

              - Thermal Break: Complete thermal break with blades in full closed position.

            - Seals:

              - Blades: Replaceable; extruded EPDM, Santoprene or silicone, [or damper manufacturer-offered equivalent, ]as required by performance requirements. Seals are to be mechanically attached in extruded blade slots.

Retaining optional text in "Jambs" Subparagraph below is less restrictive. Not all listed manufacturers offer compression-type jamb seals. Some use silicone seals.

              - Jambs: Replaceable; polycarbonate, compression type[ or mechanically attached extruded silicone].

            - Axles:

              - Diameter: Minimum [0.44 inch (11 mm)] [0.5 inch (13 mm)] <Insert diameter>.

              - Material: Aluminum or plated steel.

              - Mechanically attached to blades.

            - Bearings:

              - Material: Molded inner and outer bearings of [acetal] [Celcon] [or] [polycarbonate], as required by operating conditions.

              - Mounting: Inner bearing fixed to axle, rotating within an outer bearing inserted in the frame, resulting in no metal-to-metal contact.

              - Where blade axles are installed in vertical position, provide thrust bearings.

            - Linkage:

              - Hardware: [Plated] [or] [stainless] steel.

              - Material: [Aluminum,] [plated steel] [or] [stainless steel].

              - Mounting: Concealed in frame.

Retain "Transitions with Sleeve" Subparagraph below for manufacturer to include close transitions as integral part of factory damper assembly for field connection to round and flat oval ducts.

            - Transitions with Sleeve:

              - For round and flat oval duct applications, provide damper assembly with integral transitions to mate to adjoining field connections.

              - Factory mount damper in a sleeve with a close transition to mate to field connection.

                - Sleeve length not less than [12 inches (300 mm)] <Insert length> for dampers without jackshafts and not less than [16 inches (450 mm)] <Insert length> for dampers with jackshafts.

                - Oversize damper and sleeve for duct connection size plus minimum [4 inches (100 mm)] <Insert dimension>.

              - Fabricate sleeve and transitions of materials (aluminum, galvanized steel, or stainless steel) to match damper frame[ or adjoining duct].

              - Match end connections (flange or sleeve) to field connections.

Retain "Additional Corrosion Protection for Corrosive Environments" Subparagraph below for applications requiring additional protection against corrosion.

            - Additional Corrosion Protection for Corrosive Environments:

Retain one of first two subparagraphs below, or both. Consult damper manufacturer for finish options best suited for a specific application. First subparagraph is sometimes used where dampers are exposed to coastal climates. If requirements differ by damper application, indicate requirements for each different application on Drawings.

              - Provide anodized finish, minimum of 0.0007 inch (0.018 mm) thick, for aluminum surfaces in contact with airstream.

              - Paint surfaces exposed to airstream with an [enamel] [or] [epoxy] <Insert finish> finish. Prepare surfaces to be painted according to paint manufacturer's instructions.

              - Construct axles, damper linkage, and hardware of Type 316L stainless steel.

      - RECTANGULAR CONTROL DAMPERS WITH INTEGRAL AIRFLOW MONITORING

        - General Requirements:

          - Factory assemble multiple damper sections to provide a single damper assembly of size required by the application.

            - Include multisection damper assemblies with intermediate reinforcing where required between individual sections being joined together. Construct reinforcing of same material (aluminum) as damper frame.

          - Factory install actuator(s) as integral part of damper assembly. Coordinate field requirements for actuators, such as type, fail-safe position, power supply, location, and mounting requirements with damper manufacturer.

        - Rectangular Control Dampers with Aluminum Airfoil Blades and Integral Airflow Monitoring:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain rectangular control dampers, with aluminum airfoil blades and integral airflow monitoring, from single manufacturer.

All listed manufacturers may not offer products that comply with all requirements and options indicated; consult manufacturers.

"AMCA Certification" Subparagraph below requires test results to be verified by AMCA staff and the manufacturer to have obtained the proper license from AMCA, in order for the products to bear AMCA's Certified Ratings Seal for air performance, air leakage, or both. Consult manufacturers.

          - [AMCA Certification: Test, rate, and seal, in accordance with AMCA 511 for air performance and air leakage.]

          - Performance:

            - Leakage:

              - AMCA 511, Class 1A, at 1 in. wg (250 Pa) Differential Static Pressure: Leakage not to exceed 3 cfm/sq. ft. (15.2 L/s per sq. m) against 1 in. wg (250 Pa) differential static pressure when tested in accordance with AMCA 500D.

              - AMCA 511, Class 1, at 4 in. wg (1000 Pa) Differential Static Pressure: Leakage not to exceed 8 cfm/sq. ft. (40.6 L/s per sq. m) against 4 in. wg (1000 Pa) differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop (Damper and Airflow Measurement): [0.15 in. wg (37.5 Pa)] <Insert pressure> at [1500 fpm (7.6 m/s)] <Insert velocity> across a [24-by-24-inch (600-by-600-mm)] <Insert size> damper when tested in accordance with AMCA 500D, figure 5.3.

            - Pressure Rating: Damper close-off pressure equal to [fan shutoff pressure] <Insert requirement> with a maximum blade deflection of [1/180] <Insert deflection> of blade length.

            - Temperature: [Minus 20 to plus 140 deg F (Minus 29 to plus 60 deg C)] <Insert temperature range>.

            - Velocity (Damper Only): Up to [4000 fpm (20 m/s)] [5000 fpm (25 m/s)] <Insert velocity range>.

          - Construction:

            - Damper Frame:

              - Material: ASTM B211/B211M, Alloy 6063 T5 extruded-aluminum profiles, minimum [0.125 inch (3 mm)] <Insert thickness> thick.

              - Arrangement: Hat-shaped channel with attachment to factory furnished sleeve.

              - Width: Not less than [5 inches (125 mm)] <Insert width>.

            - Damper Blades:

              - Configuration: Parallel or opposed blade configuration as required by application.

              - Material: ASTM B211/B211M, Alloy 6063 T5 extruded-aluminum profiles, [0.07 inch (1.8 mm)] <Insert thickness> thick.

              - Shape: Hollow, airfoil.

              - Length: As required by close-off pressure rating, not to exceed [48 inches (1200 mm)] <Insert length>.

              - Width: Not to exceed [6 inches (150 mm)] <Insert width>.

            - Damper Seals:

              - Blades: Replaceable; extruded Santoprene, silicone, [or damper manufacturer-offered equivalent, ]as required by performance requirements. Damper seals are to be mechanically attached in extruded blade slots.

Retaining optional text in "Jambs" Subparagraph below is less restrictive. Not all listed manufacturers offer stainless steel compression-type jamb seals. Some use silicone seals.

              - Jambs: Replaceable; stainless steel, compression type[ or mechanically attached extruded silicone].

            - Axles:

              - Diameter: Minimum [0.375 inch (10 mm)] [0.5 inch (13 mm)] <Insert diameter>.

              - Material: [Aluminum,] [plated steel] [or] [stainless steel] [, specific to application indicated].

              - Mechanically attached to blades.

            - Bearings:

              - Material: Molded [acetal] [Celcon/polycarbonate] [nylon] [synthetic] [or] stainless steel sleeve, as required by operating conditions, mounted in frame.

              - Where blade axles are installed in vertical position, provide thrust bearings.

            - Linkage:

              - Hardware: [Plated] [or] [stainless] steel.

              - Material: [Aluminum,] [plated steel] [or] [stainless steel] [, specific to application indicated].

              - Mounting: Concealed in frame.

            - Sleeve:

              - General: Factory mount damper assembly and airflow measurement assembly in a common sleeve with a continuous-perimeter flanged face to mate to field connection. Coordinate field-mounting requirements for each application.

              - Length: Not less than [15 inches (375 mm)] [18 inches (450 mm)] <Insert dimension>.

              - Material: [Aluminum] [galvanized steel] [stainless steel] [or] [aluminum, galvanized steel, or stainless steel to match adjoining duct].

              - Thickness:

                - Sleeve Face Sizes through [24 inches (600 mm)] <Insert dimension>: Minimum [14 gauge (2 mm)] [16 gauge (1.6 mm)] <Insert thickness>.

                - Sleeves with Larger Face Size: Minimum [12 gauge (2.7 mm)] [14 gauge (2 mm)] [16 gauge (1.6 mm)] <Insert thickness>.

Retain "Additional Corrosion Protection for Corrosive Environments" Subparagraph below for applications requiring additional protection against corrosion.

            - Additional Corrosion Protection for Corrosive Environments:

Retain one of first two subparagraphs below, or both. Consult damper manufacturer for finish options best suited for a specific application. First subparagraph is sometimes used where dampers are exposed to coastal climates. If requirements differ by damper application, indicate requirements for each different application on Drawings.

              - Provide anodized finish, minimum of 0.0007 inch (0.018 mm) thick, for aluminum surfaces in contact with airstream.

              - Paint surfaces exposed to airstream with an [enamel] [or] [epoxy] <Insert finish> finish. Prepare surfaces to be painted in accordance with paint manufacturer's instructions.

              - Construct axles, damper linkage, and hardware of Type 316L stainless steel.

Retain "Pressure Airflow Measurement" Subparagraph below to include airflow measurement products that use static and total pressure measurements to determine velocity pressure for airflow measurement.

          - Pressure Airflow Measurement:

            - Performance:

              - Accuracy: Within [3] [5] <Insert number> percent of the actual flow rate between the range of minimum to design airflow and velocity. For applications with a large variation in range between the minimum and design airflow, configure the damper sections and flow measurement assemblies as required to comply with the stated accuracy over entire modulating range.

              - Velocity Range: [300 to 2000 fpm (10 m/s)] [300 to 5000 fpm (25 m/s)] [Indicated on Drawings] <Insert velocity range>.

              - Provide temperature and altitude compensation and correction to maintain accuracy over temperature range encountered at site altitude.

              - Suitable for operation with untreated and unfiltered air.

            - Flow Straightener: Provide a straightening device as part of flow measurement assembly [, if required ]to achieve specified accuracy with installed configuration indicated.

            - Flow Sensors: Hollow, ASTM B211/B211M, Alloy 6063 T5 extruded-aluminum profiles with anodized finish.

            - Placement: Locate upstream of damper.

            - Pressure Transducer: Housed in NEMA 250, [Type 4] <Insert type> painted enclosure.

            - Remote Output Signal: Zero- to 10 V dc [or 4 to 20 mA ]scaled output signal proportional to flow for remote monitoring of actual airflow.

            - Tubing: Factory pipe transducer(s) to low- and high-pressure ports on flow sensors using manufacturer's standard tubing that is protected from damage during shipping and installation.

            - Factory Calibration: Factory calibrate each finished assembly before shipment in accordance with application-specific requirements.

Retain "Thermal Airflow Measurement" Subparagraph below to include airflow measurement products that use thermal dispersion to determine airflow.

          - Thermal Airflow Measurement:

            - Certification:

              - Listed and labeled in accordance with UL 873 or UL 60730.

              - BTL certified in accordance with ASHRAE 135.

              - 47 CFR, Ch. 1, Part 15, Subpart B, Class A device.

            - Performance:

              - Airflow Accuracy: Within [3] [5] <Insert number> percent of the actual flow rate between the range of minimum to design airflow. For applications with a large variation in range between the minimum and design airflow, configure the damper sections and flow measurement assemblies as required to comply with the stated accuracy over entire modulating range.

              - Ambient Operating Humidity Range (Sensors and Transmitters): Zero to 99 percent, noncondensing.

              - Temperature Accuracy: Within 0.2 deg F (0.1 deg C) over entire range.

              - Velocity Range: [0 to 5000 fpm (25 m/s)] [Indicated on Drawings] <Insert velocity range>.

              - Provide temperature and altitude compensation and correction to maintain accuracy over temperature range encountered at site altitude.

              - Suitable for operation in untreated and unfiltered air.

            - Flow Straightener: Provide a straightening device as part of flow measurement assembly [, if required ]to achieve specified accuracy with installed configuration indicated.

            - Sensors:

              - Number of sensors determined by manufacturer for application to comply with accuracy requirements indicated.

              - Temperature of each sensor assembly velocity weighted and averaged by transmitter before output if temperature sensor has an accuracy worse than 0.1 deg F (0.06 deg C).

              - Each sensor with two individually wired, hermetically sealed thermistors.

              - Mount thermistors in sensor using a marine-grade, waterproof material.

              - Protect thermistor leads, and do not expose to the environment.

              - Independently determine airflow rate and temperature at each sensor measurement point.

              - Furnish each sensor probe with an integral cable for connection to transmitter.

              - Sensor Probe Material: Anodized, extruded Alloy 6063 aluminum tube.

              - Probe Assembly Mounting Bracket Material: [Plated] [or] [stainless] steel.

              - Connection Enclosure: NEMA 250, [Type 1 or 4 for indoor applications] [Type 4 for outdoor applications] <Insert enclosure type>.

            - Transmitters:

              - Microprocessor based.

              - Integral digital display capable of simultaneously displaying total airflow and average temperature, individual airflow, and temperature readings of each independent sensor assembly.

              - Capable of field configuration and diagnostics using touch interface and digital display.

              - Password-protected programmable settings.

              - Field selectable between IP and SI units for airflow, temperature, and velocity.

              - Power supply, including the following:

                - On-off power switch.

                - Protection from transients and power surges.

                - Circuitry to ensure reset after power disruption, transients, and brownouts.

                - Transformer to convert field power source to operating voltage required.

              - Enclosure: NEMA 250, [Type 1 or 4 for indoor applications] [Type 4 for outdoor applications] <Insert enclosure type>.

              - Remote Signal Interface:

Retain any of first three subparagraphs below.

                - Linear Analog Signals for Airflow and Temperature: Fuse protected and isolated, field selectable, 0 to 10 V dc or 4 to 20 mA.

                - RS-485: BACnet-MS/TP.

                - Ethernet: BACnet Ethernet, BACnet-IP.

              - Factory Calibration: Factory calibrate each airflow station at a minimum of [16] <Insert value> airflow rates and [three] <Insert value> temperatures to standards that are traceable to NIST.

          - Damper Actuator: Electric, modulating actuator with proportional control [and position feedback ]signals; complying with requirements in "Electric and Electronic Control-Damper Actuators" Article.

      - RECTANGULAR CONTROL DAMPERS WITH INTEGRAL AIRFLOW CONTROL

        - General Requirements:

          - Factory assemble multiple damper sections to provide a single damper assembly of size required by the application.

            - Include multisection damper assemblies with intermediate reinforcing where required between individual sections being joined together. Construct reinforcing of same material (aluminum) as damper frame.

          - Factory install actuator(s) as integral part of damper assembly. Coordinate field requirements for actuators, such as type, fail-safe position, power supply, location, and mounting requirements with damper manufacturer.

        - Rectangular Control Dampers with Aluminum Airfoil Blades and Integral Airflow Control:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain rectangular control dampers, with aluminum airfoil blades and integral airflow control, from single manufacturer.

All listed manufacturers may not offer products that comply with all requirements and options indicated; consult manufacturers.

"AMCA Certification" Subparagraph below requires test results to be verified by AMCA staff and the manufacturer to have obtained the proper license from AMCA, in order for the products to bear AMCA's Certified Ratings Seal for air performance, air leakage, or both. Consult manufacturers.

          - [AMCA Certification: Test, rate, and seal, in accordance with AMCA 511 for air performance and air leakage.]

          - Performance:

            - Leakage:

              - AMCA 511, Class 1A, at 1 in. wg (250 Pa) Differential Static Pressure: Leakage not to exceed 3 cfm/sq. ft. (15.2 L/s per sq. m) against 1 in. wg (250 Pa) differential static pressure when tested in accordance with AMCA 500D.

              - AMCA 511, Class 1, at 4 in. wg (1000 Pa) Differential Static Pressure: Leakage not to exceed 8 cfm/sq. ft. (40.6 L/s per sq. m) against 4 in. wg (1000 Pa) differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop (Damper and Flow Measurement): [0.15 in. wg (37.5 Pa)] <Insert pressure> at [1500 fpm (7.6 m/s)] <Insert velocity> across a [24-by-24-inch (600-by-600-mm)] <Insert size> damper when tested in accordance with AMCA 500D, figure 5.3.

            - Pressure Rating: Damper close-off pressure equal to [fan shutoff pressure] <Insert requirement> with a maximum blade deflection of [1/180] <Insert deflection> of blade length.

            - Temperature (Damper and Flow Measurement): [Minus 20 to plus 140 deg F (Minus 29 to plus 60 deg C)] <Insert temperature range>.

            - Velocity (Damper Only): Up to [4000 fpm (20 m/s)] [5000 fpm (25 m/s)] <Insert velocity range>.

          - Construction:

            - Damper Frame:

              - Material: ASTM B211/B211M, Alloy 6063 T5 extruded-aluminum profiles, minimum [0.125 inch (3 mm)] <Insert thickness> thick.

              - Arrangement: Hat-shaped channel with attachment to factory-furnished sleeve.

              - Width: Not less than [5 inches (125 mm)] <Insert width>.

            - Damper Blades:

              - Configuration: Parallel or opposed blade configuration as required by application.

              - Material: ASTM B211/B211M, Alloy 6063 T5 extruded-aluminum profiles, [0.07 inch (1.8 mm)] <Insert thickness> thick.

              - Shape: Hollow, airfoil.

              - Length: As required by close-off pressure rating, not to exceed [48 inches (1200 mm)] <Insert length>.

              - Width: Not to exceed [6 inches (150 mm)] <Insert width>.

            - Damper Seals:

              - Blades: Replaceable; extruded Santoprene, silicone, [or damper manufacturer-offered equivalent, ]as required by performance requirements. Mechanically attached in extruded blade slots.

Retaining optional text in "Jambs" Subparagraph below is less restrictive. Not all listed manufacturers offer stainless steel compression-type jamb seals. Some use silicone seals.

              - Jambs: Replaceable; stainless steel, compression type[ or mechanically attached extruded silicone].

            - Axles:

              - Diameter: Minimum [0.375 inch (10 mm)] [0.5 inch (13 mm)] <Insert diameter>.

              - Material: [Plated steel] [or] [stainless steel] [, specific to application indicated].

              - Mechanically attached to blades.

            - Bearings:

              - Material: Molded [acetal] [Celcon/polycarbonate] [nylon] [synthetic] [or] stainless steel sleeve, as required by operating conditions, mounted in frame.

              - Where blade axles are installed in vertical position, provide thrust bearings.

            - Linkage:

              - Hardware: [Plated] [or] [stainless] steel.

              - Material: [Aluminum,] [plated steel] [or] [stainless steel] [, specific to application indicated].

              - Mounting: Concealed in frame.

            - Sleeve:

              - General: Factory mount damper assembly and airflow measurement assembly in a common sleeve with a continuous-perimeter flanged face to mate to field connection. Coordinate field-mounting requirements for each application.

              - Length: Not less than [15 inches (375 mm)] [18 inches (450 mm)] <Insert dimension>.

              - Material: [Galvanized steel] [galvanized steel or stainless steel to match adjoining duct] [or] [stainless steel].

              - Thickness:

                - Sleeve Face Sizes through [24 inches (600 mm)] <Insert dimension>: Minimum [14 gauge (2 mm)] [16 gauge (1.6 mm)] <Insert thickness>.

                - Sleeves with Larger Face Size: Minimum [12 gauge (2.7 mm)] [14 gauge (2 mm)] [16 gauge (1.6 mm)] <Insert thickness>.

Retain "Additional Corrosion Protection for Corrosive Environments" Subparagraph below for applications requiring additional protection against corrosion.

            - Additional Corrosion Protection for Corrosive Environments:

Retain one of first two subparagraphs below, or both. Consult damper manufacturer for finish options best suited for a specific application. First subparagraph is sometimes used where dampers are exposed to coastal climates. If requirements differ by damper application, indicate requirements for each different application on Drawings.

              - Provide anodized finish, minimum of 0.0007 inch (0.018 mm) thick, for aluminum surfaces in contact with airstream.

              - Paint surfaces exposed to airstream with an [enamel] [or] [epoxy] <Insert finish> finish. Prepare surfaces to be painted according to paint manufacturer's instructions.

              - Construct axles, damper linkage, and hardware of Type 316L stainless steel.

Retain "Pressure Airflow Measurement and Control" Subparagraph below to include airflow measurement products that use static and total pressure measurements to determine velocity pressure for airflow measurement.

          - Pressure Airflow Measurement and Control:

            - Performance:

              - Accuracy: Within [3] [5] <Insert number> percent of the actual flow rate between the range of minimum to design airflow and velocity. For applications with a large variation in range between the minimum and design airflow, configure the damper sections and flow measurement assemblies as required to comply with the stated accuracy over entire modulating range.

              - Velocity Range: [150 to 2000 fpm (10 m/s)] [Indicated on Drawings] <Insert velocity range>.

              - Provide temperature and altitude compensation and correction to maintain accuracy over temperature range encountered at site altitude.

              - Suitable for operation with untreated and unfiltered air.

            - Flow Straightener: Provide a straightening device as part of flow measurement assembly [, if required ]to achieve specified accuracy with installed configuration indicated.

            - Flow Sensors: Hollow, ASTM B211/B211M, Alloy 6063 T5 extruded-aluminum profiles with anodized finish.

            - Placement: Locate upstream (inlet side) of damper.

            - Programmable Controller: Factory calibrated and programmed in nonvolatile memory for application-specific airflow set point(s) and range to control desired airflow. Include controller with the following:

              - On-off power switch.

              - Protection from transients and power surges.

              - Circuitry to ensure reset after power disruption, transients, and brownouts.

            - Remote Control and Monitoring Interface:

              - Airflow Measurement: 0 to 10 V dc or 4 to 20 mA scaled output signal proportional to airflow.

              - Airflow Set Point: 0 to 10 V dc or 4 to 20 mA scaled input signal proportional to airflow.

              - Carbon Dioxide Level: 0 to 10 V dc or 4 to 20 mA scaled input signal proportional to carbon dioxide.

              - Damper Actuator Position Feedback: 0 to 10 V dc or 4 to 20 mA scaled output signal.

              - Damper Position Override Command: 0 to 10 V dc or 4 to 20 mA scaled input signal.

              - Set-Point Alarm: Binary signal.

              - <Insert remote interface requirement>.

            - Remote Control and Monitoring Serial Interface: RS-485, BACnet-MS/TP.

            - Terminal Strip: Screw terminals for interface to field wiring.

            - Transformer: Rated for not less than [100] <Insert value> V A. Provide transformer with primary and secondary protection and primary disconnecting means. Coordinate requirements with field power connection.

            - Tubing: Factory pipe transducer(s) to low- and high-pressure ports on flow sensors using manufacturer's standard tubing that is protected from damage during shipping and installation.

            - Control Enclosure: Factory mount controller, transducers, control transformer, terminal strip, and other control components and electronics within NEMA 250, [Type 1 or 4 for indoor applications] [Type 4 for outdoor applications] <Insert enclosure type>.

            - Factory Calibration: Factory calibrate each finished assembly before shipment to the application-specific requirements.

Retain "Thermal Airflow Measurement and Control" Subparagraph below to include airflow measurement products that use thermal dispersion to determine airflow.

          - Thermal Airflow Measurement and Control:

            - Certification:

              - Listed and labeled in accordance with UL 873 or UL 60730.

              - BTL certified in accordance with ASHRAE 135.

              - 47 CFR, Ch. 1, Part 15, Subpart B, Class A device.

            - Performance:

              - Airflow Accuracy: Within [3] [5] <Insert number> percent of the actual flow rate between the range of minimum to design airflow. For applications with a large variation in range between the minimum and design airflow, configure the damper sections and flow measurement assemblies as required to comply with the stated accuracy over entire modulating range.

              - Ambient Operating Humidity Range (Sensors and Transmitters): Zero to 99 percent, noncondensing.

              - Temperature Accuracy: Within 0.2 deg F (0.1 deg C) over entire range.

              - Velocity Range: [0 to 3000 fpm (15 m/s)] [0 to 5000 fpm (25 m/s)] [Indicated on Drawings] <Insert velocity range>.

              - Provide temperature and altitude compensation and correction to maintain accuracy over temperature range encountered at site altitude.

              - Suitable for operation in untreated and unfiltered air.

            - Flow Straightener: Provide a straightening device as part of flow measurement assembly [, if required ]to achieve specified accuracy with installed configuration indicated.

            - Sensors:

              - Number of sensors determined by manufacturer for application to comply with accuracy requirements indicated.

              - Temperature of each sensor assembly velocity weighted and averaged by transmitter before output if temperature sensor has an accuracy worse than 0.1 deg F (0.06 deg C).

              - Each sensor with two individually wired, hermetically sealed thermistors.

              - Mount thermistors in sensor using a marine-grade, waterproof material.

              - Protect thermistor leads, and do not expose to the environment.

              - Independently determine airflow rate and temperature at each sensor measurement point.

              - Furnish each sensor probe with an integral cable for connection to transmitter.

              - Sensor Probe Material: Anodized, extruded Alloy 6063 aluminum tube.

              - Probe Assembly-Mounting Brackets Material: [Plated] [or] [stainless] steel.

              - Connection Enclosure: NEMA 250, [Type 1 or 4 for indoor applications] [Type 4 for outdoor applications] <Insert enclosure type>.

            - Transmitters:

              - Microprocessor based.

              - Integral digital display capable of simultaneously displaying total airflow and average temperature, individual airflow, and temperature readings of each independent sensor assembly.

              - Capable of field configuration and diagnostics using touch interface and digital display.

              - Password-protected programmable settings.

              - Field selectable between IP and SI units for airflow, temperature, and velocity.

              - Power supply, including the following:

                - On-off power switch.

                - Protection from transients and power surges.

                - Circuitry to ensure reset after power disruption, transients, and brownouts.

              - Enclosure: NEMA 250, [Type 1 or 4 for indoor applications] [Type 4 for outdoor applications] <Insert enclosure type>.

            - Programmable Controller: Factory calibrated and programmed in nonvolatile memory for application-specific airflow set point(s) and range to control desired airflow. Include controller with the following:

              - On-off power switch.

              - Protection from transients and power surges.

              - Circuitry to ensure reset after power disruption, transients, and brownouts.

              - Digital display.

              - Capable of field configuration and diagnostics using touch interface and digital display.

            - Remote Control and Monitoring Interface:

              - Airflow Measurement: 0 to 10 V dc or 4 to 20 mA scaled output signal proportional to airflow.

              - Airflow Set Point: 0 to 10 V dc or 4 to 20 mA scaled input signal proportional to airflow.

              - Carbon Dioxide Level: 0 to 10 V dc or 4 to 20 mA scaled input signal proportional to carbon dioxide.

              - Damper Actuator Position Feedback: 0 to 10 V dc or 4 to 20 mA scaled output signal.

              - Damper Position Override Command: 0 to 10 V dc or 4 to 20 mA scaled input signal.

              - Set-Point Alarm: Binary signal.

              - Temperature Measurement: 0 to 10 V dc or 4 to 20 mA scaled output signal proportional to air temperature.

              - <Insert remote interface requirement>.

            - Remote Control and Monitoring Serial Interface: RS-485, BACnet-MS/TP; Ethernet, BACnet Ethernet, or BACnet-IP.

            - Terminal Strip: Screw terminals for interface to field wiring.

            - Transformer: Rated for not less than [100] <Insert value> V A. Provide transformer with primary and secondary protection and primary disconnecting means. Coordinate requirements with field power connection.

            - Control Enclosure: Factory mount controller, control transformer, and terminal strip within NEMA 250, [Type 1 or 4 for indoor applications] [Type 4 for outdoor applications] <Insert enclosure type>.

            - Factory Calibration: Factory calibrate each airflow station at a minimum of [16] <Insert value> airflow rates and [three] <Insert value> temperatures to standards that are traceable to NIST.

          - Damper Actuator: Electric, modulating actuator with proportional control [and position feedback ]signals; complying with requirements in "Electric and Electronic Control-Damper Actuators" Article.

      - RECTANGULAR INDUSTRIAL-DUTY CONTROL DAMPERS

        - General Requirements:

          - Factory assemble multiple damper sections to provide a single damper assembly of size required by the application.

            - Include intermediate reinforcing required between individual sections being joined together of same material (galvanized steel, stainless steel) as damper frame.

Retain subparagraph below for damper manufacturer to have single-source responsibility for damper assembly with actuators.

          - Factory install actuator(s) as integral part of damper assembly. Coordinate field requirements for actuators, such as type, fail-safe position, power supply, location, and mounting requirements with damper manufacturer.

        - Rectangular Industrial-Duty Control Dampers with Galvanized-Steel Airfoil Blades and Frames:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain rectangular industrial-duty control dampers, with galvanized-steel airfoil blades and frames, from single manufacturer.

All listed manufacturers may not offer products that comply with all requirements and options indicated. Consult manufacturers for additional information.

          - Performance:

            - Leakage: Not to exceed [3 cfm/sq. ft. (15.2 L/s per sq. m)] [4 cfm/sq. ft. (20.3 L/s per sq. m)] <Insert value> against [1 in. wg (250 Pa)] <Insert value> differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop: [0.1 in. wg (25 Pa)] <Insert pressure drop> at [1500 fpm (7.6 m/s)] <Insert velocity> across a [24-by-24-inch (600-by-600-mm)] <Insert size> damper when tested in accordance with AMCA 500D, figure [5.3] <Insert figure no.>.

            - Pressure Rating: Damper close-off pressure equal to [fan shutoff pressure] <Insert requirement> with a maximum blade deflection of [1/240] <Insert deflection> of blade length, but not less than [10 in. wg (2500 Pa)] <Insert pressure>.

            - Temperature: [Minus 40 to plus 250 deg F (Minus 40 to plus 121 deg C)] [Minus 40 to plus 400 deg F (Minus 40 to plus 204 deg C)] <Insert temperature range>.

            - Velocity: Up to [4000 fpm (20 m/s)] [5000 fpm (25 m/s)] [6000 fpm (30 m/s)] <Insert velocity>.

          - Construction:

            - Frame:

              - Material: Galvanized steel.

              - Shape: C-shaped channel.

              - Mating Face Size: Minimum [2 inches (50 mm)] <Insert size>.

              - Thickness: Minimum [14 gauge (2 mm)] <Insert thickness> thick.

In "Width" Subparagraph below, second option provides additional protection to blades.

              - Width: Not less than [8 inches (250 mm)] [open blade width plus 2 inches (50 mm)] <Insert dimension>.

            - Blades:

              - Configuration: Parallel or opposed blade as required by application.

              - Material: Galvanized steel.

              - Thickness: Minimum [14 gauge (2 mm)] [16 gauge (1.6 mm)] <Insert thickness> thick.

              - Shape: Hollow, airfoil.

              - Length: Not to exceed [36 inches (900 mm)] [48 inches (1200 mm)] [60 inches (1500 mm)] <Insert dimension>.

              - Width: Not to exceed [6 inches (150 mm)] [8 inches (200 mm)] <Insert dimension>.

            - Seals:

              - Blades: Replaceable, mechanically attached [silicone] [or] [stainless steel] <Insert material>.

              - Jambs: Stainless steel, [double ]compression type.

            - Axles:

              - Attachment: Mechanically attached to blades.

              - Diameter: Minimum 0.75 inch (19 mm).

              - Material: [Plated] [or] [stainless].

              - Length: [Continuous across entire length of blade] <Insert length>.

            - Bearings:

              - Material: Stainless steel.

Second option in "Mounting" Subparagraph below is the more common standard product offering.

              - Mounting: [Bolted to frame] [Pressed into frame] [Bolted or pressed in frame] [Outboard bearings bolted to frame with shaft seals] [Mounting requirements as indicated by application] <Insert mounting requirements>.

              - Where blade axles are installed in vertical position, provide thrust bearings.

            - Linkage:

First option in "Arrangement" Subparagraph below is the more common standard product offering.

              - Arrangement: [Blade-to-blade linkage concealed in frame] [Blade-to-blade face linkage exposed to airstream] <Insert requirement>.

              - Material: [Plated] [or] [stainless].

              - Hardware: Stainless steel.

Retain "Additional Corrosion Protection for Corrosive Environments" Subparagraph below for applications requiring additional protection against corrosion. Consult damper manufacturer for finish options best suited for a specific application. If requirements differ by damper application, indicate requirements for each different application on Drawings.

            - Additional Corrosion Protection for Corrosive Environments:

              - [Where indicated, paint] [Paint] surfaces exposed to airstream with an [enamel] [or] [epoxy] <Insert finish> finish. Prepare surfaces to be painted according to paint manufacturer's instructions.

        - Rectangular Industrial-Duty Control Dampers with Stainless Steel Airfoil Blades and Frames:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain rectangular industrial-duty control dampers, with stainless steel airfoil blades and frames, from single manufacturer.

All listed manufacturers may not offer products that comply with all requirements and options indicated. Consult manufacturers for additional information.

          - Performance:

            - Leakage: Not to exceed [3 cfm/sq. ft. (15.2 L/s per sq. m)] [4 cfm/sq. ft. (20.3 L/s per sq. m)] <Insert value> against [1 in. wg (250 Pa)] <Insert value> differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop: [0.1 in. wg (25 Pa)] <Insert pressure drop> at [1500 fpm (7.6 m/s)] <Insert velocity> across a [24-by-24-inch (600-by-600-mm)] <Insert size> damper when tested in accordance with AMCA 500D, figure [5.3] <Insert figure no.>.

            - Pressure Rating: Damper close-off pressure equal to [fan shutoff pressure] <Insert requirement> with a maximum blade deflection of [1/240] <Insert deflection> of blade length, but not less than [10 in. wg (2500 Pa)] <Insert pressure>.

            - Temperature: [Minus 40 to plus 250 deg F (Minus 40 to plus 121 deg C)] [Minus 40 to plus 400 deg F (Minus 40 to plus 204 deg C)] <Insert temperature range>.

            - Velocity: Up to [4000 fpm (20 m/s)] [5000 fpm (25 m/s)] [6000 fpm (30 m/s)] <Insert velocity>.

          - Construction:

            - Frame:

              - Material: Stainless steel, [Type 304] [or] [Type 316] [Type 304 or 316 as indicated by application] <Insert type>.

              - Shape: C-shaped channel.

              - Mating Face Size: Minimum [2 inches (50 mm)] <Insert size>.

              - Thickness: Minimum [14 gauge (2 mm)] <Insert thickness> thick.

In "Width" Subparagraph below, second option provides additional protection to blades.

              - Width: Not less than [8 inches (250 mm)] [open blade width plus 2 inches (50 mm)] <Insert dimension>.

            - Blades:

              - Configuration: Parallel or opposed blade as required by application.

              - Material: Stainless steel, [Type 304] [or] [Type 316] [Type 304 or 316 as indicated by application] <Insert type>.

              - Thickness: Minimum [14 gauge (2 mm)] [16 gauge (1.6 mm)] <Insert thickness> thick.

              - Shape: Hollow, airfoil.

              - Length: Not to exceed [36 inches (900 mm)] [48 inches (1200 mm)] [60 inches (1500 mm)] <Insert dimension>.

              - Width: Not to exceed [6 inches (150 mm)] [8 inches (200 mm)] <Insert dimension>.

            - Seals:

              - Blades: Replaceable, mechanically attached [silicone] [or] [stainless steel] <Insert material>.

              - Jambs: Type 316 stainless steel, [double ]compression type.

            - Axles:

              - Attachment: Mechanically attached to blades.

              - Diameter: Minimum 0.75 inch (19 mm).

              - Material: Stainless steel, [Type 304] [or] [Type 316] [Type 304 or 316 as indicated by application] <Insert type>.

              - Length: [Continuous across entire length of blade] <Insert length>.

            - Bearings:

              - Material: Stainless steel.

Second option in "Mounting" Subparagraph below is the more common standard product offering.

              - Mounting: [Bolted to frame] [Pressed into frame] [Bolted or pressed in frame] [Outboard bearings bolted to frame with shaft seals] [Mounting requirements as indicated by application] <Insert mounting requirements>.

              - Where blade axles are installed in vertical position, provide thrust bearings.

            - Linkage:

First option in "Arrangement" Subparagraph below is the more common standard product offering.

              - Arrangement: [Blade-to-blade linkage concealed in frame] [Blade-to-blade face linkage exposed to airstream] <Insert requirement>.

              - Material: Stainless steel, [Type 304] [or] [Type 316] [Type 304 or 316 as indicated by application] <Insert type>.

              - Hardware: Stainless steel, [Type 304] [or] [Type 316] [Type 304 or 316 as indicated by application] <Insert type>.

      - ROUND CONTROL DAMPERS

        - General Requirements:

Retain subparagraph below for damper manufacturer to have single-source responsibility for damper assembly with actuators.

          - Factory install actuator as integral part of damper assembly. Coordinate field requirements for actuators, such as type, fail-safe position, power supply, location, and mounting requirements with damper manufacturer.

        - Round, Galvanized-Steel Control Dampers with Sleeve End Connections:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain round, galvanized-steel control dampers with sleeve end connections from single manufacturer.

Listed manufacturers make similar products but may not comply with all requirements and options. Consult manufacturers for additional information.

          - Performance:

            - Leakage: Not to exceed [0.15 cfm/in. (0.0028 L/s per mm)] <Insert leakage> of perimeter blade at [4 in. wg (1000 Pa)] <Insert pressure> differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop: 0.05 in. wg (12.5 Pa) at 1500 fpm (7.6 m/s) across a 12-inch (300-mm) damper when tested in accordance with AMCA 500D, figure 5.3.

            - Pressure Rating: [4 in. wg (1000 Pa)] [6 in. wg (1500 Pa)] [8 in. wg (2000 Pa) for sizes through 12 inches (300 mm), 6 in. wg (1500 Pa) for larger sizes] <Insert pressure>.

            - Temperature: Up to [180 deg F (82 deg C)] [200 deg F (93 deg C)] <Insert temperature>.

            - Velocity: Up to [3000 fpm (15 m/s)] [4000 fpm (20 m/s)] <Insert velocity>.

          - Size Range: [4 to 24 inches (100 to 600 mm)] <Insert size range>.

          - Construction:

            - Frame:

              - End Connection: Sleeve-type connection for mating to adjacent ductwork.

              - Length: Minimum 6 inches (150 mm).

              - Material: Galvanized steel, minimum 20 gauge (1.0 mm) thick.

              - Stiffeners: Outward-turned beads positioned approximately 1-1/2 inches (38 mm) inboard of each end.

              - Standoff: Provide 2-inch- (50-mm-) high, sheet metal standoff for mounting actuator to axle while accommodating field-installed duct insulation.

            - Blade: Double-thickness circular flat blades sandwiched together and constructed of galvanized steel.

            - Blade Seal: EPDM, neoprene or silicone seal fully encompassing blade edge.

            - Axle: 0.5-inch- (13-mm-) diameter plated steel, mechanically attached to blade.

            - Bearings: Bronze or stainless steel sleeve pressed into frame.

        - Round, Stainless Steel Control Dampers with Sleeve End Connections:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain round, stainless steel control dampers with sleeve end connections from single manufacturer.

Listed manufacturers make similar products but may not comply with all requirements and options; consult manufacturers.

          - Performance:

            - Leakage: Not to exceed [0.15 cfm/in. (0.0028 L/s per mm)] <Insert leakage> of perimeter blade at [4 in. wg (1000 Pa)] <Insert pressure> differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop: 0.05 in. wg (12.5 Pa) at 1500 fpm (7.6 m/s) across a 12-inch (300-mm) damper when tested in accordance with AMCA 500D, figure 5.3.

            - Pressure Rating: [4 in. wg (1000 Pa)] [6 in. wg (1500 Pa)] [8 in. wg (2000 Pa) for sizes through 12 inches (300 mm), 6 in. wg (1500 Pa) for larger sizes] <Insert pressure>.

            - Temperature: Up to [180 deg F (82 deg C)] [200 deg F (93 deg C)] <Insert temperature>.

            - Velocity: Up to [3000 fpm (15 m/s)] [4000 fpm (20 m/s)] <Insert velocity>.

          - Size Range: [4 to 24 inches (100 to 600 mm)] <Insert size range>.

          - Construction:

            - Frame:

              - End Connection: Sleeve-type connection for mating to adjacent ductwork.

              - Length: Minimum 6 inches (150 mm).

              - Material: Type 304 stainless steel, minimum 20 gauge (1.0 mm) thick.

              - Stiffeners: Outward-turned beads positioned approximately 1-1/2 inches (38 mm) inboard of each end.

              - Standoff: Provide 2-inch- (50-mm-) high, sheet metal standoff for mounting actuator to axle while accommodating field-installed duct insulation.

            - Blade: Double-thickness circular flat blades sandwiched together and constructed of Type 304 stainless steel.

            - Blade Seal: EPDM, neoprene or silicone seal fully encompassing blade edge.

            - Axle: 0.5-inch- (13-mm-) diameter, Type 304 or 316 stainless steel, mechanically attached to blade.

            - Bearings: Bronze or stainless steel sleeve pressed into frame.

        - Round, Galvanized-Steel Control Dampers with Flanged End Connections:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain round, galvanized-steel control dampers with flanged end connections from single manufacturer.

Listed manufacturers make similar products but may not comply with all requirements and options; consult manufacturers.

          - Performance:

            - Leakage: Not to exceed [0.15 cfm/in. (0.0028 L/s per mm)] <Insert leakage> of perimeter blade at [4 in. wg (1000 Pa)] <Insert pressure> differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop: 0.05 in. wg (12.5 Pa) at 1500 fpm (7.6 m/s) across a 12-inch (300-mm) damper when tested in accordance with AMCA 500D, figure 5.3.

            - Pressure Rating: [4 in. wg (1000 Pa)] [6 in. wg (1500 Pa)] [8 in. wg (2000 Pa) for sizes through 12 inches (300 mm), 6 in. wg (1500 Pa) for larger sizes] <Insert pressure>.

            - Temperature: Up to [250 deg F (121 deg C)] <Insert temperature>.

            - Velocity: Up to [2500 fpm (13 m/s)] [3000 fpm (15 m/s)] [4000 fpm (20 m/s)] <Insert velocity>.

          - Size Range: [4 to 48 inches (100 to 1200 mm)] <Insert size range>.

          - Construction:

            - Frame:

              - Material: Galvanized steel, thickness as follows:

                - Sizes through 18 Inches (450 mm) in Diameter: Minimum 16 gauge (1.6 mm) thick.

                - Larger Sizes: Minimum 12 gauge (2.8 mm) thick.

              - Flanges:

                - Outward-turned flanges with bolt holes on each end of frame for mating to adjacent ductwork.

                - Face: Not less than 1-1/2 inches (38 mm).

                - Thickness: Minimum 12 gauge (2.8 mm) thick.

              - Length (Flange Face to Face): Not less than 8 inches (200 mm).

              - Standoff: Provide 3-inch- (75-mm-) high, standoff for mounting actuator to axle while accommodating field-installed duct insulation.

            - Blade: Reinforced double-thickness circular flat blades sandwiched together or reinforced single-thickness circular flat blades; constructed of galvanized steel.

              - Double-Thickness Blades (Each Side):

                - Sizes through 18 Inches (450 mm): Minimum 18 gauge (1.3 mm) thick.

                - Larger Sizes: Minimum 16 gauge (1.6 mm) thick.

              - Single-Thickness Blades:

                - Sizes through 36 Inches (900 mm): Minimum 14 gauge (2 mm) thick.

                - Larger Sizes: Minimum 12 gauge (2.8 mm) thick.

            - Blade Stop: Located in airstream; galvanized steel, full-circumference bar[ or pin].

            - Blade Seal: EPDM, neoprene or silicone, mechanically attached to blade and fully encompassing blade edge. For double-thickness blade designs, sandwich seal between blades.

            - Axle: Continuous, plated steel, mechanically attached to blade and angle reinforced as required.

              - Blade Diameter through 24 Inches (600 mm): Minimum 1/2-inch (13-mm) axle diameter.

              - Larger Sizes: Minimum 3/4-inch (19-mm) axle diameter.

            - Bearings: [Bronze or ]stainless steel sleeve pressed into frame.

        - Round, Stainless Steel Control Dampers with Flanged End Connections:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain round, stainless steel control dampers with flanged end connections from single manufacturer.

Listed manufacturers make similar products but may not comply with all requirements and options; consult manufacturers.

          - Performance:

            - Leakage: Not to exceed [0.15 cfm/in. (0.0028 L/s per mm)] <Insert leakage> of perimeter blade at [4 in. wg (1000 Pa)] <Insert pressure> differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop: 0.05 in. wg (12.5 Pa) at 1500 fpm (7.6 m/s) across a 12-inch (300-mm) damper when tested in accordance with AMCA 500D, figure 5.3.

            - Pressure Rating: [4 in. wg (1000 Pa)] [6 in. wg (1500 Pa)] [8 in. wg (2000 Pa) for sizes through 12 inches (300 mm), 6 in. wg (1500 Pa) for larger sizes] <Insert pressure>.

            - Temperature: Up to [250 deg F (121 deg C)] <Insert temperature>.

            - Velocity: Up to [2500 fpm (13 m/s)] [3000 fpm (15 m/s)] [4000 fpm (20 m/s)] <Insert velocity>.

          - Size Range: [4 to 48 inches (100 to 1200 mm)] <Insert size range>.

          - Construction:

            - Frame:

              - Material: Type 304 stainless steel, thickness as follows:

                - Sizes through 18 Inches (450 mm) in Diameter: Minimum 16 gauge (1.6 mm) thick.

                - Larger Sizes: Minimum 12 gauge (2.8 mm) thick.

              - Flanges:

                - Outward-turned flanges with bolt holes on each end of frame for mating to adjacent ductwork.

                - Face: Not less than 1-1/2 inches (38 mm).

                - Thickness: Minimum 12 gauge (2.8 mm) thick.

              - Length (Flange Face to Face): Not less than 8 inches (200 mm).

              - Standoff: Provide 3-inch- (75-mm-) high, standoff for mounting actuator to axle while accommodating field-installed duct insulation.

            - Blade: Reinforced double-thickness circular flat blades sandwiched together or reinforced single-thickness circular flat blades; constructed of Type 304 stainless steel.

              - Double-Thickness Blades (Each Side):

                - Sizes through 18 Inches (450 mm): Minimum 18 gauge (1.3 mm) thick.

                - Larger Sizes: Minimum 16 gauge (1.6 mm) thick.

              - Single-Thickness Blades:

                - Sizes through 36 Inches (900 mm): Minimum 14 gauge (2 mm) thick.

                - Larger Sizes: Minimum 12 gauge (2.8 mm) thick.

            - Blade Stop: Located in airstream; Type 304 stainless steel, full-circumference bar[ or pin].

            - Blade Seal: EPDM, neoprene or silicone, mechanically attached to blade and fully encompassing blade edge. For double-thickness blade designs, sandwich seal between blades.

            - Axle: Continuous, Type 304 stainless steel, mechanically attached to blade and angle reinforced as required.

              - Blade diameter through 24 Inches (600 mm): Minimum 1/2-inch (13-mm) axle diameter.

              - Larger Sizes: Minimum 3/4-inch (19-mm) axle diameter.

            - Bearings: Stainless steel sleeve pressed into frame.

      - ROUND INDUSTRIAL-DUTY CONTROL DAMPERS

        - General Requirements:

Retain subparagraph below for damper manufacturer to have single-source responsibility for damper assembly with actuators.

          - Factory install actuator as integral part of damper assembly. Coordinate field requirements for actuators, such as type, fail-safe position, power supply, location, and mounting requirements with damper manufacturer.

        - Round, Carbon Steel, Industrial-Duty Control Dampers:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain round, carbon steel, industrial-duty control dampers from single manufacturer.

Listed manufacturers make similar products but may not comply with all requirements and options; consult manufacturers.

          - Performance:

            - Leakage: Not to exceed [0.15 cfm/in. (0.0028 L/s per mm)] <Insert leakage> of perimeter blade at [4 in. wg (1000 Pa)] <Insert pressure> differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop: 0.05 in. wg (12.5 Pa) at 1500 fpm (7.6 m/s) across a 12-inch (300-mm) damper when tested in accordance with AMCA 500D, figure 5.3.

            - Pressure Rating: Minimum [13 in. wg (3250 Pa)] <Insert pressure>.

            - Temperature: Up to [250 deg F (121 deg C)] [400 deg F (204 deg C)] <Insert temperature>.

            - Velocity: Up to [5000 fpm (25 m/s)] [6000 fpm (30 m/s)] <Insert velocity>.

          - Size Range: [4 to 72 inches (100 to 1800 mm)] <Insert size range>.

          - Construction:

            - Frame:

              - Material: Carbon steel.

                - Sizes through 24 Inches (600 mm) in Diameter: Minimum 10 gauge (4 mm) thick.

                - Sizes 26 through 48 Inches (650 through 1200 mm) in Diameter: Minimum 1/4 inch (6 mm) thick.

                - Larger Sizes: Minimum 5/16 inch (8 mm) thick.

              - Flanges:

                - Outward-turned flanges with bolt holes on each end of frame for mating to adjacent ductwork.

                - Face: Not less than 1-1/4 inches (31 mm) for damper sizes through 12 inches (300 mm) in diameter, 1-1/2 inches (38 mm) for damper sizes 14 through 24 inches (350 through 600 mm) in diameter, and 2 inches (50 mm) for larger sizes.

              - Length (Flange Face to Face):

                - Sizes through 8 Inches (200 mm) in Diameter: Not less than 6 inches (150 mm).

                - Larger Sizes: Not less than 9 inches (225 mm).

              - Standoff: Provide 3-inch (75-mm) standoff for mounting actuator to axle while accommodating field-installed duct insulation.

            - Blade: Reinforced circular flat blade constructed of carbon steel.

              - Sizes through 24 Inches (600 mm): Minimum 0.15 inch (4 mm) thick.

              - Sizes 26 through 48 Inches (650 through 1200 mm): Minimum 0.19 inch (5 mm) thick.

              - Larger Sizes: Minimum 1/4 inch (6 mm) thick.

            - Blade Stop: Full-circumference carbon steel bar, minimum 1/2 by 1/4 inch (13 by 6 mm).

            - Blade Seal: EPDM, neoprene or silicone, mechanically attached to blade and fully encompassing blade edge.

            - Axle: Continuous plated-steel axle mechanically attached to blade and angle reinforced as required.

              - Blade Diameter through 32 Inches (800 mm): Minimum 3/4 inch (19 mm) in diameter axle.

              - Blade Diameter 33 through 44 Inches (825 through 1100 mm): Minimum 1-inch (19-mm) axle diameter.

              - Blade Diameter 45 through 52 Inches (1125 through 1300 mm): Minimum 1-1/2-inch (38-mm) axle diameter.

              - Larger Sizes: Minimum 2-inch (50-mm) axle diameter.

            - Axle Shaft Seals: [Viton O-rings] [or] [double gland stuffing boxes] where indicated for application.

            - Bearings: [Grease-lubricated ball bearings bolted to frame] [Bolted grease-lubricated ball bearings located on outboard of frame with axle shaft seals].

          - Finish: Prime and paint carbon steel surfaces with a corrosion-resistant finish as recommended by manufacturer and suitable for airstream encountered at temperature range indicated. Prepare surfaces to be finished according to paint manufacturer's requirements.

        - Round, Stainless Steel, Industrial-Duty Control Dampers:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain round, stainless steel, industrial-duty control dampers from single manufacturer.

Listed manufacturers make similar products but may not comply with all requirements and options; consult manufacturers.

          - Performance:

            - Leakage: Not to exceed [0.15 cfm/in. (0.0028 L/s per mm)] <Insert leakage> of perimeter blade at [4 in. wg (1000 Pa)] <Insert pressure> differential static pressure when tested in accordance with AMCA 500D.

            - Pressure Drop: 0.05 in. wg (12.5 Pa) at 1500 fpm (7.6 m/s) across a 12-inch (300-mm) damper when tested in accordance with AMCA 500D, figure 5.3.

            - Pressure Rating: Minimum [13 in. wg (3250 Pa)] <Insert pressure>.

            - Temperature: Up to [250 deg F (121 deg C)] [400 deg F (204 deg C)] <Insert temperature>.

            - Velocity: Up to [5000 fpm (25 m/s)] [6000 fpm (30 m/s)] <Insert velocity>.

          - Size Range: [4 to 72 inches (100 to 1800 mm)] <Insert size range>.

          - Construction:

            - Frame:

              - Material: Stainless steel, [Type 304] [or] [Type 316] [Type 304 or 316 as indicated by application] <Insert type>.

                - Sizes through 24 Inches (600 mm) in Diameter: Minimum 10 gauge (4 mm) thick.

                - Sizes 26 through 48 Inches (650 through 1200 mm) in Diameter: Minimum 1/4 inch (6 mm) thick.

                - Larger Sizes: Minimum 5/16 inch (8 mm) thick.

              - Flanges:

                - Outward-turned flanges with bolt holes on each end of frame for mating to adjacent ductwork.

                - Face: Not less than 1-1/4 inches (31 mm) for damper sizes through 12 inches (300 mm) in diameter, 1-1/2 inches (38 mm) for damper sizes 14 through 24 inches (350 through 600 mm) in diameter, and 2 inches (50 mm) for larger sizes.

              - Length (Flange Face to Face):

                - Sizes through 8 Inches (200 mm) in Diameter: Not less than 6 inches (150 mm).

                - Larger Sizes: Not less than 9 inches (225 mm).

              - Standoff: Provide 3-inch (75-mm) standoff for mounting actuator to axle while accommodating field-installed duct insulation.

            - Blade: Reinforced circular flat blade constructed of stainless steel, [Type 304] [or] [Type 316] [Type 304 or 316 as indicated by application] <Insert type>.

              - Sizes through 24 Inches (600 mm): Minimum 0.15 inch (4 mm) thick.

              - Sizes 26 through 48 Inches (650 through 1200 mm): Minimum 0.19 inch (5 mm) thick.

              - Larger Sizes: Minimum 1/4 inch (6 mm) thick.

            - Blade Stop: Full-circumference bar, minimum 1/2 by 1/4 inch (13 by 6 mm) stainless steel, [Type 304] [or] [Type 316] [Type 304 or 316 as indicated by application] <Insert type>.

            - Blade Seal: EPDM, neoprene or silicone, mechanically attached to blade and fully encompassing blade edge.

            - Axle: Continuous axle mechanically attached to blade and angle reinforced as required. Axle constructed of stainless steel, [Type 304] [or] [Type 316] [Type 304 or 316 as indicated by application] <Insert type>.

              - Blade Diameter through 32 Inches (800 mm): Minimum 3/4-inch (19-mm) axle diameter.

              - Blade Diameter 33 through 44 Inches (825 through 1100 mm): Minimum 1-inch (19-mm) axle diameter.

              - Blade Diameter 45 through 52 Inches (1125 through 1300 mm): Minimum 1-1/2-inch (38-mm) axle diameter.

              - Larger Sizes: Minimum 2-inch (50-mm) axle diameter.

            - Axle Shaft Seals: [Viton O-rings] [or] [double gland stuffing boxes] where indicated for application.

            - Bearings: [Grease-lubricated ball bearings bolted to frame] [Bolted grease-lubricated ball bearings located on outboard of frame with axle shaft seals].

          - Finish: [Mill] <Insert finish>.

      - GENERAL CONTROL-DAMPER ACTUATORS REQUIREMENTS

        - Select actuators to operate related damper(s) with sufficient reserve power to provide smooth modulating action or two-position action and proper speed of response at velocity and pressure conditions to which the damper is subjected.

        - Select actuators with sufficient power and torque to close off against the maximum system pressures encountered. Actuators are to be sized to close off against the fan shutoff pressure as a minimum requirement.

        - The total damper area operated by an actuator is not to exceed 80 percent of manufacturer's maximum area rating.

        - Provide one actuator for each damper assembly where possible. Operate multiple actuators required to drive a single damper assembly in unison.

        - Avoid the use of excessively oversized actuators, which could overdrive and cause linkage failure when the damper blade has reached either its full open or closed position.

        - Use jackshafts and shaft couplings in lieu of blade-to-blade linkages when driving axially aligned damper sections.

        - Provide mounting hardware and linkages for connecting actuator to damper.

        - Select actuators to fail-safe in desired position in the event of a power [and signal ]failure.

In "Actuator Fail-Safe Positions" Paragraph below, retain second option with any subparagraphs. Indicate fail-safe position on Drawings for projects with multiple conditions with different requirements.

        - Actuator Fail-Safe Positions: [See Drawings.] [As indicated below:]

In subparagraphs below, "Last position" option is not available with some pneumatic actuator products. If "Last position" is required, consult manufacturer for double-acting actuator product options that can satisfy the requirement.

          - Exhaust Air: [Close] [Last position] [Open].

          - Outdoor Air: [Close] [Last position] [Open].

          - Supply Air: [Close] [Last position] [Open].

          - Return Air: [Close] [Last position] [Open].

          - <Insert system and fail-safe position>.

      - ELECTRIC AND ELECTRONIC CONTROL-DAMPER ACTUATORS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain electric and electronic control-damper actuators from single manufacturer.

        - Type: Motor operated, with or without gears, electric and electronic.

        - Voltage:

          - [See Drawings] [Voltage selection is delegated to professional designing control system] [24 V] [120 V] <Insert requirement>.

          - Actuator to deliver torque required for continuous uniform movement of controlled device from limit to limit when operated at rated voltage.

          - Actuator to function properly within a range of 85 to 120 percent of nameplate voltage.

        - Construction:

          - Less Than 100 W: Fiber or reinforced nylon gears with steel shaft, copper alloy or nylon bearings, and pressed-steel enclosures.

          - 100 up to 400 W: Gears ground steel, oil immersed, shaft-hardened steel running in bronze, copper alloy, or ball bearings. Operator and gear trains are to be totally enclosed in dustproof cast-iron, cast-steel, or cast-aluminum housing.

          - Greater Than 400 W: Totally enclosed reversible induction motors with auxiliary hand crank and permanently lubricated bearings.

        - Local Field Adjustment: Make spring-return actuators easily switchable from fail-safe open to fail-safe closed in the field without replacement.

        - Local Manual Override: Provide gear-type actuators with an external manual adjustment mechanism to allow manual positioning of the damper when the actuator is not powered.

        - Two-Position Actuators: Single direction, spring return or reversing type.

        - Modulating Actuators:

          - Capable of stopping at all points across full range, and starting in either direction from any point in range.

          - Control Input Signal:

Retain subparagraphs below that remain after revising "Control-Damper Applications" Article. See the Evaluations for further discussion.

            - Three Point, Tristate, or Floating Point: Clockwise and counter-clockwise inputs. One input drives actuator to open position, and other input drives actuator to close position. No signal of either input remains in last position.

            - Proportional: Actuator drives proportional to input signal and modulates throughout its angle of rotation. Suitable for [0 to 10] [or] [2 to 10] V dc [and] [4 to 20 mA] signals.

            - Pulse Width Modulation (PWM): Actuator drives to a specified position according to a pulse duration (length) of signal from a dry-contact closure, triac sink, or source controller.

Retaining "Programmable Multifunction" Subparagraph below limits manufacturer choices. Belimo Americas (USA) is one manufacturer offering the product. Consult manufacturers for more information.

            - Programmable Multifunction:

              - Control input, position feedback, and running time are to be factory or field programmable.

              - Diagnostic feedback of hunting or oscillation, mechanical overload, mechanical travel, and mechanical load limit.

              - Service data, including at a minimum, number of hours powered and number of hours in motion.

        - Position Feedback:

Retain one of first two subparagraphs below, or both, to provide a signal for remote monitoring of position through positive means. Remote monitoring requires additional control system inputs. Coordinate requirements with interface to control system.

          - [Equip] [Where indicated, equip] two-position actuators with limit switches or other positive means of a position indication signal for remote monitoring of [open] [and] [close] position.

          - [Equip] [Where indicated, equip] modulating actuators with a position feedback through [current] [or] [voltage] signal for remote monitoring.

          - Provide a position indicator and graduated scale on each actuator indicating open and closed travel limits.

        - Fail-Safe:

          - Where indicated, provide actuator to fail-safe to an end position.

          - Internal spring-return mechanism to drive controlled device to an end position (open or close) on loss of power.

          - Batteries, capacitors, and other nonmechanical forms of fail-safe operation are acceptable only where uniquely indicated.

        - Integral Overload Protection:

          - Provide against overload throughout the entire operating range in both directions.

          - Electronic overload, digital rotation sensing circuitry, mechanical end switches, or magnetic clutches are acceptable methods of protection.

        - Damper Attachment:

          - Unless otherwise required for damper interface, provide actuator designed to be directly coupled to damper shaft without need for connecting linkages.

          - Attach actuator to damper drive shaft in a way that ensures maximum transfer of power and torque without slippage.

          - Bolt and setscrew method of attachment is acceptable only if provided with at least two points of attachment.

        - Temperature and Humidity:

          - Temperature: Suitable for operating temperature range encountered by application with minimum operating temperature range of [minus 20 to plus 120 deg F (minus 29 to plus 49 deg C)] <Insert temperature range>.

          - Humidity: Suitable for humidity range encountered by application; minimum operating range is to be from [5 to 95] <Insert numbers> percent relative humidity, noncondensing.

        - Enclosure:

          - Suitable for ambient conditions encountered by application.

          - NEMA 250, [Type 2] [or] [Type 4] for indoor and protected applications.

          - NEMA 250, [Type 4] [or] [Type 4X] for outdoor and unprotected applications.

          - NEMA 250, [Type 7] [or] [Type 9] for hazardous applications requiring explosion-proof construction.

          - Provide actuator enclosure with a heater and controller where required by application.

        - Stroke Time:

          - Select operating stroke time to be compatible with equipment and system operation[, and as follows].

Retain any of first three subparagraphs below to restrict performance. Where requirements vary by application, copy and edit subparagraphs as required or indicate requirements on Drawings.

            - Operate damper from fully closed to fully open position within [15] [30] [60] [75] [90] [150] <Insert number> seconds.

            - Operate damper from fully open to fully closed position within [15] [30] [60] [75] [90] [150] <Insert number> seconds.

            - Move damper to fail-safe position within [5] [15] [30] <Insert number> seconds.

          - For actuators operating in smoke-control and other life-safety systems, comply with governing code and NFPA requirements.

        - Sound: Where actuators are located in tenant-occupied rooms with a room sound-level criteria of [NC-35] <Insert NC level> or lower, comply with the following sound levels:

          - Spring Return: [45] <Insert number> dBA.

          - Nonspring Return: [45] <Insert number> dBA.

      - PNEUMATIC CONTROL-DAMPER ACTUATORS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain pneumatic control-damper actuators from single manufacturer.

        - Where two or more actuators are installed for interrelated operation in unison, such as dampers used for mixing, provide the dampers with a positive positioner.

        - Equip pneumatic modulating actuators with a positive positioner, having the following performance characteristics:

          - Linearity: Within [1] <Insert value> percent of output signal span.

          - Hysteresis: [0.5] <Insert number> percent of the span.

        - Provide each positioner with an integrally mounted air set and pressure gauges for instrument air supply, instrument input, and positioner output. Operate on a 3 to 15 psig (21 to 103 kPa) input signal unless otherwise required by the application to comply with the control sequence of operation.

        - Rate actuators for a pressure of at least [1.1] <Insert value> times main supply air pressure to actuator, but not less than [25 psig (172 kPa)] <Insert pressure>.

        - Single-Action (Spring-Return) Diaphragm Actuators:

          - Travel: Rotary or linear travel as required by application.

          - Fail-Safe Position (Loss of Air): Air-to-open or air-to-close, as required by application.

          - Construction:

            - Diaphragm: Reinforced synthetic rubber or nitrile. Provide actuators with replaceable diaphragms[ where indicated for the application].

            - Diaphragm Casing and Plate: Cast iron, steel, or cast aluminum.

            - Spring, Stem, and Spring Adjuster: Steel or steel alloy.

            - Yoke: Cast iron, steel, or cast aluminum.

        - Double-Action (Air-to-Air) Rack-and-Pinion Actuators:

          - Travel: Rotary travel for control of quarter-turn (zero to 90 degrees) control dampers.

          - Fail-Safe Position (Loss of Air): Last position.

          - Construction:

            - Body: Anodized extruded-aluminum alloy.

            - End Caps: Cast-aluminum alloy.

            - Pistons: Cast-aluminum alloy.

            - Piston O-Ring Seals: NBR.

            - Output Shaft and Pinion: Zinc-plated carbon steel or stainless steel.

            - Travel Stops: Adjustable, stainless steel.

            - Fasteners: Stainless steel.

        - Single-Action (Spring-Return) Rack-and-Pinion Actuators:

          - Travel: Rotary travel for control of quarter-turn (zero to 90 degrees) control dampers.

          - Fail-Safe Position (Loss of Air): Air-to-open or air-to-close, as required by application.

          - Construction:

            - Body: Anodized extruded-aluminum alloy.

            - End Caps: Cast-aluminum alloy.

            - Pistons: Cast-aluminum alloy.

            - Piston O-Ring Seals: NBR.

            - Output Shaft and Pinion: Zinc-plated carbon steel or stainless steel.

            - Springs: Coated steel, steel, or steel alloy.

            - Travel Stops: Adjustable, stainless steel.

            - Fasteners: Stainless steel.

        - Provide actuator with adjustable stops for both maximum and minimum positions.

Retain "Local Manual Override" Paragraph below for applications that require local override of damper actuator operation without disconnecting the actuator from the damper.

        - Local Manual Override: Where indicated, provide actuators with an external manual adjustment mechanism to allow manual positioning of the damper through the actuator.

        - Local Position Indication: Provide a position indicator and graduated scale on each actuator. Indicate open and closed travel limits.

        - Enclosure:

          - Suitable for ambient conditions encountered by application.

          - Install actuator(s) in a supplemental enclosure with a heater and controller where required by application.

        - Position Feedback Signal:

Retain one of two subparagraphs below, or both, to provide a signal for remote monitoring of position through positive means. Remote monitoring requires additional control system inputs. Coordinate requirements with interface to control system.

          - [Equip] [Where indicated, equip] two-position actuators with limit switches or other positive means of a position indication signal for remote monitoring of [open] [and] [close] position.

          - [Equip] [Where indicated, equip] modulating actuators with a position feedback through [current] [or] [voltage] signal for remote monitoring.

        - Stroke Time:

          - Select operating stroke time to be compatible with equipment and system operation[, and as follows].

Retain any of first three subparagraphs below to restrict performance. Where requirements vary by application, copy and edit subparagraphs as required or indicate requirements on Drawings.

            - Operate damper from fully closed to fully open position within [15] [30] <Insert number> seconds.

            - Operate damper from fully open to fully closed position within [15] [30] <Insert number> seconds.

            - Move damper to fail-safe position within [5] [15] [30] <Insert number> seconds.

          - For actuators operating in smoke-control and other life-safety systems, comply with governing code and NFPA requirements.

- EXECUTION

      - EXAMINATION

        - Examine substrates and conditions for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

        - Examine roughing-in for dampers and instruments installed in duct systems to verify actual locations of connections before installation.

        - Prepare written report, endorsed by Installer, listing conditions detrimental to performance.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - CONTROL-DAMPER APPLICATIONS

Retain this article unless all requirements for control dampers and actuators for different applications are indicated on Drawings. Where Drawings indicate only some requirements, revise this article accordingly.

        - Select from damper types indicated to achieve performance requirements and characteristics indicated while subjected to full range of system operation encountered.

        - Rectangular Control-Damper Applications:

Copy and revise subparagraphs below to suit each unique application requiring a different control-damper and actuator type. Indicate requirements on Drawings for projects with numerous requirements.

          - Exhaust Air: [Rectangular dampers with aluminum airfoil blades] [Rectangular dampers with galvanized-steel airfoil blades] [Rectangular dampers with stainless steel airfoil blades] [Rectangular dampers with aluminum flat blades] [Rectangular dampers with galvanized-steel flat blades] [Rectangular dampers with stainless steel flat blades]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

          - Outdoor Air: [Rectangular dampers with aluminum airfoil blades] [Rectangular dampers with galvanized-steel airfoil blades] [Rectangular dampers with stainless steel airfoil blades] [Rectangular dampers with aluminum flat blades] [Rectangular dampers with galvanized-steel flat blades] [Rectangular dampers with stainless steel flat blades]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

          - Return Air: [Rectangular dampers with aluminum airfoil blades] [Rectangular dampers with galvanized-steel airfoil blades] [Rectangular dampers with stainless steel airfoil blades] [Rectangular dampers with aluminum flat blades] [Rectangular dampers with galvanized-steel flat blades] [Rectangular dampers with stainless steel flat blades]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

          - Supply Air: [Rectangular dampers with aluminum airfoil blades] [Rectangular dampers with galvanized-steel airfoil blades] [Rectangular dampers with stainless steel airfoil blades] [Rectangular dampers with aluminum flat blades] [Rectangular dampers with galvanized-steel flat blades] [Rectangular dampers with stainless steel flat blades]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

        - Rectangular Control Dampers with Insulated Blade Applications:

Copy and revise subparagraphs below to suit each unique application requiring a different control-damper and actuator type. Indicate requirements on Drawings for projects with numerous requirements.

          - Exhaust Air: [Rectangular dampers with insulated aluminum airfoil blades] [Rectangular dampers with insulated aluminum airfoil blades and thermal break frames]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

          - Outdoor Air: [Rectangular dampers with insulated aluminum airfoil blades] [Rectangular dampers with insulated aluminum airfoil blades and thermal break frames]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

          - Return Air: [Rectangular dampers with insulated aluminum airfoil blades] [Rectangular dampers with insulated aluminum airfoil blades and thermal break frames]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

          - Supply Air: [Rectangular dampers with insulated aluminum airfoil blades] [Rectangular dampers with insulated aluminum airfoil blades and thermal break frames]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

        - Rectangular Control Dampers with Integral Airflow Applications:

Copy and revise subparagraphs below to suit each unique application requiring a different control-damper and actuator type. Indicate requirements on Drawings for projects with numerous requirements.

          - Applications with Airflow Measurement: Rectangular dampers with aluminum airfoil blades and integral airflow measurement using [pressure] [or] [thermal] sensing.

          - Applications with Airflow Control: Rectangular dampers with aluminum airfoil blades and integral airflow control using [pressure] [or] [thermal] sensing.

        - Rectangular Industrial-Duty Control-Damper Applications:

Copy and revise subparagraphs below to suit each unique application requiring a different control-damper and actuator type. Indicate requirements on Drawings for projects with numerous requirements.

          - Exhaust Air: [Rectangular industrial-duty dampers with galvanized-steel airfoil blades] [Rectangular industrial-duty dampers with stainless steel airfoil blades]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

          - Outdoor Air: [Rectangular industrial-duty dampers with galvanized-steel airfoil blades] [Rectangular industrial-duty dampers with stainless steel airfoil blades]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

          - Return Air: [Rectangular industrial-duty dampers with galvanized-steel airfoil blades] [Rectangular industrial-duty dampers with stainless steel airfoil blades]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

          - Supply Air: [Rectangular industrial-duty dampers with galvanized-steel airfoil blades] [Rectangular industrial-duty dampers with stainless steel airfoil blades]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

        - Round Control-Damper Applications:

Copy and revise subparagraphs below to suit each unique application requiring a different control-damper and actuator type. Indicate requirements on Drawings for projects with numerous requirements.

          - Exhaust Air: [Round galvanized steel dampers, sleeve ends] [Round stainless steel dampers, sleeve ends] [Round galvanized-steel dampers, flange ends] [Round stainless steel dampers, flange ends]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

          - Outdoor Air: [Round galvanized-steel dampers, sleeve ends] [Round stainless steel dampers, sleeve ends] [Round galvanized-steel dampers, flange ends] [Round stainless steel dampers, flange ends]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

          - Return Air: [Round galvanized-steel dampers, sleeve ends] [Round stainless steel dampers, sleeve ends] [Round galvanized-steel dampers, flange ends] [Round stainless steel dampers, flange ends]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

          - Supply Air: [Round galvanized-steel dampers, sleeve ends] [Round stainless steel dampers, sleeve ends] [Round galvanized-steel dampers, flange ends] [Round stainless steel dampers, flange ends]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

        - Round Industrial-Duty Control-Damper Applications:

Copy and revise subparagraphs below to suit each unique application requiring a different control-damper and actuator type. Indicate requirements on Drawings for projects with numerous requirements.

          - Exhaust Air: [Round carbon steel, industrial-duty dampers] [Round, stainless steel, industrial-duty dampers]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

          - Outdoor Air: [Round carbon steel, industrial-duty dampers] [Round, stainless steel, industrial-duty dampers]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

          - Return Air: [Round carbon steel, industrial-duty dampers] [Round, stainless steel, industrial-duty dampers]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

          - Supply Air: [Round carbon steel, industrial-duty dampers] [Round, stainless steel, industrial-duty dampers]; <Insert value> maximum air pressure and <Insert value> maximum air velocity.

      - INSTALLATION, GENERAL

        - Furnish and install products required to satisfy most stringent requirements indicated.

        - Properly support dampers and actuators, tubing, wiring, and conduit to comply with requirements indicated. Brace all products to prevent lateral movement and sway or a break in attachment when subjected to a seismic, wind, or others forces common to the application.

        - Provide ceiling, floor, roof, [and ]wall openings[, and sleeves ]required by installation. Before proceeding with drilling, punching, or cutting, check location first for concealed products that could potentially be damaged. Patch, flash, grout, seal, and refinish openings to match adjacent condition.

        - Seal penetrations made in fire-rated and acoustically rated assemblies.

        - Fastening Hardware:

          - Wrenches, pliers, or other tools that will cause injury to or mar surfaces of rods, nuts, and other parts are prohibited for assembling and tightening nuts.

          - Tighten bolts and nuts firmly and uniformly. Do not overstress threads by excessive force or by oversized wrenches.

          - Lubricate threads of bolts, nuts, and screws with graphite and oil before assembly.

        - Install products in locations that are accessible and that will permit calibration and maintenance from floor, equipment platforms, or catwalks. Where ladders are required for Owner's access, confirm unrestricted ladder placement is possible under occupied condition.

        - Corrosive Environments:

          - Use products that are suitable for environment to which they will be subjected.

          - If possible, avoid or limit use of materials in corrosive environments, including, but not limited to, the following:

            - Laboratory exhaust airstreams.

            - Process exhaust airstreams.

            - <Insert applications>.

          - Use Type 316 stainless steel tubing and fittings when in contact with a corrosive environment.

          - When conduit is in contact with a corrosive environment, use Type 316 stainless steel conduit and fittings or conduit and fittings that are coated with a corrosive-resistant coating that is suitable for environment.

          - Where actuators are located in a corrosive environment and are not corrosive resistant from manufacturer, field install products in NEMA 250, Type 4X enclosure constructed of Type 316L stainless steel.

      - CONTROL DAMPERS

        - Install smooth transitions, not exceeding [15] [30] <Insert number> degrees, to dampers larger or smaller than adjacent duct. Install transitions as close to damper as possible but at distance to avoid interference and impact to performance. Consult manufacturer for recommended clearance.

        - Clearance:

          - Locate dampers for easy access and provide separate support of dampers that cannot be handled by service personnel without hoisting mechanism.

          - Install dampers with at least [24 inches (600 mm)] <Insert distance> of clear space on sides of dampers requiring service access unless more space is recommended by manufacturer. Provide code required clearances as applicable.

        - Service Access:

          - Install dampers and actuators to be accessible for visual inspection and service.

          - Install access door(s) in duct or equipment located upstream of damper to allow service personnel to hand clean any portion of damper, linkage, and actuator. Comply with requirements in Section 233300 "Air Duct Accessories."

        - Install dampers straight and true, level in all planes, and square in all dimensions.

        - Install supplementary structural reinforcement for large multiple-section dampers if factory-furnished support alone cannot handle loading.

        - Attach field-installed actuator(s) to damper drive shaft.

        - For duct-mounted and equipment-mounted dampers installed outside of equipment, install a visible and accessible indication of damper position from outside.

      - IDENTIFICATION

        - Identify system components, wiring, cabling, and terminals. Each piece of wire, cable, and tubing is to have the same designation at each end for operators to determine continuity at points of connection. Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

        - Install engraved phenolic nameplate with damper identification on damper[ and on face of ceiling where damper is concealed above ceiling].

      - ELECTRICAL CONNECTIONS

        - Install electrical power to field-mounted control devices requiring electrical power.

        - Connect wiring in accordance with Section 260519 "Low-Voltage Electrical Power Conductors and Cables" and Section 260523 "Control-Voltage Electrical Power Cables."

        - Ground equipment in accordance with Section 260526 "Grounding and Bonding for Electrical Systems."

        - Furnish and install raceways. Comply with requirements in Section 260533.13 "Conduits for Electrical Systems."

        - Furnish and install circuit breakers. Comply with requirements in Section 262816 "Enclosed Switches and Circuit Breakers."

        - Install electrical devices furnished by manufacturer, but not factory mounted, in accordance with NFPA 70 and NECA 1.

        - Install nameplate for each electrical connection, indicating electrical equipment designation and circuit number feeding connection.

Retain one of two subparagraphs below. First subparagraph cross-references Section 260553 "Identification for Electrical Systems" and should be retained for consistent electrical identification. Second subparagraph is an abbreviated version of the product specified in Section 260553 "Identification for Electrical Systems."

          - Nameplate to be laminated acrylic or melamine plastic signs, as specified in Section 260553 "Identification for Electrical Systems."

          - Nameplate to be laminated acrylic or melamine plastic signs with a black background and engraved white letters at least 1/2 inch (13 mm) high.

      - CONTROL CONNECTIONS

Retain "Pneumatic Control Connections" Paragraph below for pneumatic control valves.

        - Pneumatic Control Connections: Connect pneumatic control valve actuators and accessories to pneumatic main and signal air. Comply with requirements in Section 230923 "Direct Digital Control (DDC) System for HVAC."

        - Install control signal wiring to field-mounted control devices.

        - Connect control signal wiring in accordance with Section 260523 "Control-Voltage Electrical Power Cables."

        - Furnish and install raceways. Comply with requirements in Section 260533.13 "Conduits for Electrical Systems."

      - CLEANING

        - Remove grease, mastic, adhesives, dust, dirt, stains, fingerprints, labels, and other foreign materials from exposed surfaces.

      - STARTUP

        - Control-Damper Checkout:

          - Check installed products before continuity tests, leak tests, and calibration.

          - Check dampers for proper location and accessibility.

          - Verify that control dampers are installed correctly for flow direction.

          - Verify that proper blade alignment, either parallel or opposed, has been provided.

          - Verify that damper frame attachment is properly secured and sealed.

          - Verify that damper actuator and damper linkage attachment are secure.

          - Verify that actuator wiring is complete, enclosed, and connected to correct power source.

          - Verify that damper blade travel is smooth and unobstructed throughout operating range.

Retain "Pneumatic Control Dampers" Paragraph below for pneumatic control dampers.

          - Pneumatic Control Dampers:

            - Check instrument tubing for proper isolation, fittings, slope, dirt legs, drains, material, and support.

            - Verify air supply for each product is properly installed.

            - Verify that pressure gauges are provided in each air line to damper actuator and positioner.

      - ADJUSTMENT, CALIBRATION, AND TESTING

        - Stroke and adjust control dampers following manufacturer's recommended procedure, from 100 percent open to 100 percent closed back to 100 percent open.

Retain first paragraph below for dampers with pilot positioners.

        - Stroke control dampers with pilot positioners. Adjust damper and positioner following manufacturer's recommended procedure, so damper is 100 percent closed, 50 percent closed, and 100 percent open at proper air pressure.

        - Check and document open and close cycle times for applications with a cycle time of less than [30] <Insert value> seconds.

        - For control dampers equipped with positive position indication, check feedback signal at multiple positions to confirm proper position indication.

END OF SECTION 230923.12