Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 230923.33 - VIBRATION INSTRUMENTS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Mechanical vibration switches.

          - Electronic vibration switches.

          - Combination vibration switch and transmitters.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 230923 "Direct-Digital Control System for HVAC" for control equipment and software, relays, electrical power devices, uninterruptible power supply units, wire, and cable.

          - Section 230993 "Sequence of Operations for HVAC Controls" for requirements that relate to this Section.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

        - RMS: Root-mean-square value of alternating voltage, which is the square root of the mean value of the square of the voltage values during a complete cycle.

      - ACTION SUBMITTALS

        - Product Data: For the following:

          - Mechanical vibration switches.

          - Electronic vibration switches.

          - Combination vibration switch and transmitters.

        - Product Data Submittals: For each product, including the following:

          - Construction details, material descriptions, dimensions of individual components and profiles, and finishes.

          - Operating characteristics, electrical characteristics, and furnished accessories indicating default control signal with loss of power, calibration data specific to each unique application, and electrical power requirements.

          - Product description with complete technical data, performance curves, and product specification sheets.

          - Installation operation and maintenance instructions including factors affecting performance.

        - Shop Drawings:

          - Include plans, elevations, sections, and[ mounting] details.

          - Include details of product assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

          - Include diagrams for power, signal, and control wiring.

          - Include number-coded identification system for unique identification of wiring and cable.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: To include in operation and maintenance manuals.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - MECHANICAL VIBRATION SWITCHES

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Requirements in remaining paragraphs are based on Metrix's "Model 5550."

        - Description: Inertia-sensitive armature mechanism trips on high vibration and operates snap action switch.

        - Performance:

          - Frequency Range: Zero to 3600 rpm.

          - Vibration Range: Zero to [2] [5] [10] g.

          - Temperature Limits: Minus 40 to 158 deg F (Minus 40 to 70 deg C).

          - Electrical Rating: 15 A at 125- or 480-V ac.

          - Switch Type: [SPDT] [DPDT] snap switch.

          - Start Delay: 20 to 30 seconds, by applying reset voltage at start signal to prevent switch from tripping.

Retain first paragraph below for hazardous environments.

        - Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for hazardous environments Class I, Groups B, C, and D; Class II, Groups E, F, and G.

        - Operator Interface:

          - Vibration Set-Point Adjustment: Zero to 100 percent of range.

          - Push-button reset on switch face and reset coil for remote reset.

        - Enclosure Construction:

          - Cast aluminum.

          - NEMA 250, [Type 4] [or] [Type 4X].

          - Electrical Connection: Screw terminals.

          - Conduit Connection: 3/4-inch (21-mm) trade size.

      - ELECTRONIC VIBRATION SWITCHES

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Requirements in remaining paragraphs are based on Metrix's "Model 5477."

        - Description:

          - Accelerometer-based velocity response.

          - Single set point.

        - Performance:

          - Frequency Range: 3 to 500 Hz.

          - Vibration Range: Zero to 1.0 inch (25.4 mm) per second.

          - Temperature Limits: Minus 4 to 167 deg F (Minus 20 to 75 deg C).

          - Electrical Rating: 5-A inductive, 60-A surge for one cycle; normally open-triac leakage is 10 mA.

          - Trip Logic: Field-selectable, normally open-/normally closed-triac, non-latching, automatic reset.

          - Start Trip Timer: 30 seconds.

          - Monitor Trip Delay: 3 seconds.

Retain first paragraph below for hazardous environments.

        - Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for hazardous environments Class I, Groups C and D; Class II, Groups E, F, and G.

        - Operator Interface:

          - Vibration Set-Point Adjustment: Externally adjustable with tamperproof gradual dial.

          - Trip Indicator: Flashing red LED.

          - Digital Display: 2.5-digit numerical display of vibration level.

        - Enclosure Construction:

          - Cast aluminum.

          - Screw-on cover.

          - NEMA 250, Type 4.

          - Electrical Connection: Two wires, 24 inches (600 mm) long.

          - Conduit Connection: 1/2-inch (16-mm) trade size, sealed entry.

          - Flange mounting adapter, as applicable.

      - COMBINATION VIBRATION SWITCH AND TRANSMITTERS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Requirements in remaining paragraphs are based on Metrix's "PRO6000 Series." Microprocessor based with fully programmable options.

        - Description:

          - Input sensitivity.

          - Full-scale vibration range.

          - Mode: Peak or rms.

          - Trip delay.

          - Start delay.

          - Relay State: Latching or non-latching.

          - Relay: Non-energized, normally open or energized, normally closed.

        - Accelerometer integral to unit with capability of multiple remote sensor inputs.

          - Instrument furnished with programming and setup software.

        - Performance:

          - Frequency Range for Integral Accelerometer: 2 to 1000 Hz.

          - Ambient Temperature Limits: Minus 40 to 185 deg F (Minus 40 to 85 deg C).

          - Humidity: 100 percent condensing.

        - Analog Output Current Signal:

          - Two-wire, 4- to 20-mA dc current source.

          - Signal capable of operating into 1000-ohm load.

        - Digital Output Signal: [Single] [Dual] relay(s).

        - Operator Interface:

          - USB or keypad configurable.

          - Digital Display: Two lines of display.

        - Enclosure Construction:

          - Cast aluminum.

          - Screw-on cover.

          - NEMA 250, Type 4X.

          - Electrical Connection: Screw terminals.

          - Conduit Connection: 3/4-inch (21-mm) trade size.

- EXECUTION

      - EXAMINATION

        - Examine substrates and conditions for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

        - Prepare written report, endorsed by Installer, listing conditions detrimental to performance.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

Retain "Vibration Instrument Applications" Article below unless requirements for instruments for different applications are indicated on Drawings.

      - VIBRATION INSTRUMENT APPLICATIONS

Copy and edit paragraph below to suit each unique application requiring a different instrument type.

        - <Insert application>: [Mechanical switch] [Electronic switch] [Combination switch and transmitter].

      - INSTALLATION

        - Install products level, plumb, parallel, and perpendicular with building construction.

        - Use manufacturer's mounting brackets to accommodate field mounting. Securely support and brace products to prevent vibration and movement.

        - Properly support instrument wiring and conduit to comply with requirements indicated. Brace all products to prevent lateral movement and sway or a break in attachment when subjected to a <Insert value> force.

        - Fastening Hardware:

          - Stillson wrenches, pliers, and other tools that cause injury to or mar surfaces of rods, nuts, and other parts are prohibited for work of assembling and tightening nuts.

          - Tighten bolts and nuts firmly and uniformly. Do not overstress threads by excessive force or by oversized wrenches.

          - Lubricate threads of bolts, nuts, and screws with graphite and oil before assembly.

        - Install products in locations that are accessible and that permit calibration and maintenance from floor, equipment platforms, or catwalks. Where ladders are required for Owner's access, confirm unrestricted ladder placement is possible under occupied condition.

        - Corrosive Environments:

          - Use products that are suitable for environment to which they are subjected.

          - If possible, avoid or limit use of materials in corrosive environments.

          - When conduit is in contact with a corrosive environment, use Type 316 stainless steel conduit and fittings or conduit and fittings that are coated with a corrosive-resistant coating that is suitable for environment.

          - Where instruments are located in a corrosive environment and are not corrosive resistant from manufacturer, field install products in a NEMA 250, Type 4X enclosure constructed of Type 316L stainless steel.

      - ELECTRICAL CONNECTIONS

        - Furnish and install electrical power to products requiring electrical connections.

        - Furnish and install circuit breakers. Comply with requirements in Section 262816 "Enclosed Switches and Circuit Breakers."

        - Furnish and install power wiring. Comply with requirements in Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

        - Furnish and install raceways. Comply with requirements in Section 260533.13 "Conduits for Electrical Systems."

      - IDENTIFICATION

        - Identify system components, wiring, cabling, and terminals. Each piece of wire is to have the same designation at each end for operators to determine continuity at points of connection. Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

        - Install engraved phenolic nameplate with instrument identification.

      - ADJUSTMENT, CALIBRATION, AND TESTING

        - Description:

          - Calibrate each instrument installed that is not factory calibrated and provided with calibration documentation.

          - Provide a written description of proposed field procedures and equipment for calibrating each type of instrument. Submit procedures before calibration and adjustment.

          - For each analog instrument, make a three-point test of calibration for both linearity and accuracy.

          - Equipment and procedures used for calibration are to comply with instrument manufacturer's written instructions.

          - Provide diagnostic and test equipment for calibration and adjustment.

          - Field instruments and equipment used to test and calibrate installed instruments are to have accuracy at least twice the instrument accuracy being calibrated. For example, an installed instrument with an accuracy of 1 percent is to be checked by an instrument with an accuracy of 0.5 percent.

          - Calibrate each instrument according to instrument instruction manual supplied by manufacturer.

          - If after calibration indicated performance cannot be achieved, replace out-of-tolerance instruments.

          - Comply with field-testing requirements and procedures indicated by ASHRAE Guideline 11, "Field Testing of HVAC Control Components," in the absence of specific requirements and to supplement requirements indicated.

        - Analog Signals:

          - Check analog voltage signals using a precision voltage meter at zero, 50, and 100 percent.

          - Check analog current signals using a precision current meter at zero, 50, and 100 percent.

        - Digital Signals:

          - Check digital signals using a jumper wire.

          - Check digital signals using an ohmmeter to test for contact.

        - Switches: Calibrate switches to make or break contact at set points indicated.

      - ADJUSTING

        - Occupancy Adjustments: When requested within [12] <Insert number> months from date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions. Provide up to [two] <Insert number> visits to Project during other-than-normal occupancy hours for this purpose.

END OF SECTION 230923.33