Copyright 2022 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 231213 - FACILITY FUEL-OIL PUMPS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Submersible fuel-oil storage tank pumps.

          - Fuel-oil pumps - simplex.

          - Fuel-oil pumps - multiplex.

          - Fuel-oil polishing systems.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

          - Submersible fuel-oil storage tank pumps.

          - Fuel-oil pumps - simplex.

          - Fuel-oil pumps - multiplex.

          - Fuel-oil polishing systems.

        - Product Data Submittals: For each product.

          - Include construction details, material descriptions, and dimensions of individual components and profiles.

          - Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

        - Shop Drawings: For fuel-oil pumps[ and fuel-oil polishing systems].

          - Include construction details and dimensions of individual components for fuel-oil pumps.

          - Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

          - Scale: [1/4 inch per foot (1:50)] <Insert scale>.

Retain "Delegated Design Submittals" Paragraph below if design services have been delegated to Contractor. If seismic restraints are not applicable, signing and sealing by professional engineer may not be required. Verify with authorities having jurisdiction.

        - Delegated Design Submittals: For vibration isolation[ and seismic restraints] indicated to comply with performance requirements and design criteria, including analysis data[ signed and sealed by the qualified professional engineer responsible for their preparation].

          - Detail fabrication and assembly of anchors[ and seismic restraints].

          - Design Calculations: Calculate requirements for selecting seismic restraints.

          - Detail fabrication and assembly of hangers, supports, and attachments of the same to building structure.

      - INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Retain "Coordination Drawings" Paragraph below where coordination is required for installation of products and materials by separate installers. Preparation of coordination drawings requires participation of each trade involved; coordinate with other Sections specifying products and materials to be included. See Section 013100 "Project Management and Coordination."

        - Coordination Drawings: Plans and details, or Building Information Model (BIM), drawn to scale, showing items described in this Section and coordinated with all building trades.

Retain "Seismic Qualification Certificates" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 230548 "Vibration and Seismic Controls for HVAC." See ASCE/SEI 7 for certification requirements for equipment and components.

        - Seismic Qualification Certificates: For fuel-oil pumps[, and fuel-oil polishing systems,] from manufacturer.

          - Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

          - Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

          - Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

Coordinate "Qualification Statements" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article. If inserting additional entities or specialist, add qualifications to "Quality Assurance" Article.

        - Qualification Statements: For professional engineer.

        - Sample Warranties: For [fuel-oil pumps] [fuel-oil polishing system].

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For fuel-oil pumps[ and fuel-oil polishing systems].

      - MAINTENANCE MATERIAL SUBMITTALS

See Section 017700 "Closeout Procedures" for submission of maintenance material items.

        - Extra Stock Material: Furnish extra materials[, from the same production run,] to Owner that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

        - Drive Belt: [One] <Insert number> for each belt-driven pump.

      - QUALITY ASSURANCE

        - Delegated Design Engineer Qualifications: A professional engineer who is legally qualified to practice in [state] <Insert jurisdiction> where Project is located and who is experienced in providing engineering services of the type indicated.

      - WARRANTY

When warranties are required and available, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

        - Manufacturer Warranty: [Manufacturer agrees] [Installer agrees] [Manufacturer and installer agree] to repair or replace fuel-oil pumps[ and fuel-oil polishing systems] that fail in materials or workmanship within specific warranty period.

Verify warranty periods in "Warranty Period for Fuel-Oil Pumps" and "Warranty Period for Fuel-Oil Polishing Systems" paragraphs below.

        - Warranty Period for Fuel-Oil Pumps: <Insert number> year(s) from date of Substantial Completion.

        - Warranty Period for Fuel-Oil Polishing Systems: <Insert number> year(s) from date of Substantial Completion.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - PERFORMANCE REQUIREMENTS

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by an NRTL, and marked for intended location and use.

        - Maximum Operating-Pressure Ratings: [3 psig (21 kPa)] <Insert pressure> fuel-oil supply pressure at oil-fired appliances.

Retain "Delegated Design" Paragraph below if Contractor is required to assume responsibility for design.

        - Delegated Design: Engage a qualified professional engineer, as defined in Section 014000 "Quality Requirements," to design restraint and anchors for fuel-oil pumps[ and fuel-oil polishing systems], including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

Retain "Seismic Performance" Paragraph below for projects requiring seismic design. Delete paragraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

        - Seismic Performance: Factory-installed support attachments for pumps [and fuel-oil polishing systems ]are to withstand the effects of earthquake motions determined in accordance with [ASCE/SEI 7] <Insert requirement>.

Retain first subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

          - The term "withstand" means "the unit will remain in place without separation of any parts when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

For life-safety components required to function after an earthquake (such as fire-sprinkler systems, components that contain hazardous content, system components serving critical healthcare functions, and storage racks in structures open to the public), the Component Importance Factor is 1.5. For other components, the Component Importance Factor is 1.0 unless the structure is in Seismic Use Group III and component is necessary for continued operation of facility or failure of component could impair continued operation of facility, in which case the Component Importance Factor is 1.5.

          - Component Importance Factor: [1.5] [1.0].

See ASCE/SEI 7, Coefficients for Architectural Component Table and Seismic Coefficients for Mechanical and Electrical Components Table, for requirements to be inserted in subparagraph below.

          - <Insert requirements for Component Amplification Factor and Component Response Modification Factor>.

        - Listed and labeled for fuel-oil service by an NRTL acceptable to authorities having jurisdiction.

      - SUBMERSIBLE FUEL-OIL STORAGE TANK PUMPS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain submersible fuel-oil storage tank pumps from single manufacturer.

        - Comply with UL 79, UL 87, and UL 343.

          - Impeller: Turbine.

          - Housing and Volute: Cast iron.

          - Bearings: Bronze, self-lubricating.

          - Seals: Mechanical.

          - Shaft: Polished steel.

          - Suspension Piping: Telescoping to accommodate tank diameter and depth of bury.

          - Base: Steel.

          - Pressure Relief: Built in.

          - Discharge Check Valve: Built in.

          - Drive: Direct, close coupled.

        - Controls: Pump controller panel complying with UL 353 and UL 508C and with interlock and terminals for connections to fuel-oil-burning equipment.

Retain desired control features from 11 subparagraphs below.

          - Maintain minimum manifold pressure with outdoor-air temperature less than [60 deg F (16 deg C)] <Insert temperature>.

          - Seven-day schedule.

          - Stage multiple pumps to maintain pressure at a common supply manifold.

          - Alternate pumps to equalize run time.

          - Alarm motor failure.

          - Manual reset dry-run protection.

          - Stop pumps if fuel level falls below pump suction.

          - De-energize and sound alarm for pump, locked-rotor condition.

          - Sound alarm for open circuit and for high and low voltage.

          - Lights indicate normal power on, run, and off conditions.

          - Interface with automatic control system. Comply with requirements in Section 230923 "Direct Digital Control (DDC) System for HVAC" to control and indicate the following:

            - Start/stop pump set when required by schedule, fuel-fired appliance operation, day tank level control, or weather conditions.

            - Operating status.

            - Alarm off-normal status.

If Project has more than one submersible fuel-oil pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

          - Number of Stages: <Insert number>.

          - Capacity: <Insert gph (L/s)>.

          - Discharge Pressure: <Insert psig (kPa)>.

          - Outlet Size: <Insert NPS (DN)>.

          - Motor Speed: <Insert rpm>.

          - Motor Horsepower: <Insert value>.

          - Electrical Characteristics:

            - Volts: [120] [208] [240] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: 60.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

      - FUEL-OIL PUMPS - SIMPLEX

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain fuel-oil pumps - simplex, from single manufacturer.

        - Description: Comply with UL 343 and HI 3.1-3.5.

          - Type: Positive-displacement, rotary type.

          - Impeller: [Steel gear with crescent] [Carbon vane].

          - Housing: Cast-iron foot mounted.

          - Bearings: Bronze, self-lubricating.

          - Shaft: Polished steel.

          - Seals: Mechanical.

          - Base: Steel.

          - Pressure Relief: Built in.

          - Discharge Check Valve: Built in.

Some manufacturers provide close-coupled pumps in "Drive" Paragraph below only in certain size ranges.

        - Drive: [V-belt with guard; gear reducer; or direct, close coupled] [V-belt with guard] [Gear reducer] [Direct, close coupled].

        - Controls:

Retain desired control features from nine subparagraphs below.

          - Maintain minimum manifold pressure with outdoor-air temperature less than [60 deg F (16 deg C)] <Insert temperature>.

          - Seven-day schedule.

          - Alarm motor failure.

          - Manual reset dry-run protection.

          - Stop pump if fuel level falls below pump suction.

          - De-energize and sound alarm for pump, locked-rotor condition.

          - Sound alarm for open circuit and for high and low voltage.

          - Lights are to indicate normal power on, run, and off conditions.

          - Interface with automatic control system. Comply with requirements in Section 230923 "Direct Digital Control (DDC) System for HVAC" to control and indicate the following:

            - Start/stop pump set when required by schedule, fuel-fired appliance operation, day tank level control, or weather conditions.

            - Operating status.

            - Alarm off-normal status.

If Project has more than one simplex fuel-oil transfer pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

          - Number of Stages: <Insert number>.

          - Capacity: <Insert gph (L/s)>.

          - Inlet Vacuum: <Insert inches Hg (kPa)>.

          - Discharge Pressure: <Insert psig (kPa)>.

          - Inlet and Outlet Size: <Insert NPS (DN)>.

          - Motor Speed: <Insert rpm>.

          - Motor Horsepower: <Insert value>.

          - Electrical Characteristics:

            - Volts: [120] [208] [240] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: 60.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

      - FUEL-OIL PUMP SETS - MULTIPLEX

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Paragraph below to require all fuel-oil pump sets-multiplex from a single manufacturer. Some product options/characteristic indicated are not available from multiple manufacturers and may limit competition. Consult manufacturers.

        - Source Limitations: Obtain fuel-oil pump sets - multiplex, from single manufacturer.

        - Description: Comply with HI 3.1-3.5.

          - Type: Positive-displacement, rotary type.

Second option in "Configuration" Subparagraph below may not be available from all manufacturers and may limit competition. Consult manufacturers for availability.

          - Configuration: [Duplex] [Triplex].

          - Impeller: [Steel gear with crescent] [Carbon vane].

          - Housing: Cast-iron foot mounted.

          - Bearings: Bronze, self-lubricating.

          - Shaft: Polished steel.

          - Seals: Mechanical.

          - Base: Steel.

          - Pressure Relief: Built in.

          - Discharge Check Valve: Built in.

Some manufacturers provide close-coupled pumps in "Drive" Paragraph below only in certain size ranges. Consult manufacturers.

        - Drive: [V-belt with guard, gear reducer, or direct close coupled] [V-belt with guard] [Gear reducer] [Direct close coupled].

        - Controls:

Retain desired control features from 11 subparagraphs below.

          - Maintain minimum manifold pressure with outdoor-air temperature less than [60 deg F (16 deg C)] <Insert temperature>.

          - Seven-day schedule.

          - Stage multiple pumps to maintain pressure at a common supply manifold.

          - Alternate pumps to equalize run time.

          - Alarm motor failure.

          - Manual reset dry-run protection.

          - Stop pumps if fuel level falls below pump suction.

          - De-energize and sound alarm for pump, locked-rotor condition.

          - Sound alarm for open circuit and for high and low voltage.

          - Lights indicate normal power on, run, and off conditions.

          - Interface with automatic control system. Comply with requirements in Section 230923 "Direct Digital Control (DDC) System for HVAC" to control and indicate the following:

            - Start/stop pump set when required by schedule, fuel-fired appliance operation, day tank level control, or weather conditions.

            - Operating status.

            - Alarm off-normal status.

        - Piping Furnished with Pumps: Steel with ferrous fittings and threaded or welded joints.

        - Strainers Furnished with Pumps: Duplex, basket type with corrosion-resistant-metal-screen baskets.

If Project has more than one duplex or triplex fuel-oil transfer pump set, delete "Capacities and Characteristics" Paragraph below and schedule pump sets on Drawings.

        - Capacities and Characteristics:

          - Number of Stages: <Insert number>.

          - Capacity (Each Pump): <Insert gph (L/s)>.

          - Inlet Vacuum: <Insert inches Hg (kPa)>.

          - Discharge Pressure: <Insert psig (kPa)>.

          - Inlet and Outlet Size: <Insert NPS (DN)>.

          - Motor Speed: <Insert rpm>.

          - Motor Horsepower (Each Pump): <Insert value>.

          - Electrical Characteristics (Pump Set):

            - Volts: [120] [208] [240] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: 60.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

      - FUEL-OIL POLISHING SYSTEMS

Retain this article for fuel systems that serve diesel-engine-driven equipment. Authorities having jurisdiction may require this system for some types of facilities such as healthcare facilities. Fuel-polishing systems circulate fuel oil from storage tanks through filters and back to storage tanks to remove moisture, particulates, and biological growth. A fuel maintenance program may be implemented by using fuel oil before it begins to deteriorate (approximately one month), by periodic replacement of fuel oil, or by polishing/filtering the fuel and adding stabilizers.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain fuel-oil polishing system from single manufacturer.

        - Description: Factory-fabricated and -wired, fuel-oil polishing system for fuel-oil filtration; with enclosure, filter, fuel-oil pump, and controls.

          - System to be FM Global approved and be listed and labeled an NRTL acceptable to authorities having jurisdiction.

          - Enclosure: NEMA 250, Type 3R, painted steel containing pumps, filters, accessories, and controls. Hinged door on the front of enclosure.

          - Pump: Comply with HI 3.1-3.5, steel gear with crescent, positive-displacement, direct-coupled, rotary type.

          - Materials: Cast-iron housing; bronze bearings; steel shaft; mechanical seals; and built-in, pressure relief bypass valve.

          - Piping: Steel with malleable-iron fittings and threaded joints or wrought-steel fittings and welded joints.

          - Spin-on, Replaceable, Multistage Filters:

            - Stage 1: 100-mesh strainer.

            - Stage 2: Centrifuge to separate particulates and water from oil.

            - Stage 3: Coalescing water and particulate filter.

            - Stage 4: 30-micron particulate removal.

            - Stage 5: 10-micron particulate removal.

            - Stage 6: Minimum 99.5 percent water removal with see-through bowl and water-sensor probe.

            - Stage 7: Minimum 99 percent [1.5] [3] [5]-micron particulate removal.

Retain "Multiple-Tank Manifolds" Subparagraph below for multiple fuel-oil storage tanks.

          - Multiple-Tank Manifolds:

            - Manifold fabricated of Schedule 80, black steel pipe and threaded nipples for [two] [three] [four] tanks.

            - Solenoid valves for supply and return piping to each tank.

            - Strainers for each tank supply connection.

Retain "Programmable Logic Controller" Subparagraph below for multiple fuel-oil storage tanks and where system size and complexity justify.

          - Programmable Logic Controller:

            - Provide fully automatic operation of system.

            - Alarm on maximum 15 in. Hg (51 kPa) vacuum at pump suction indicating plugged filter.

            - Alarm on high water level in filter.

            - Alarm on leak in enclosure.

            - Touchscreen; with minimum 2-line, 20-character, illuminated digital display.

            - Display pressure differential across filter.

            - Display pressure differential across coalescer.

            - Controller strip heater with thermostat.

Fuel-quality analyzer is available from a limited number of manufacturers. Consult manufacturers to verify availability.

          - Fuel-Quality Analyzer: Continuously monitors fuel quality to detect and record particulate contamination and presence of water.

          - Interface with automatic control system is specified in Section 230923 "Direct Digital Control (DDC) System for HVAC" to control and indicate the following:

            - Start/stop system when required by schedule.

            - Operating status.

            - Alarm off-normal status.

If Project has more than one fuel-oil polishing system, delete "Pump Capacities and Characteristics" Paragraph below and schedule systems on Drawings.

        - Pump Capacities and Characteristics:

          - Capacity (Each Pump): [3 gpm (0.19 L/s)] [8 gpm (0.50 L/s)] [24 gpm (1.5 L/s)] <Insert value>.

Verify maximum pump suction lift with manufacturer.

          - Maximum Suction Lift: [15 ft. (4.6 m)] <Insert value>.

          - Inlet and Outlet Size: <Insert NPS (DN)>.

          - Motor Horsepower (Each Pump): <Insert value>.

          - Electrical Characteristics (Pump Set):

            - Volts: [120] [208] [240] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: 60.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

      - MOTORS

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

        - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings.

          - Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain subparagraphs below if options are available from equipment manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

          - Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

          - Motor Bearings: <Insert requirements>.

          - Unusual Service Conditions:

            - Ambient Temperature: <Insert deg C>.

            - Altitude: <Insert feet (m)> above sea level.

            - High humidity.

            - <Insert conditions>.

          - Efficiency: Premium efficient.

          - NEMA Design: <Insert designation>.

          - Service Factor: <Insert value>.

- EXECUTION

      - EXAMINATION

        - Examine roughing-in for fuel-oil pumps to verify actual locations of pump connections before equipment installation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - EARTHWORK

        - Comply with requirements in Section 312000 "Earth Moving" for excavating, trenching, and backfilling.

      - PREPARATION

Retain first paragraph below for renovations and additions.

        - Close equipment shutoff valves before turning off fuel oil to premises or piping section.

        - Comply with NFPA 30 and NFPA 31 requirements for prevention of accidental ignition.

      - INSTALLATION OF FUEL-OIL PUMPS

        - Submersible Fuel-Oil Storage Tank Pumps:

          - Suspend pumps from supply piping and anchor to bottom of tank.

        - Simplex and Multiplex Fuel-Oil Pumps:

          - Install pumps with access space for periodic maintenance including removal of motors, impellers, and accessories.

          - Set pumps on and anchor to concrete base.

          - Pump Mounting:

Retain first subparagraph below to require pumps to be installed on cast-in-place concrete equipment bases.

            - Install base-mounted pumps on cast-in-place concrete equipment bases. Comply with requirements for equipment bases and foundations specified in Section 033000 "Cast-in-Place Concrete."

Retain one of first two subparagraphs below if vibration isolation is required. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic control device type and minimum deflection in supported equipment schedule on Drawings.

            - Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

            - Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

Retain "Equipment Mounting" Subparagraph below for in-line pumps suspended from structure.

          - Equipment Mounting: Install in-line pumps with continuous-thread hanger rods and [elastomeric hangers] [spring hangers] [spring hangers with vertical-limit stop] of size required to support weight of in-line pumps.

Retain one of two subparagraphs below if vibration isolation is required. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

            - Comply with requirements for seismic-restraint devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

            - Comply with requirements for hangers and supports specified in Section 230529 "Hangers and Supports for HVAC Piping and Equipment."

        - Install two-piece, full-port ball valves at suction and discharge of pumps. Comply with requirements in Section 230523.12 "Ball Valves for HVAC Piping."

        - Install mechanical leak-detector valves at pump discharge.

        - Install [Y-pattern] [basket] [T-pattern] strainer on inlet side of all fuel-oil pumps.

        - Install check valve on discharge of all fuel-oil pumps unless provided with built-in check valve.

        - Install suction piping with minimum fittings and change of direction.

        - Install vacuum and pressure gauge, upstream and downstream, respectively, at each pump to measure the differential pressure across the pump. Pressure gauges are specified in Section 230519 "Meters and Gauges for HVAC Piping."

      - INSTALLATION OF FUEL-OIL POLISHING SYSTEMS

Retain this article for fuel-oil polishing system installation.

        - Polishing System Mounting:

Retain first subparagraph below to require system to be installed on cast-in-place concrete equipment bases.

          - Install equipment cabinet on cast-in-place concrete equipment base. Comply with requirements for equipment bases and foundations specified in Section 033000 "Cast-in-Place Concrete."

Retain one of two subparagraphs below if vibration isolation is required. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

          - Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

          - Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

        - Install suction line, with foot valve, at one end of storage tank, 1 inch (25 mm) from the bottom of tank.

        - Install return line at the opposite end of storage tank from suction line.

      - LABELING AND IDENTIFYING

        - Install nameplates and signs on each fuel-oil pump. Comply with requirements in Section 230553 "Identification for HVAC Piping and Equipment."

      - FIELD QUALITY CONTROL

Retain first option in "Testing Agency" Paragraph below if Owner hires an independent testing agency.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain "Manufacturer's Field Service" Paragraph below to require a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

        - Manufacturer's Field Service: Engage a factory-authorized service representative to [support] [supervise] field tests and inspections.

        - Tests and Inspections:

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

          - Start fuel-oil transfer pumps [and fuel-oil polishing system pumps ]to verify for proper operation of pump, and check for leaks.

          - Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

          - Fuel-oil pumps[ and fuel-oil polishing systems] will be considered defective if they do not pass tests and inspections.

        - Prepare test and inspection reports.

      - DEMONSTRATION

        - [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain [fuel-oil pumps] [ and fuel-oil polishing system] <Insert other>.

END OF SECTION 231213