Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 232113 - HYDRONIC PIPING

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Access Manufacturer-Provided, AIA MasterSpec-Based Sections:

<Double click here for this Section based on specific manufacturer’s products set as Basis-of-Design at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED 2009, LEED v4, LEED v4.1, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using the hypertext links.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Copper tube and fittings.

          - Steel pipe and fittings.

          - Stainless steel pipe and fittings.

          - Plastic pipe and fittings.

          - Fiberglass pipe and fittings.

          - Piping joining materials.

          - Transition fittings.

          - Dielectric fittings.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data: For each type of the following:

          - Pipe and tube.

          - Fittings.

          - Joining materials.

          - Transition fittings.

        - Sustainable Design Submittals:

          - <Double click to insert sustainable design text for adhesives.>

          - <Double click to insert sustainable design text for EPDs and HPDs.>

Retain "Delegated Design Submittals" Paragraph below if design services have been delegated to Contractor.

        - Delegated Design Submittals:

          - Design calculations and detailed fabrication and assembly of pipe anchors and alignment guides, hangers and supports for multiple pipes, expansion joints and loops, and attachments of the same to the building structure.

          - Locations of pipe anchors, alignment guides, and expansion joints and loops.

          - Locations of and details for penetrations, including sleeves and sleeve seals for exterior walls, floors, basement, and foundation walls.

          - Locations of and details for penetration and firestopping for fire- and smoke-rated wall and floor and ceiling assemblies.

      - INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Coordinate paragraph with other Sections specifying products listed below. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

        - Coordination Drawings: Piping layout, or BIM model, drawn to scale, indicating the items described in this Section, and coordinated with all building trades.

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Data: For Installer.

Retain "Welding certificates" Paragraph below if retaining "Steel Support Welding" or "Pipe Welding" Paragraph in "Quality Assurance" Article.

        - Welding certificates.

      - QUALITY ASSURANCE

        - Installer Qualifications:

Retain "Installers of Pressure-Sealed Joints" Subparagraph below for pressure-sealed joints in copper or steel piping.

          - Installers of Pressure-Sealed Joints: Installers are to be certified by pressure-seal joint manufacturer as having been trained and qualified to join piping with pressure-seal pipe couplings and fittings.

Retain "Fiberglass Pipe and Fitting Installers" Subparagraph below for fiberglass pipe assembly.

          - Fiberglass Pipe and Fitting Installers: Installers of RTRF and RTRP are to be certified by manufacturer of pipes and fittings as having been trained and qualified to join fiberglass piping with manufacturer-recommended adhesive.

Retain "Steel Support Welding" and "Pipe Welding" paragraphs below for welded supports or piping. Retain "Welding certificates" Paragraph in "Informational Submittals" Article if retaining below.

        - Steel Support Welding: Qualify procedures and personnel in accordance with AWS D1.1/D1.1M.

        - Pipe Welding: Qualify procedures and operators in accordance with ASME Boiler and Pressure Vessel Code: Section IX.

          - Comply with ASME B31.9 for materials, products, and installation.

          - Certify that each welder has passed AWS qualification tests for welding processes involved and that certification is current.

      - WARRANTY

Delete this article if polypropylene piping (PP-R or PP-RCT) product type is not retained.

When warranties are required and available, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws. Most manufacturers offer 10-year extended warranties on their equipment. Verify available warranties and warranty periods.

        - PP-R and PP-RCT Manufacturer's Warranty: Manufacturer agrees to repair or replace PP-R and PP-RCT pipe and fittings that fail in materials or workmanship within 10 years from date of Substantial Completion.

          - Warranty is to cover labor and material costs of repairing and/or replacing defective materials and repairing any incidental damage caused by failure of the piping system due to defects in materials or manufacturing.

          - Warranty is to be in effect only upon submission by Contractor to manufacturer of valid pressure/leak documentation indicating that the system was tested and passed manufacturer's pressure/leak test and any other manufacturer requirements.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - PERFORMANCE REQUIREMENTS

Performance requirements in this article are for the piping system. Individual components may have higher pressure or temperature ratings.

        - Hydronic piping components and installation are to be capable of withstanding the following minimum working pressures and temperatures unless otherwise indicated:

Pressures and temperatures below are provided for information only and should be inserted for each Project as the working pressures and temperatures are unique.

          - Hot-Water Heating Piping: [100 psig (689 kPa)] <Insert psig (kPa)> at [200 deg F (93 deg C)] [180 deg F (82 deg C)] <Insert temperature>.

          - Chilled-Water Piping: [150 psig (1034 kPa)] <Insert psig (kPa)> at [73 deg F (22 deg C)] <Insert temperature>.

          - Dual-Temperature Heating- and Cooling-Water Piping: [100 psig (1034 kPa)] <Insert psig (kPa)> at [180 deg F (82 deg C)] <Insert temperature>.

          - Condenser-Water Piping: [150 psig (1034 kPa)] <Insert psig (kPa)> at [73 deg F (66 deg C)] <Insert temperature>.

          - Glycol Cooling-Water Piping: [150 psig (1034 kPa)] <Insert psig (kPa)> at [150 deg F (66 deg C)] <Insert temperature>.

          - Makeup-Water Piping: [80 psig (552 kPa)] [150 psig (1034 kPa)] <Insert value> at [73 deg F (22 deg C)] [150 deg F (66 deg C)] <Insert temperature>.

          - Condensate-Drain Piping: [150 deg F (66 deg C)] [180 deg F (82 deg C)] <Insert temperature>.

          - Air-Vent Piping: [180 deg F (82 deg C)] [200 deg F (93 deg C)] <Insert temperature>.

          - Pressure-Relief-Valve-Inlet and -Outlet Piping: Equal to the pressure of the piping system to which it is attached.

      - COPPER TUBE AND FITTINGS

Tube in "Drawn-Temper Copper Tube" Paragraph below is generally available in NPS 1/8 to NPS 12 (DN 6 to DN 300). Drawn-temper copper tube is commonly referred to as "hard" copper tube.

        - Drawn-Temper Copper Tube: [ASTM B88, Type K (ASTM B88M, Type A)] [and] [ASTM B88, Type L (ASTM B88M, Type B)].

Tube in "Annealed-Temper Copper Tube" Paragraph below is generally available in NPS 1/8 to NPS 12 (DN 6 to DN 300). Annealed-temper copper tubing is commonly referred to as "soft" copper tube.

        - Annealed-Temper Copper Tube: [ASTM B88, Type K (ASTM B88M, Type A)] [and] [ASTM B88, Type L (ASTM B88M, Type B)].

        - DWV Copper Tube: ASTM B306, Type DWV.

Fittings in "Cast-Copper, Solder-Joint Fittings" Paragraph below are generally available in NPS 1/4 to NPS 12 (DN 8 to DN 300).

        - Cast-Copper, Solder-Joint Fittings: ASME B16.18 pressure fittings. Do not use solder joints on pipe sizes greater than NPS 4 (DN 100).

Fittings in "Wrought-Copper, Solder-Joint Fittings" Paragraph below are generally available in NPS 1/4 to NPS 8 (DN 8 to DN 200).

        - Wrought-Copper, Solder-Joint Fittings: ASME B16.22 pressure fittings. Do not use solder joints on pipe sizes greater than NPS 4 (DN 100).

Flanges in "Bronze Flanges" Paragraph below are generally available in NPS 1/2 to NPS 12 (DN 15 to DN 300).

        - Bronze Flanges: ASME B16.24, Class 150, with solder-joint ends. Do not use solder joints on pipe sizes greater than NPS 4 (DN 100).

Unions in "Cast-Copper Unions" Paragraph below are generally available in NPS 1/4 to NPS 4 (DN 8 to DN 100).

        - Cast-Copper Unions: MSS SP-123, cast-copper-alloy, hexagonal-stock body, with ball-and-socket, metal-to-metal seating surfaces and solder-joint or threaded ends. Do not use solder joints on pipe sizes greater than NPS 4 (DN 100).

Unions in "Wrought-Copper Unions" Paragraph below are generally available in NPS 1/4 to NPS 4 (DN 8 to DN 100).

        - Wrought-Copper Unions: ASME B16.22. Do not use solder joints on pipe sizes greater than NPS 4 (DN 100).

Retain "Copper-Tube, Mechanically Formed Tee Fitting" Paragraph below if formed tees can be used instead of tee fittings in copper tubing; delete if prohibited by authority having jurisdiction.

        - Copper-Tube, Mechanically Formed Tee Fitting: For forming T-branch on copper water tube.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Description: Tee formed in copper tube in accordance with ASTM F2014.

        - Grooved, Mechanical-Joint, Copper Tube Appurtenances:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain grooved mechanical-joint copper tube appurtenances from single manufacturer.

          - Grooved-End Copper Fittings: ASTM B75 (ASTM B75M) copper tube or ASTM B584 bronze castings.

          - Grooved-End-Tube Couplings: To fit copper-tube dimensions; rigid pattern unless otherwise indicated; gasketed fitting EPDM gasket rated for minimum [230 deg F (110 deg C)] <Insert temperature> for use with ferrous housing, and steel bolts and nuts; 300 psig (2060 kPa) minimum CWP pressure rating.

Fittings in "Copper-Tube, Pressure-Seal-Joint Fittings - Copper or Bronze" Paragraph below are generally available in NPS 1/2 to NPS 4 (DN 15 to DN 100), although some manufacturers provide them only up to NPS 2 (DN 25).

        - Copper-Tube, Pressure-Seal-Joint Fittings - Copper or Bronze:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain copper-tube pressure-seal-joint fittings from single manufacturer.

          - Housing: Copper or bronze.

          - O-Rings and Pipe Stops: EPDM.

          - Tools: Manufacturer's special tools.

          - Minimum 200 psig (1370 kPa) working pressure rating at 250 deg F (121 deg C).

      - STEEL PIPE AND FITTINGS

        - Steel Pipe: ASTM A53/A53M black steel with plain ends; welded and seamless, Grade B, and schedule number as indicated in Part 3,"Piping Applications" Article.

        - Cast-Iron Threaded Fittings: ASME B16.4; Classes 125 and 250 as indicated in Part 3, "Piping Applications" Article.

        - Malleable-Iron Threaded Fittings: ASME B16.3, Classes 150 and 300 as indicated in Part 3, "Piping Applications" Article.

        - Malleable-Iron Unions: ASME B16.39; Classes 150, 250, and 300 as indicated in Part 3, "Piping Applications" Article.

Coordinate flange class in "Cast-Iron Pipe Flanges and Flanged Fittings" Paragraph below with products in other parts of this Section and in related Sections to match face size and bolt patterns.

        - Cast-Iron Pipe Flanges and Flanged Fittings: ASME B16.1, Classes 25, 125, and 250; raised ground face, and bolt holes spot faced as indicated in "Piping Applications" Article.

        - Wrought-Steel Fittings: ASTM A234/A234M; wall thickness to match adjoining pipe.

        - Cast- and Forged-Steel Flanges and Flanged Fittings: ASME B16.5, including bolts, nuts, and gaskets of the following material group, end connections, and facings:

          - Material Group: 1.1.

          - End Connections: Butt welding.

          - Facings: Raised face.

        - Grooved Mechanical-Joint Fittings and Couplings:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain grooved mechanical-joint fittings and couplings from single manufacturer.

          - Joint Fittings: ASTM A536, Grade 65-45-12 ductile iron; ASTM A47/A47M, Grade 32510 malleable iron; ASTM A53/A53M, Type F, E, or S, Grade B fabricated steel; or ASTM A106/A106M, Grade B steel fittings with grooves or shoulders constructed to accept grooved-end couplings; with nuts, bolts, locking pin, locking toggle, or lugs to secure grooved pipe and fittings.

          - Couplings: Ductile- or malleable-iron housing and [EPDM] [or] [nitrile] gasket of central cavity pressure-responsive design; with nuts, bolts, locking pin, locking toggle, or lugs to secure grooved pipe and fittings.

        - Plain-End Mechanical-Joint Couplings:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain plain-end mechanical-joint couplings from single manufacturer.

          - Housing: ASTM A536, Grade 65-45-12 segmented ductile iron or Type 304 stainless steel.

          - Housing coating: [None] <Insert coating type>.

          - Gasket: [EPDM] [NBR].

          - Sealing Mechanism: Double-lip sealing system or carbon steel case-hardened jaws.

          - Bolts, hex nuts, washers, or lock bars based on manufacturer's design.

          - Minimum Pressure Rating: Equal to that of the joined pipes.

Nonreinforced, welded, in-branch connections weaken a main pipeline; reinforcement is necessary unless wall thickness of both mains and branches is sufficient to sustain pressure required in "Performance Requirements" Article.

        - Steel Pipe Nipples: ASTM A733, made of same materials and wall thicknesses as pipe in which they are installed.

      - STAINLESS STEEL PIPE AND FITTINGS

Pipe in "Stainless Steel Pipe, Plain Ends" Paragraph below is available in NPS 1/8 to NPS 30 (DN 6 to DN 750).

        - Stainless Steel Pipe, Plain Ends: ASTM A312/A312M plain ends, seamless; stainless steel of types and schedules as indicated in Part 3 "Piping Applications" Article.

        - Appurtenances for Grooved-End, Stainless Steel Pipe:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain appurtenances for grooved-end stainless steel pipe from single manufacturer.

          - Fittings for Grooved-End, Stainless Steel Pipe: Stainless steel casting with dimensions matching stainless steel pipe.

AWWA C606 covers couplings in NPS 3/4 to NPS 24 (DN 20 to DN 600) in "Mechanical Couplings for Grooved-End, Stainless Steel Pipe" Subparagraph below.

          - Mechanical Couplings for Grooved-End, Stainless Steel Pipe:

            - AWWA C606 for stainless steel pipe dimensions.

            - Stainless steel housing sections.

            - Stainless steel bolts and nuts.

            - EPDM gaskets suitable for hot and cold water.

            - Minimum Pressure Rating:

              - NPS 8 (DN 200) and Smaller: [600 psig (4137 kPa)] <Insert value>.

              - NPS 10 to NPS 12 (DN 250 to DN 300): [400 psig (2758 kPa)] <Insert value>.

              - NPS 14 to NPS 24 (DN 350 to DN 600): [250 psig (1725 kPa)] <Insert value>.

Fittings in "Stainless Steel Piping, Pressure-Seal-Joint Fittings" Paragraph below are generally available in NPS 1/2 to NPS 2 (DN 13 to DN 50).

        - Stainless Steel Piping, Pressure-Seal-Joint Fittings:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Obtain stainless steel piping pressure-seal-joint fittings from single manufacturer.

          - Material: ASTM A312/A312M, Type 316, stainless steel, Schedule 10.

          - Fittings: Type O-Rings and Pipe Stop: EPDM.

          - Tools: Manufacturer's special tool.

          - Minimum 300 psig (2070 kPa) working-pressure rating at 230 deg F (110 deg C).

      - PLASTIC PIPE AND FITTINGS

See the Evaluations for discussion of product characteristics and maximum temperatures.

Pipe in "CPVC Plastic Pipe" Paragraph below is available in NPS 1/4 to NPS 16 (DN 8 to DN 400).

        - CPVC Plastic Pipe: ASTM F441/F441M, with wall thickness as indicated in "Piping Applications" Article.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain CPVC plastic pipe from single manufacturer.

Fittings in "CPVC Socket Fittings" Subparagraph below are available in NPS 1/4 to NPS 6 (DN 8 to DN 150).

          - CPVC Socket Fittings: [ASTM F438 for Schedule 40] [and] [ASTM F439 for Schedule 80].

Fittings in "CPVC Threaded Fittings" Subparagraph below are available in NPS 1/4 to NPS 6 (DN 8 to DN 150).

          - CPVC Threaded Fittings: ASTM F437, Schedule 80.

Piping in "CPVC Piping System" Subparagraph below is available in NPS 1-1/2 and NPS 2 (DN 40 and DN 50).

          - CPVC Piping System: ASTM D2846/D2846M, SDR, pipe and socket fittings.

Tubing in "CPVC Tubing System" Subparagraph below is available in NPS 1/4 to NPS 2 (DN 8 to DN 50).

          - CPVC Tubing System: ASTM D2846/D2846M, SDR, tube and socket fittings.

Piping in "PVC Plastic Pipe" Paragraph below is available in NPS 1/2 to NPS 16 (DN 13 to DN 400).

        - PVC Plastic Pipe: ASTM D1785, with wall thickness as indicated in "Piping Applications" Article.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain PVC plastic pipe from single manufacturer.

Fittings in "PVC Socket Fittings" Subparagraph below are available in NPS 1/8 to NPS 12 (DN 6 to DN 300).

          - PVC Socket Fittings: [ASTM D2466 for Schedule 40] [and] [ASTM D2467 for Schedule 80].

Fittings in "PVC Schedule 80 Threaded Fittings" Subparagraph below are available in NPS 1/8 to NPS 6 (DN 6 to DN 150).

          - PVC Schedule 80 Threaded Fittings: ASTM D2464.

Pipe in "Polypropylene (PP-R and PP-RCT) Pipe" Paragraph below is generally available in nominal 1/2-inch to nominal 24-inch diameter (20-mm actual OD to 630-mm actual OD).

        - Polypropylene (PP-R and PP-RCT) Pipe:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain polypropylene (PP-R and PP-RCT) pipe from single manufacturer.

          - Description: ASTM F2389; pipe pressure rating to comply with temperature and pressure ratings of code requirements for the applicable service.

            - Polypropylene Fittings: ASTM F2389, socket fusion, butt fusion, electrofusion, or fusion outlet fittings to be used for fusion-welded joints between pipe and fittings.

            - Mechanical fittings and transition fittings to be used where transitions are made to other piping materials or to valves and appurtenances.

            - Polypropylene pipe is to be unthreaded. Threaded transition fittings in accordance with ASTM F2389 to be used where a threaded connection is required.

Retain "Smoke and Fire Ratings" Paragraph below when plenum-rated PP-R and PP-RCT piping systems are required.

        - Smoke and Fire Ratings:

          - Where indicated on Drawings that a plenum-rated piping system is required, the pipe is to be wrapped and/or insulated with fiberglass or mineral wool pipe insulation; field installed.

            - The system is to have a flame-spread classification of less than 25 and smoke-developed rating of less than 50.

            - Pipe, wrap, or insulation as a system to comply with the requirements of CAN/ULC-S102.2, ASTM E84, or UL 2846.

            - For insulation required for thermal and condensation conditions, see Section 230719 "HVAC Piping Insulation."

      - FIBERGLASS PIPE AND FITTINGS

Fiberglass pipe and fittings are not listed in Ch. 46, "Pipes, Tubes, and Fittings," of the 2016 ASHRAE HVAC Systems and Equipment Handbook.

Piping is available with ends for other types of joints. See the Evaluations for discussion of product characteristics and maximum temperatures and pressures.

        - RTRP: ASTM D2996, filament-wound pipe with tapered bell and spigot ends for adhesive joints.

        - RTRF: Compression or spray-up/contact molded of same material, pressure class, and joining method as pipe.

        - Flanges: ASTM D4024; full-face gaskets suitable for the service, minimum 1/8-inch (3.2-mm) thick, 60-70 durometer. Provide ASTM A307, Grade B, hex head bolts with washers.

      - PIPING JOINING MATERIALS

        - Pipe-Flange Gasket Materials: Suitable for chemical and thermal conditions of piping system contents.

          - ASME B16.21, nonmetallic, flat, asbestos free, 1/8-inch (3.2-mm) maximum thickness unless otherwise indicated.

            - Full-Face Type: For flat-face, Class 125, cast-iron and cast-bronze flanges.

            - Narrow-Face Type: For raised-face, Class 250, cast-iron and steel flanges.

        - Flange Bolts and Nuts: ASME B18.2.1, carbon steel, unless otherwise indicated.

        - Plastic, Pipe-Flange Gasket, Bolts, and Nuts: Type and material recommended by piping system manufacturer unless otherwise indicated.

See the Evaluations for discussions of solder and brazing materials described in "Solder Filler Metals" and "Brazing Filler Metals" paragraphs below.

        - Solder Filler Metals: ASTM B32, lead-free alloys.

        - Flux: ASTM B813, water flushable.

        - Brazing Filler Metals: AWS A5.8/A5.8M, BCuP Series, copper-phosphorus alloys for joining copper with copper; or BAg-1, silver alloy for joining copper with bronze or steel.

        - Welding Filler Metals: Comply with AWS D10.12M/D10.12 for welding materials appropriate for wall thickness and chemical analysis of steel pipe being welded.

        - Solvent Cements for CPVC Piping: ASTM F493.

          - <Double click to insert sustainable design text for solvent cement.>

          - <Double click to insert sustainable design text for low emitting adhesives.>

        - Solvent Cements for PVC Piping: ASTM D2564. Include primer in accordance with ASTM F656.

          - <Double click to insert sustainable design text for solvent cement.>

          - <Double click to insert sustainable design text for adhesive primer.>

          - <Double click to insert sustainable design text for low emitting adhesives.>

          - <Double click to insert sustainable design text for adhesive primer.>

        - Fiberglass Pipe Adhesive: As furnished or recommended by pipe manufacturer.

          - <Double click to insert sustainable design text for fiberglass pipe adhesive.>

          - <Double click to insert sustainable design text for low emitting adhesives.>

      - TRANSITION FITTINGS

        - General Requirements:

          - Same size as pipes to be joined.

          - Pressure rating at least equal to pipes to be joined.

          - End connections compatible with pipes to be joined.

        - Fitting-Type Transition Couplings: Manufactured piping coupling or specified piping system fitting.

Fittings in "Plastic-to-Metal Transition Fittings" Paragraph below are available in at least NPS 1/2 to NPS 2 (DN 15 to DN 50).

        - Plastic-to-Metal Transition Fittings:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain plastic-to-metal transition fittings from single manufacturer.

          - Description:

            - [CPVC] [or] [PVC] one-piece fitting with manufacturer's Schedule 80 equivalent dimensions.

            - One end with threaded brass insert and one solvent-cement-socket[ or threaded] end.

          - One-piece fitting with one threaded brass or copper insert and one solvent-cement-joint end of material and wall thickness to match plastic pipe material.

        - Plastic-to-Metal Transition Unions:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain plastic-to-metal transition unions from single manufacturer.

          - Brass or copper end and solvent-cement-joint end of union to match pipe in size and material.

          - Description:

            - [CPVC] [or] [PVC] four-part union.

            - Brass[ or stainless steel] threaded end.

            - Solvent-cement-joint[ or threaded] plastic end.

            - Rubber O-ring.

            - Union nut.

      - DIELECTRIC FITTINGS

        - General Requirements: Assembly of copper alloy and ferrous materials with separating nonconductive insulating material. Include end connections compatible with pipes to be joined.

Fittings in "Dielectric Unions" Paragraph below are available in NPS 1/2 to NPS 2 (DN 15 to DN 50).

        - Dielectric Unions:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain dielectric unions from single manufacturer.

          - Description:

            - Standard: ASSE 1079.

Revise pressure rating in "Pressure Rating" Subparagraph below to suit Project, or insert other options for specific applications.

            - Pressure Rating: [125 psig (860 kPa) minimum at 180 deg F (82 deg C)] [150 psig (1035 kPa)] [250 psig (1725 kPa)] <Insert value>.

            - End Connections: Solder-joint copper alloy and threaded ferrous. Solder joints are not to be used on pipe sizes greater than NPS 4 (DN 100).

Fittings in "Dielectric Flanges" Paragraph below are available in NPS 1-1/2 to NPS 4 (DN 40 to DN 100).

        - Dielectric Flanges:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain dielectric flanges from single manufacturer.

          - Description:

            - Standard: ASSE 1079.

            - Factory-fabricated, bolted, companion-flange assembly.

Revise pressure rating in "Pressure Rating" Subparagraph below to suit Project, or insert other options for specific applications.

            - Pressure Rating: [125 psig (860 kPa) minimum at 180 deg F (82 deg C)] [150 psig (1035 kPa)] [175 psig (1200 kPa)] [300 psig (2070 kPa)] <Insert value>.

            - End Connections: Solder-joint copper alloy and threaded ferrous; threaded solder-joint copper alloy and threaded ferrous.

Flanges in "Dielectric-Flange Insulating Kits" Paragraph below are available in NPS 1/2 to NPS 48 (DN 15 to DN 1200).

        - Dielectric-Flange Insulating Kits:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain dielectric-flange insulating kits from single manufacturer.

          - Description:

            - Nonconducting materials for field assembly of companion flanges.

Revise pressure rating in "Pressure Rating" Subparagraph below to suit Project, or insert other options for specific applications.

            - Pressure Rating: [150 psig (1035 kPa)] <Insert value>.

            - Gasket: Neoprene or phenolic.

            - Bolt Sleeves: Phenolic or polyethylene.

            - Washers: Phenolic with steel backing washers.

Nipples in "Dielectric Nipples" Paragraph below are available in NPS 1/2 to NPS 4 (DN 15 to DN 100).

        - Dielectric Nipples:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain dielectric nipples from single manufacturer.

          - Description:

            - Standard: IAPMO PS 66.

            - Electroplated steel nipple, complying with ASTM F1545.

Revise pressure rating and temperature in "Pressure Rating" Subparagraph below to suit Project, or insert other options for specific applications.

            - Pressure Rating: Minimum [300 psig (2070 kPa) at 225 deg F (107 deg C)] <Insert value and temperature>.

            - End Connections: Male threaded or grooved.

            - Lining: Inert and noncorrosive, propylene.

- EXECUTION

      - PIPING APPLICATIONS

This article is organized to first present the service and pipe size or size range, and then to present optional piping materials and joining methods. Retain the services and sizes and size ranges applicable to Project; then retain the selected piping materials and joining methods. Coordinate selection of piping materials and joining methods with piping materials described in Part 2.

        - Hot-Water Heating Piping, Aboveground, NPS 2 (DN 50) and Smaller, to Be Any of the Following:

Retain one or more of six subparagraphs below.

          - [Type K (Type A)] [Type L (Type B)] <Insert type>, drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] [pressure-seal] [grooved mechanical] [mechanically formed tee] joints.

          - [Schedule 40] <Insert schedule number>, Grade B, steel pipe; [Class 125, cast-iron] [Class 150, malleable-iron] [Class 250, cast-iron] [Class 300, malleable-iron] fittings; and [threaded] [grooved mechanical] joints.

          - Schedule 5, [Type 304] <Insert type>, stainless steel pipe; [Type 316] <Insert type>, stainless steel pressure-seal fittings; and pressure-seal joints.

          - [Schedule 10] [Schedule 40] <Insert schedule number>, [Type 304] <Insert type>, stainless steel pipe; [Type 304] <Insert type>, grooved mechanical joint coupling and fittings; and grooved mechanical joints.

Piping materials in subparagraphs below have temperature and pressure limitations. See the Evaluations.

          - [Schedule 40] <Insert schedule number>, CPVC plastic pipe and fittings and solvent-welded joints.

          - RTRP and RTRF with adhesive joints.

        - Hot-Water Heating Piping, Aboveground, NPS 2-1/2 (DN 65) and Larger, to Be Any of the Following:

Retain one or more of first five subparagraphs below.

          - [Type K (Type A)] [Type L (Type B)] <Insert type>, drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] [grooved mechanical] joints.

          - [Schedule 40] <Insert schedule number>, Grade B, steel pipe; [Class 125, cast-iron] [Class 150, malleable-iron] [Class 250 cast-iron] [Class 300 malleable-iron] fittings; welded joints, cast-iron flanges, flange-fittings, and flanged joints.

          - [Schedule 40] <Insert schedule number>, Grade B, steel pipe; grooved mechanical joint coupling and fittings; and grooved mechanical joints.

          - [Schedule 40] <Insert schedule number>, Grade B, steel pipe, plain-end mechanical joint couplings and fittings; and plain-end mechanical joints.

          - [Schedule 10] [Schedule 40] <Insert schedule number>, [Type 304] <Insert type>, stainless steel pipe; [Type 304] <Insert type>, grooved mechanical joint coupling and fittings; and grooved mechanical joints.

Piping materials in subparagraphs below have temperature and pressure limitations. See the Evaluations.

          - [Schedule 40] <Insert schedule number>, CPVC plastic pipe and fittings and solvent-welded joints.

          - RTRP and RTRF with adhesive or flanged joints.

        - Chilled-Water Piping, Aboveground, NPS 2 (DN 50) and Smaller, to be Any of the Following:

Retain one or more of first four subparagraphs below.

          - [Type K (Type A)] [Type L (Type B)] <Insert type>, drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] [pressure-seal] [grooved mechanical] [mechanically formed tee] joints.

          - [Schedule 40] <Insert schedule number>, Grade B steel pipe; [Class 125, cast-iron] [Class 150, malleable-iron] [Class 250, cast-iron] [Class 300, malleable-iron] fittings; and [threaded] [grooved mechanical] joints.

          - Schedule 5, [Type 304] <Insert type>, stainless steel pipe; [Type 316] <Insert type>, stainless steel pressure-seal fittings; and pressure-seal joints.

          - [Schedule 10] [Schedule 40] <Insert schedule number>, [Type 304] <Insert type>, stainless steel pipe; [Type 304] <Insert type>, grooved mechanical joint coupling and fittings; and grooved mechanical joints.

Piping materials in subparagraphs below have temperature and pressure limitations. See the Evaluations.

          - [Schedule 40] <Insert schedule number>, CPVC plastic pipe and fittings and solvent-welded joints.

          - [PP-R] [PP-RCP] plastic piping and fittings with heat fusion joints.

          - RTRP and RTRF with adhesive or flanged joints.

        - Chilled-Water Piping, Aboveground, NPS 2-1/2 (DN 65) and Larger, to Be Any of the Following:

Retain one or more of eight subparagraphs below.

          - [Type K (Type A)] [Type L (Type B)] <Insert type>, drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] [grooved mechanical] joints.

          - [Schedule 40] <Insert schedule number>, Grade B, steel pipe, wrought-steel fittings and wrought-cast or forged-steel flanges and flange fittings, and welded and flanged joints.

          - [Schedule 40] <Insert schedule number>, Grade B, steel pipe; grooved mechanical joint coupling and fittings; and grooved mechanical joints.

          - [Schedule 40] <Insert schedule number>, Grade B, steel pipe, plain-end mechanical joint coupling and fittings; and plain-end mechanical joints.

          - [Schedule 10] [Schedule 40] <Insert schedule number>, [Type 304] <Insert type>, stainless steel pipe; [Type 304] <Insert type>, grooved mechanical joint coupling and fittings; and grooved, mechanical joints.

Piping materials in subparagraphs below have temperature and pressure limitations. See the Evaluations.

          - [Schedule 40] <Insert schedule number>, CPVC plastic pipe and fittings and solvent-welded joints.

          - RTRP and RTRF with adhesive or flanged joints.

          - [PP-R] [PP-RCP] plastic piping and fittings with heat fusion joints.

        - Dual-Temperature Heating- and Cooling-Water Piping, Aboveground, NPS 2 (DN 50) and Smaller, to Be Any of the Following:

Retain one or more of seven subparagraphs below.

          - [Type K (Type A)] [Type L (Type B)] <Insert type>, drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] [pressure-seal] [grooved mechanical] [mechanically formed tee] joints.

          - [Schedule 40] <Insert schedule number>, Grade B steel pipe; [Class 125, cast-iron] [Class 150, malleable-iron] [Class 250, cast-iron] [Class 300, malleable-iron] fittings; and [threaded] [grooved mechanical] joints.

          - Schedule 5, [Type 304] <Insert type>, stainless steel pipe; [Type 316] <Insert Type> stainless steel pressure-seal couplings and fittings; and pressure-seal joints.

          - [Schedule 10] [Schedule 40] <Insert schedule number>, [Type 304] <Insert type>, stainless steel pipe; [Type 304] <Insert type>, grooved mechanical joint coupling and fittings; and grooved mechanical joints.

Piping materials in subparagraphs below have temperature and pressure limitations. See the Evaluations.

          - [Schedule 40] <Insert schedule number>, CPVC plastic pipe and fittings and solvent-welded joints.

          - [PP-R] [PP-RCP] plastic piping and fittings with heat fusion joints.

          - RTRP and RTRF with adhesive or flanged joints.

        - Dual-Temperature Heating and Cooling-Water Piping, Aboveground, NPS 2-1/2 (DN 65) and Larger, to Be Any of the Following:

Retain one or more of seven subparagraphs below.

          - [Type K (Type A)] [Type L (Type B)] <Insert type>, drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] [grooved mechanical] joints.

          - [Schedule 40] <Insert schedule number>, Grade B steel pipe, [Class 125, cast-iron] [Class 150, malleable-iron] [Class 250 cast-iron] [Class 300 malleable-iron] fittings; welded joints, cast-iron flanges and flange-fittings; and flanged joints.

          - [Schedule 40] <Insert schedule number>, Grade B steel pipe; grooved mechanical joint coupling and fittings; and grooved mechanical joints.

          - [Schedule 40] <Insert schedule number>, steel pipe, plain-end mechanical joint couplings and fittings; and plain-end mechanical joints.

          - [Schedule 10] [Schedule 40] <Insert schedule number>, [Type 304] <Insert type>, stainless steel pipe; [Type 304] <Insert type>, grooved mechanical joint coupling and fittings; and grooved mechanical joints.

Piping materials in subparagraphs below have temperature and pressure limitations. See the Evaluations.

          - [Schedule 40] <Insert schedule number>, CPVC plastic pipe and fittings and solvent-welded joints.

          - RTRP and RTRF with adhesive or flanged joints.

        - Condenser-Water Piping, Aboveground, NPS 2 (DN 50) and Smaller, to Be Any of the Following:

Retain one or more of first four subparagraphs below.

          - [Type K (Type A)] [Type L (Type B)] <Insert type>, drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] [pressure-seal] [grooved mechanical] [mechanically formed tee] joints.

          - [Schedule 40] <Insert schedule number>, Grade B, steel pipe; [Class 125, cast-iron] [Class 150, malleable-iron] [Class 250 cast-iron] [Class 300 malleable-iron], fittings; and [threaded] [grooved mechanical] joints.

          - Schedule 5, [Type 304] <Insert type>, stainless steel pipe; [Type 316] <Insert type>, stainless steel pressure-seal couplings and fittings; and pressure-seal joints.

          - [Schedule 10] [Schedule 40] <Insert schedule number>, [Type 304] <Insert type>, stainless steel pipe; [Type 304] <Insert type>, grooved mechanical joint coupling and fittings; and grooved mechanical joints.

Piping materials in subparagraphs below have temperature and pressure limitations. See the Evaluations.

          - [Schedule 40] <Insert schedule number>, CPVC plastic pipe and fittings and solvent-welded joints.

          - [PP-R] [PP-RCP] plastic piping and fittings with heat fusion joints.

          - RTRP and RTRF with adhesive joints.

        - Condenser-Water Piping, Aboveground, NPS 2-1/2 (DN 65) and Larger, to Be Any of the Following:

Retain one or more of first five subparagraphs below.

          - [Type K (Type A)] [Type L (Type B)] <Insert type>, drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] [grooved mechanical] joints.

          - [Schedule 40] <Insert schedule number>, Grade B, steel pipe, [Class 125, cast-iron] [Class 150, malleable-iron] [Class 250 cast-iron] [Class 300 malleable-iron] fittings; welded joints, cast-iron flanges and flange-fittings; and flanged joints.

          - [Schedule 40] <Insert schedule number>, Grade B, steel pipe; grooved, mechanical joint coupling and fittings; and grooved mechanical joints.

          - [Schedule 40] <Insert schedule number>, steel pipe, plain-end mechanical joint coupling and fittings; and plain-end mechanical joints.

          - [Schedule 10] [Schedule 40] <Insert schedule number>, [Type 304] <Insert type>, stainless steel pipe; [Type 304] <Insert type>, grooved mechanical joint coupling and fittings; and grooved mechanical joints.

Piping materials in subparagraphs below have temperature and pressure limitations. See the Evaluations.

          - [Schedule 40] <Insert schedule number>, CPVC plastic pipe and fittings and solvent-welded joints.

          - RTRP and RTRF with adhesive or flanged joints.

          - [PP-R] [PP-RCP] piping and fittings with heat fusion joints.

        - Glycol Cooling-Water Piping, Aboveground, NPS 2 (DN 50) and Smaller, to Be Any of the Following:

Retain one or more of first four subparagraphs below.

          - [Type K (Type A)] [Type L (Type B)] <Insert type>, drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] [pressure-seal] [grooved mechanical] [mechanically formed tee] joints.

          - [Schedule 40] <Insert schedule number>, steel pipe; [Class 125, cast-iron] [Class 150, malleable-iron] [Class 250, cast-iron] [Class 300, malleable-iron] fittings; and threaded joints.

          - Schedule 5, [Type 304] <Insert type>, stainless steel pipe; [Type 316] <Insert type>, stainless steel pressure-seal couplings and fittings; and pressure-seal joints.

          - [Schedule 10] [Schedule 40] <Insert schedule number>, [Type 304] <Insert type>, stainless steel pipe; [Type 304] <Insert type>, grooved mechanical joint coupling and fittings; and grooved mechanical joints.

Piping material subparagraphs below have temperature and pressure limitations. See the Evaluations.

          - [Schedule 40] <Insert schedule number>, CPVC plastic pipe and fittings and solvent-welded joints.

          - [PP-R] [PP-RCP] plastic piping and fittings with heat fusion joints.

          - RTRP and RTRF with adhesive or flanged joints.

        - Glycol Cooling-Water Piping, Aboveground, NPS 2-1/2 (DN 65) and Larger, to Be Any of the Following:

Retain one or more of first five subparagraphs below.

          - [Type K (Type A)] [Type L (Type B)] <Insert type>, drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] [grooved mechanical] joints.

          - [Schedule 40] <Insert schedule number>, Grade B, steel pipe, wrought-steel fittings and wrought-cast or forged-steel flanges and flange fittings, and welded and flanged joints.

          - [Schedule 40] <Insert schedule number>, Grade B, steel pipe; grooved, mechanical joint coupling and fittings; and grooved mechanical joints.

          - [Schedule 40] <Insert schedule number>, Grade B, steel pipe, plain-end mechanical joint coupling and fittings; and plain-end mechanical joints.

          - [Schedule 10] [Schedule 40] <Insert schedule number>, [Type 304] <Insert type>, stainless steel pipe; [Type 304] <Insert type>, grooved mechanical joint coupling and fittings; and grooved mechanical joints.

Piping materials in subparagraphs below have temperature and pressure limitations. See the Evaluations.

          - [Schedule 40] <Insert schedule number>, CPVC plastic pipe and fittings and solvent-welded joints.

          - RTRP and RTRF with adhesive or flanged joints.

          - [PP-R] [PP-RCP] plastic piping and fittings with heat fusion joints.

        - Makeup-Water Piping Installed Aboveground to Be Any of the Following:

Retain one or more six subparagraphs below.

          - [Type K (Type A)] [Type L (Type B)] <Insert type>, drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] [pressure-seal] [mechanical grooved] [mechanically formed tee] joints.

          - [Schedule 40] <Insert schedule number>, CPVC plastic pipe and fittings, and solvent-welded joints.

          - Schedule 5, [Type 304] <Insert type>, stainless steel pipe; [Type 316] <Insert type>, stainless steel pressure-seal couplings and fittings; and pressure-seal joints.

          - [Schedule 10] [Schedule 40] <Insert schedule number>, [Type 304] <Insert type>, stainless steel pipe; [Type 304] <Insert type>, grooved mechanical joint coupling and fittings; and grooved mechanical joints.

          - [PP-R] [PP-RCP] plastic piping and fittings with heat fusion joints.

          - RTRP and RTRF with adhesive joints.

        - Condensate-Drain Piping Installed Aboveground to Be Any of the Following:

Retain one or both of first two subparagraphs below.

          - [Type K (Type A)] [Type L (Type B)] [Type DWV] <Insert type>, drawn-temper copper tubing, wrought-copper fittings, and [soldered] [brazed] [pressure-seal] [grooved mechanical] [mechanically formed tee] joints.

          - [Schedule 40] <Insert schedule number>, PVC plastic pipe and fittings and solvent-welded joints.

          - Schedule 5, [Type 304] <Insert type>, stainless steel pipe; [Type 316] <Insert type>, stainless steel pressure-seal couplings and fittings; and pressure-seal joints.

          - [PP-R] [PP-RCP] plastic piping and fittings with heat fusion joints.

        - Air-Vent Piping:

          - Inlet: Same as service where installed with metal-to-plastic transition fittings for plastic piping systems, according to piping manufacturer's written instructions.

          - Outlet: Type K (Type A), annealed-temper copper tubing with soldered or flared joints.

        - Pressure-Relief-Valve-Inlet and -Outlet Piping for Hot-Water Piping: Same materials and joining methods as for piping specified for the service in which safety valve is installed, with metal-to-plastic transition fittings for plastic piping systems, according to piping manufacturer's written instructions.

      - INSTALLATION OF PIPING

Coordinate piping installations and specialty arrangements with Drawings. If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Drawing plans, schematics, and diagrams indicate general location and arrangement of piping systems. Indicated locations and arrangements are used to size pipe and calculate friction loss, expansion, and other design considerations. Install piping as indicated unless deviations to layout are approved on coordination drawings.

        - Install piping in concealed locations unless otherwise indicated and except in equipment rooms and service areas.

        - Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls. Diagonal runs are prohibited unless specifically indicated otherwise.

        - Install piping above accessible ceilings to allow sufficient space for ceiling panel removal.

        - Install piping to permit valve servicing.

        - Install piping at indicated slopes.

        - Install piping free of sags and bends.

        - Install fittings for changes in direction and branch connections.

        - Install piping to allow application of insulation.

        - Select system components with pressure rating equal to or greater than system operating pressure.

        - Install groups of pipes parallel to each other, spaced to permit applying insulation and servicing of valves.

        - Install drains, consisting of a tee fitting, NPS 3/4 (DN 20) ball valve, and short NPS 3/4 (DN 20) threaded nipple with cap, at low points in piping system mains and elsewhere as required for system drainage.

        - Install piping at a uniform grade of 0.2 percent upward in direction of flow.

        - Reduce pipe sizes using eccentric reducer fitting installed with level side up.

        - Install branch connections to mains using [mechanically formed ]tee fittings in main pipe, with the branch connected to the bottom of the main pipe. For up-feed risers, connect the branch to the top of the main pipe.

        - Install valves according to the following:

          - Section 230523.11 "Globe Valves for HVAC Piping."

          - Section 230523.12 "Ball Valves for HVAC Piping."

          - Section 230523.13 "Butterfly Valves for HVAC Piping."

          - Section 230523.14 "Check Valves for HVAC Piping."

          - Section 230523.15 "Gate Valves for HVAC Piping."

        - Install air vents and pressure-relief valves in accordance with Section 232116 "Hydronic Piping Specialties."

        - Install unions in piping, [NPS 2 (DN 50)] <Insert pipe size> and smaller, adjacent to valves, at final connections of equipment, and elsewhere as indicated.

        - Install flanges in piping, [NPS 2-1/2 (DN 65)] <Insert pipe size> and larger, at final connections of equipment and elsewhere as indicated.

        - Install shutoff valve immediately upstream of each dielectric fitting.

        - Comply with requirements in Section 230516 "Expansion Fittings and Loops for HVAC Piping" for installation of expansion loops, expansion joints, anchors, and pipe alignment guides.

        - Comply with requirements in Section 230553 "Identification for HVAC Piping and Equipment" for identifying piping.

        - Install sleeves for piping penetrations of walls, ceilings, and floors. Comply with requirements for sleeves specified in Section 230517 "Sleeves and Sleeve Seals for HVAC Piping."

Retain first paragraph below for piping that penetrates an exterior concrete wall or concrete slab.

        - Install sleeve seals for piping penetrations of concrete walls and slabs. Comply with requirements for sleeve seals specified in Section 230517 "Sleeves and Sleeve Seals for HVAC Piping."

        - Install escutcheons for piping penetrations of walls, ceilings, and floors. Comply with requirements for escutcheons specified in Section 230518 "Escutcheons for HVAC Piping."

      - JOINT CONSTRUCTION

        - Ream ends of pipes and tubes and remove burrs. Bevel plain ends of steel pipe.

        - Remove scale, slag, dirt, and debris from inside and outside of pipe and fittings before assembly.

        - Soldered Joints: Apply ASTM B813, water-flushable flux, unless otherwise indicated, to tube end. Construct joints in accordance with ASTM B828 or CDA's "Copper Tube Handbook," using lead-free solder alloy complying with ASTM B32.

        - Brazed Joints: Construct joints in accordance with AWS's "Brazing Handbook," "Pipe and Tube" chapter, using copper-phosphorus brazing filler metal complying with AWS A5.8/A5.8M.

        - Threaded Joints: Thread pipe with tapered pipe threads in accordance with ASME B1.20.1. Cut threads full and clean using sharp dies. Ream threaded pipe ends to remove burrs and restore full ID. Join pipe fittings and valves as follows:

          - Apply appropriate tape or thread compound to external pipe threads unless dry seal threading is specified.

          - Damaged Threads: Do not use pipe or pipe fittings with threads that are corroded or damaged. Do not use pipe sections that have cracked or open welds.

        - Welded Joints: Construct joints in accordance with AWS D10.12M/D10.12, using qualified processes and welding operators in accordance with "Quality Assurance" Article.

        - Flanged Joints: Select appropriate gasket material, size, type, and thickness for service application. Install gasket concentrically positioned. Use suitable lubricants on bolt threads.

        - Plastic Piping Solvent-Cemented Joints: Clean and dry joining surfaces. Join pipe and fittings in accordance with the following:

          - Comply with ASTM F402 for safe-handling practice of cleaners, primers, and solvent cements.

          - CPVC Piping: Join in accordance with ASTM D2846/D2846M Appendix.

          - PVC Pressure Piping: Join ASTM D1785 schedule number, PVC pipe, and PVC socket fittings in accordance with ASTM D2672. Join other-than-schedule-number PVC pipe and socket fittings in accordance with ASTM D2855.

          - PVC Nonpressure Piping: Join in accordance with ASTM D2855.

        - Fiberglass-Bonded Joints: Prepare pipe ends and fittings, apply adhesive, and join according to pipe manufacturer's written instructions.

Retain "Grooved Joints" Paragraph below for grooved-end pipe couplings for copper or steel pipe.

        - Grooved Joints: Assemble joints with coupling and gasket, lubricant, and bolts. Cut or roll grooves in ends of pipe based on pipe and coupling manufacturer's written instructions for pipe wall thickness. Use grooved-end fittings and rigid, grooved-end-pipe couplings.

Retain "Plain-End Mechanical-Coupled Joints" Paragraph below for plain-end mechanical-coupled steel pipes.

        - Plain-End Mechanical-Coupled Joints: Prepare, assemble, and test joints in accordance with manufacturer's written installation instructions.

Retain "Mechanically Formed Tee Fittings" Paragraph below for mechanically formed outlets in place of tee fittings in copper pipe.

        - Mechanically Formed Tee Fittings: Use manufacturer-recommended tools, procedure, and brazed joints.

Retain "Pressure-Seal Joints" Paragraph below for pressure-sealed joints in copper or steel piping.

        - Pressure-Seal Joints: Use manufacturer-recommended tools and procedure. Leave insertion marks on pipe after assembly.

      - INSTALLATION OF DIELECTRIC FITTINGS

        - Install dielectric fittings in piping at connections of dissimilar metal piping and tubing.

        - Dielectric Fittings for NPS 2 (DN 50) and Smaller: Use dielectric [nipples] [unions].

        - Dielectric Fittings for NPS 2-1/2 to NPS 4 (DN 65 to DN 100): Use dielectric [flanges] [flange kits] [nipples].

        - Dielectric Fittings for NPS 5 (DN 125) and Larger: Use dielectric flange kits.

      - INSTALLATION OF HANGERS AND SUPPORTS

Retain first paragraph below for projects in areas that require seismic restraints.

        - Comply with requirements for seismic-restraint devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

        - Comply with requirements in Section 230529 "Hangers and Supports for HVAC Piping and Equipment" for hangers, supports, and anchor devices.

        - Install hangers for [copper tubing] [and] [steel piping], with maximum horizontal spacing and minimum rod diameters, to comply with MSS SP-58, locally enforced codes, and authorities having jurisdiction requirements, whichever are most stringent.

        - Install hangers for plastic piping, with maximum horizontal spacing and minimum rod diameters, to comply with manufacturer's written instructions, locally enforced codes, and authorities having jurisdiction requirements, whichever are most stringent.

        - Install hangers for fiberglass piping, with maximum horizontal spacing and minimum rod diameters, to comply with manufacturer's written instructions, locally enforced codes, and authorities having jurisdiction requirements, whichever are most stringent.

        - Support horizontal piping within [12 inches (300 mm)] <Insert dimension> of each fitting and coupling.

        - Support vertical runs of [copper tubing] [and] [steel piping] to comply with MSS SP-58, locally enforced codes, and authorities having jurisdiction requirements, whichever are most stringent.

        - Support vertical runs of [CPVC] [PVC] [PP-R] [and] [PP-RCP] piping to comply with manufacturer's written instructions, locally enforced codes, and authorities having jurisdiction requirements, whichever are most stringent.

        - Support vertical runs of fiberglass piping to comply with manufacturer's written instructions, locally enforced codes, and authorities having jurisdiction requirements, whichever are most stringent.

      - TERMINAL EQUIPMENT CONNECTIONS

        - Sizes for supply and return piping connections are to be the same as or larger than equipment connections.

        - Install control valves in accessible locations close to connected equipment.

        - Install bypass piping with globe valve around control valve. If parallel control valves are installed, only one bypass is required.

        - Install ports for pressure gauges and thermometers at coil inlet and outlet connections. Comply with requirements in Section 230519 "Meters and Gauges for HVAC Piping."

      - IDENTIFICATION

        - Identify system components. Comply with requirements for identification materials and installation in Section 230553 "Identification for HVAC Piping and Equipment."

      - SYSTEM STARTUP

        - Perform the following before operating the system:

          - Open manual valves fully.

          - Inspect pumps for proper rotation.

          - Set makeup pressure-reducing valves for required system pressure.

          - Inspect air vents at high points of system and determine if all are installed and operating freely (automatic type), or bleed air completely (manual type).

          - Set temperature controls so all coils are calling for full flow.

          - Inspect and set operating temperatures of hydronic equipment, such as boilers, chillers, cooling towers, to specified values.

          - Verify lubrication of motors and bearings.

      - FIELD QUALITY CONTROL

        - Prepare hydronic piping in accordance with ASME B31.9 and as follows:

          - Leave joints, including welds, uninsulated and exposed for examination during test.

          - Provide temporary restraints for expansion joints that cannot sustain reactions due to test pressure. If temporary restraints are impractical, isolate expansion joints from testing.

          - Flush hydronic piping systems with clean water; then remove and clean or replace strainer screens.

          - Isolate equipment from piping. If a valve is used to isolate equipment, its closure is to be capable of sealing against test pressure without damage to valve. Install blinds in flanged joints to isolate equipment.

          - Install pressure-relief valve, set at a pressure no more than one-third higher than test pressure, to protect against damage by expanding liquid or other source of overpressure during test.

        - Perform the following tests on hydronic piping:

Procedures in subparagraphs below are paraphrased from ASME B31.9.

          - Use ambient-temperature water as a testing medium unless there is risk of damage due to freezing. Another liquid that is safe for workers and compatible with piping may be used.

          - While filling system, use vents installed at high points of system to release air. Use drains installed at low points for complete draining of test liquid.

          - Isolate expansion tanks and determine that hydronic system is full of water.

          - Subject piping system to hydrostatic test pressure that is not less than 1.5 times the system's working pressure. Test pressure is not to exceed maximum pressure for any vessel, pump, valve, or other component in system under test. Verify that stress due to pressure at bottom of vertical runs does not exceed 90 percent of specified minimum yield strength or 1.7 times the "SE" value in Appendix A in ASME B31.9.

          - After hydrostatic test pressure has been applied for at least 10 minutes, examine piping, joints, and connections for leakage. Eliminate leaks by tightening, repairing, or replacing components, and repeat hydrostatic test until there are no leaks.

          - Prepare written report of testing.

END OF SECTION 232113