Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 232223 - STEAM CONDENSATE PUMPS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provision for LEED 2009, LEED v4, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using hypertext links.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Single-stage, centrifugal pumps with floor-mounted receiver.

          - Regenerative turbine pumps with floor-mounted receiver.

          - Two-stage, centrifugal pumps with floor-mounted receiver.

          - Single-stage, centrifugal pumps with elevated receiver.

          - Vertical, wet-pit-mounted duplex pumps.

          - Pressure-powered pumps.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - PPE: Polyphenylene ether.

        - PPO: Polyphenylene oxide.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data: For each type of steam condensate pump.

          - Include certified performance curves and rated capacities, operating characteristics, furnished specialties, and accessories.

          - Indicate pump's operating point on curves.

          - Include receiver capacity and material.

        - Shop Drawings: For each pump/receiver.

          - Show pump layout and connections.

          - Include setting drawings with templates for installing foundation and anchor bolts and other anchorages.

          - Include diagrams for power, signal, and control wiring.

      - INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Retain "Seismic Qualification Data" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 230548 "Vibration and Seismic Controls for HVAC." See ASCE/SEI 7 for certification requirements for equipment and components.

        - Seismic Qualification Data: Certificates for steam condensate pumps/receivers, accessories, and components, from manufacturer.

          - Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

          - Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

          - Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For pumps to include in emergency, operation, and maintenance manuals.

          - Indicate actual installed items by marking submittals with an arrow or box.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - SOURCE LIMITATIONS

        - Obtain each type of pump from single source from single manufacturer.

      - PERFORMANCE REQUIREMENTS

        - ASME Compliance: Fabricate and label steam condensate receivers to comply with ASME Boiler and Pressure Vessel Code: Section VIII, Division 1.

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by an NRTL, and marked for intended location and use.

"ASHRAE/IES 90.1 Compliance" Paragraph below may be required to comply with Project requirements or authorities having jurisdiction. Sustainable design may require minimum efficiency equal to requirements in ASHRAE/IES 90.1.

        - ASHRAE/IES 90.1 Compliance: Applicable requirements in ASHRAE/IES 90.1, "Section 6 - Heating, Ventilating, and Air Conditioning."

Retain "Seismic Performance" Paragraph below for projects requiring seismic design. Delete paragraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

        - Seismic Performance: Steam condensate pumps/receivers to withstand the effects of earthquake motions determined in accordance with [ASCE/SEI 7] <Insert requirement>.

Retain first subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

          - The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

For life-safety components required to function after an earthquake (such as fire-sprinkler systems, components that contain hazardous content, and storage racks in structures open to the public), the Component Importance Factor is 1.5. For other components, the Component Importance Factor is 1.0 unless the structure is in Seismic Use Group III and component is necessary for continued operation of facility or failure of component could impair continued operation of facility, in which case the Component Importance Factor is 1.5.

          - Component Importance Factor: [1.5] [1.0].

See ASCE/SEI 7, Coefficients for Architectural Component Table and Seismic Coefficients for Mechanical and Electrical Components Table, for requirements to be inserted in subparagraph below.

          - <Insert requirements for Component Amplification Factor and Component Response Modification Factor>.

      - SINGLE-STAGE, CENTRIFUGAL PUMPS WITH FLOOR-MOUNTED RECEIVER

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Factory-fabricated, packaged, [simplex] [duplex] <Insert number of pumps>, electric-driven pumps; with receiver, float switch(es), controls, and accessories suitable for operation with steam condensate up to 200 deg F (93 deg C).

        - Receiver:

          - Floor mounted.

          - Material: [Cast iron] [Carbon steel] [Stainless steel].

          - Externally adjustable float switches.

          - Flanges for pump mounting.

          - Water-level gauge and dial thermometer.

          - Pressure gauge at each pump discharge.

          - Isolation valve between pump and receiver.

          - Lifting eyebolts.

          - Vent and overflow.

          - Inlet strainer with vertical self-cleaning bronze screen and large dirt pocket.

        - Pumps:

          - Centrifugal, close coupled, vertical design.

          - Permanently aligned.

In "Impeller" Subparagraph below, not all manufacturers offer each option. Consult manufacturers.

          - Impeller: [Bronze] [stainless steel] [or] [modified PPO/PPE blend thermoplastic].

          - Mechanical seals rated at 250 deg F (120 deg C).

          - Mounted on receiver flange.

        - Motor:

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph.

          - Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] <Insert type>.

Retain "Enclosure Materials," "Motor Bearings," "Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

          - Enclosure Materials: Cast iron, cast aluminum, or rolled steel.

In "Motor Bearings" Subparagraph below, confirm options availability with manufacturers.

          - Motor Bearings: [Permanently lubricated] [Grease-lubricated] ball bearings.

          - Service Conditions:

            - Ambient Temperature: <Insert deg C>.

            - Altitude: <Insert feet (meters)> above sea level.

            - High Humidity: <Insert wet bulb deg F (deg C)>.

            - <Insert conditions>.

          - Efficiency: Premium efficient.

          - NEMA Design: <Insert designation>.

          - Service Factor: <Insert value>.

        - Control Panel:

In first subparagraph below, confirm options availability with manufacturers.

          - NEMA 250, [Type 1] [Type 12] <Insert type> enclosure with hinged door and grounding lug, mounted on pump.

          - Combination magnetic starter with fused disconnect[ for each pump,] and cover interlock.

          - Factory wired between pumps and float switches, for single external electrical connection.

          - Provide fused, control-power transformer if exceeds 230 V ac.

Retain first two subparagraphs below for multiple pump units.

          - Electrical pump alternator to operate pumps in [lead-lag] <Insert sequence> sequence and allow [both] [all] pumps to operate on receiver high level.

          - Manual control to override electrical pump alternator and manually select the lead pump.

          - Hand-off-auto selector switch.

          - Momentary-contact "TEST" push button on cover for each pump.

          - Numbered terminal strip.

          - Disconnect switch.

If Project has more than one type or configuration of small floor-mounted pump with receiver and float switches, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

          - Number of Pumps: <Insert number>.

          - Capacity, Each Pump:

            - Flow: <Insert gpm (L/s)>.

            - Discharge Head: <Insert psig (kPa)>.

            - Discharge Size: <Insert NPS (DN)>.

            - Speed: <Insert rpm>.

            - Motor Horsepower: <Insert value>.

          - Receiver:

            - Capacity: <Insert gal. (L)>.

            - Inlet Size: <Insert NPS (DN)>.

            - Height to Inlet: <Insert inches (mm)>.

          - Electrical Characteristics:

            - Volts: [120] [230] [240] <Insert value>.

            - Phase: Single.

            - Hertz: 60.

            - Full-Load Amperes: <Insert value> A.

            - Minimum Circuit Ampacity: <Insert value> A.

            - Maximum Overcurrent Protection: <Insert value> A.

      - REGENERATIVE TURBINE PUMPS WITH FLOOR-MOUNTED RECEIVER

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Factory-fabricated, packaged, [simplex] [duplex], electric-driven regenerative turbine pumps; with receiver, pumps, float switch(es), controls, and accessories suitable for operation with steam condensate up to [210 deg F (99 deg C)] <Insert temperature>.

        - Receiver:

          - Floor mounted.

          - Material: [Cast iron] [Welded steel] <Insert material>.

          - Externally adjustable float switches.

          - Flanges for pump mounting.

          - Water-level gauge and dial thermometer.

          - Pressure gauge at each pump discharge.

          - Bronze fitting isolation valve between pump and receiver.

          - Lifting eyebolts.

          - Vent and overflow.

          - Cast-iron inlet strainer with vertical self-cleaning bronze screen and large dirt pocket.

        - Pumps:

          - Regenerative turbine, close coupled.

          - Permanently aligned.

          - Bronze fitted.

          - Mechanical seals rated at 250 deg F (120 deg C).

          - Independent pump control circuit for each pump.

          - Mounted on base or receiver flange.

          - Rated to operate with a minimum of 2 ft. (610 mm) of NPSH.

        - Motor:

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph.

          - Enclosure: [Open, dripproof] <Insert type>.

Retain "Enclosure Materials," "Motor Bearings," "Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

          - Enclosure Materials: Cast iron, cast aluminum, or rolled steel.

In "Motor Bearings" Subparagraph below, confirm options availability with manufacturer.

          - Motor Bearings: [Permanently lubricated] [Grease-lubricated] ball bearings.

          - Service Conditions:

            - Ambient Temperature: <Insert deg C>.

            - Altitude: <Insert feet (meters)> above sea level.

            - High Humidity: <Insert wet bulb deg F (deg C)>.

            - <Insert conditions>.

          - Efficiency: Premium efficient.

          - NEMA Design: <Insert designation>.

          - Service Factor: <Insert value>.

        - Control Panel:

In first subparagraph below, confirm options availability with manufacturer.

          - NEMA 250, [Type 1] [Type 12] <Insert type> enclosure with hinged door and grounding lug, mounted on pump.

          - Combination magnetic starter with fused disconnects[ for each pump,] and cover interlock.

          - Factory wired between pumps and float switches, for single external electrical connection.

          - Provide fused, control-power transformer if exceeds 230 V ac.

Retain first three subparagraphs below for multiple pump units.

          - Electrical pump alternator to operate pumps in [lead-lag] <Insert sequence> sequence and allow both pumps to operate on receiver high level.

          - Manual control to override electrical pump alternator and manually select the lead pump.

          - Hand-off-auto selector switch.

          - Momentary-contact "TEST" push button on cover for each pump.

          - Numbered terminal strip.

          - Disconnect switch.

If Project has more than one type or configuration of small floor-mounted regenerative turbine pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

          - Number of Pumps: <Insert number>.

          - Capacity, Each Pump:

            - Flow: <Insert gpm (L/s)>.

            - Discharge Head: <Insert psig (kPa)>.

            - Discharge Size: <Insert NPS (DN)>.

            - Speed: <Insert rpm>.

            - Motor Horsepower: <Insert value>.

          - Receiver:

            - Capacity: <Insert gal. (L)>.

            - Inlet Size: <Insert NPS (DN)>.

            - Height to Inlet: <Insert inches (mm)>.

          - Electrical Characteristics:

Power supply to this pump includes controls.

            - Volts: [120] [230] [240] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: 60.

            - Full-Load Amperes: <Insert value> A.

            - Minimum Circuit Ampacity: <Insert value> A.

            - Maximum Overcurrent Protection: <Insert value> A.

      - TWO-STAGE, CENTRIFUGAL PUMPS WITH FLOOR-MOUNTED RECEIVER

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Factory-fabricated, packaged, [simplex] [duplex] <Insert number of pumps>, electric-driven pumps; with receiver, pumps, controls, and accessories suitable for operation with steam condensate up to 210 deg F (99 deg C).

        - Receiver:

          - Floor mounted.

          - Material: [Carbon steel] [Type 304 stainless steel] [Type 316 stainless steel].

          - Externally adjustable float switches.

          - Flanges for pump mounting.

          - Water-level gauge and dial thermometer.

          - Pressure gauge at each pump discharge.

          - Isolation valves between receiver and pump discharge.

          - Lifting eyebolts.

          - Vent and overflow.

          - Inlet strainer with self-cleaning bronze screen, dirt pocket, and cleanout plug on receiver inlet.

        - Pumps:

          - Centrifugal, two stage, close coupled.

          - Vertical design, permanently aligned.

          - Impeller: [Type 304] [Type 316] stainless steel.

          - Stainless steel shafts.

          - Mechanical seals rated at 250 deg F (120 deg C).

          - Rated to operate with a minimum of 2 ft. (610 mm) of NPSH.

          - Mounted on receiver flanges.

        - Motor:

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph.

          - Enclosure: [Open, dripproof] [Totally enclosed fan cooled] <Insert type>.

Retain "Enclosure Materials," "Motor Bearings," "Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

          - Enclosure Materials: Cast iron, cast aluminum, or rolled steel.

In "Motor Bearings" Subparagraph below, confirm options availability with manufacturers.

          - Motor Bearings: [Permanently lubricated] [Grease-lubricated] ball bearings.

          - Service Conditions:

            - Ambient Temperature: <Insert deg C>.

            - Altitude: <Insert feet (meters)> above sea level.

            - High Humidity: <Insert wet bulb deg F (deg C)>.

            - <Insert conditions>.

          - Efficiency: Premium efficient.

          - NEMA Design: <Insert designation>.

          - Service Factor: <Insert value>.

        - Control Panel:

In first subparagraph below, confirm options availability with manufacturers.

          - NEMA 250, [Type 1] [Type 12] <Insert type> enclosure with hinged door and grounding lug, mounted on pump.

          - Combination magnetic starter with fused disconnect[ for each pump,] and cover interlock.

          - Factory wired between pumps and float switches, for single external electrical connection.

          - Provide fused, control-power transformer if exceeds 230 V ac.

Retain first three subparagraphs below for multiple pump units.

          - Electrical pump alternator to operate pumps in [lead-lag] <Insert sequence> sequence and allow both pumps to operate on receiver high level.

          - Manual control to override electrical pump alternator and manually select the lead pump.

          - Hand-off-auto selector switch.

          - Momentary-contact "TEST" push button on cover for each pump.

          - Numbered terminal strip.

          - Disconnect switch.

If Project has more than one type or configuration of large duplex floor-mounted pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

          - Number of Pumps: <Insert number>.

          - Capacity, Each Pump:

            - Flow: <Insert gpm (L/s)>.

            - Discharge Head: <Insert psig (kPa)>.

            - Discharge Size: <Insert NPS (DN)>.

            - Speed: <Insert rpm>.

            - Motor Horsepower: <Insert value>.

          - Receiver:

            - Capacity: <Insert gal. (L)>.

            - Inlet Size: <Insert NPS (DN)>.

            - Height to Inlet: <Insert inches (mm)>.

          - Electrical Characteristics:

            - Volts: [120] [208] [230] [240] [480] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: 60.

            - Full-Load Amperes: <Insert value> A.

            - Minimum Circuit Ampacity: <Insert value> A.

            - Maximum Overcurrent Protection: <Insert value> A.

      - SINGLE-STAGE, CENTRIFUGAL PUMPS WITH ELEVATED RECEIVER

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Factory-fabricated, packaged, [simplex] [duplex] <Insert number of pumps>, electric-driven pumps; with receiver, pumps, controls, and accessories suitable for operation with steam condensate up to 212 deg F (100 deg C).

        - Receiver:

          - Mounted on fabricated-steel supports.

          - Material: [Cast iron] [Welded steel] [Stainless steel].

          - Externally adjustable float switches.

          - Water-level gauge and dial thermometer.

          - Pressure gauge at each pump discharge.

          - Isolation valves between receiver and pumps.

          - Lifting eyebolts.

          - Inlet cascade baffle and convex heads.

          - Inlet strainer with self-cleaning bronze screen, dirt pocket, and cleanout plug on receiver inlet.

        - Pumps:

          - Centrifugal, close coupled.

          - Permanently aligned.

In "Impeller" Subparagraph below, not all manufacturers offer each option. Consult manufacturers.

          - Impeller: [Bronze] [stainless steel] [or] [modified PPO/PPE blend thermoplastic].

          - Stainless steel shafts.

          - Mechanical seals rated at 250 deg F (120 deg C).

          - Mounted on base below the receiver.

          - Rated to operate with a minimum of 2 ft. (610 mm) of NPSH.

        - Motor:

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph.

          - Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] <Insert type>.

Retain "Enclosure Materials," "Motor Bearings," "Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

          - Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

In "Motor Bearings" Subparagraph, confirm options availability with manufacturers.

          - Motor Bearings: [Permanently lubricated] [Grease-lubricated] ball bearings.

          - Service Conditions:

            - Ambient Temperature: <Insert deg C>.

            - Altitude: <Insert feet (meters)> above sea level.

            - High Humidity: <Insert wet bulb deg F (deg C)>.

            - <Insert conditions>.

          - Efficiency: Premium efficient.

          - NEMA Design: <Insert designation>.

          - Service Factor: <Insert value>.

        - Pipe: ASTM A53/A53M, Type S, Grade B or ASTM A106/A106M; Schedule 80; seamless steel.

        - Fittings NPS 2 (DN 50) and Smaller: ASME B16.1, Class 125 cast iron, threaded.

        - Fittings NPS 2-1/2 (DN 65) and Larger: ASTM A234/A234M, steel, for welded connections.

        - Control Panel:

In first subparagraph below, confirm options availability with manufacturer.

          - NEMA 250, [Type 1] [Type 12] <Insert type> enclosure with hinged door and grounding lug, mounted on pump.

          - Combination magnetic starter with fused disconnect[ for each pump,] and cover interlock.

          - Factory wired between pumps and float switches, for single external electrical connection.

          - Provide fused, control-power transformer if exceeds 230 V ac.

Retain first three subparagraphs below for multiple pump units.

          - Electrical pump alternator to operate pumps in [lead-lag] <Insert sequence> sequence and allow [both] [all] pumps to operate on receiver high level.

          - Manual control to override electrical pump alternator and manually select the lead pump.

          - Hand-off-auto selector switch.

          - Momentary-contact "TEST" push button on cover for each pump.

          - Numbered terminal strip.

          - Disconnect switch.

If Project has more than one type or configuration of large floor-mounted pump with elevated receiver, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

          - Number of Pumps: <Insert number>.

          - Capacity, Each Pump:

            - Flow: <Insert gpm (L/s).>

            - Discharge Head: <Insert psig (kPa)>.

            - Discharge Size: <Insert NPS (DN)>.

            - Speed: <Insert rpm>.

            - Motor Horsepower: <Insert value>.

          - Receiver:

            - Capacity: <Insert gal. (L)>.

            - Inlet Size: <Insert NPS (DN)>.

            - Height to Inlet: <Insert inches (mm)>.

          - Electrical Characteristics:

            - Volts: [120] [208] [230] [240] [480] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: 60.

            - Full-Load Amperes: <Insert value> A.

            - Minimum Circuit Ampacity: <Insert value> A.

            - Maximum Overcurrent Protection: <Insert value> A.

      - VERTICAL, WET-PIT-MOUNTED DUPLEX PUMPS

Coordinate basin dimensions, inlet size, and location on Drawings.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Factory-fabricated, packaged, duplex, electric-driven pumps; with controls and accessories suitable for operation with steam condensate up to 200 deg F (93 deg C).

        - Basin: Cast iron, with hub-type inlets.

          - Cast-iron inlet strainer with vertical self-cleaning bronze screen and large dirt pocket.

          - Discharge pressure gauges.

Retain "Anchor Flange" Subparagraph below where required to anchor basin to concrete slab if there is a ground-water problem.

          - Anchor Flange: Cast iron, attached to basin, in location and of size required to anchor basin to concrete slab.

        - Basin Cover: Cast-iron or steel cover for each pump with gasketed openings for access to pumps, pump shafts, control rods, discharge piping, and vent connections.

        - Pumps:

          - Vertical, wet-pit mounted, flexible coupled, and suspended.

          - Cast-iron casing with open inlet.

          - Stainless steel shaft with oil-lubricated, bronze, intermediate sleeve bearings; 48-inch (1200-mm) maximum intervals where basin depth is more than 48 inches (1200 mm); and grease-lubricated, ball-type, thrust bearings.

          - Shaft Couplings: Flexible, capable of absorbing vibration.

          - Impeller: Bronze.

          - Mechanical seals rated at 250 deg F (120 deg C), with carbon rotating ring bearing on a ceramic seat held by a stainless steel spring and enclosed by a flexible bellows and gasket.

        - Motors:

          - Vertically mounted on cast-iron pedestal.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph.

          - Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] <Insert type>.

Retain "Enclosure Materials," "Motor Bearings," "Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

          - Enclosure Materials: Cast iron, cast aluminum, or rolled steel.

In "Motor Bearings" Subparagraph, confirm options availability with manufacturers.

          - Motor Bearings: [Permanently lubricated] [Grease-lubricated] ball bearings.

          - Service Conditions:

            - Ambient Temperature: <Insert deg C>.

            - Altitude: <Insert feet (meters)> above sea level.

            - High Humidity: <Insert wet bulb deg F (deg C)>.

            - <Insert conditions>.

          - Efficiency: Premium efficient.

          - NEMA Design: <Insert designation>.

          - Service Factor: <Insert value>.

        - Pump Discharge Piping: Manufacturer's standard steel or bronze pipe unless otherwise indicated.

        - Control Panel:

In first subparagraph below, confirm options availability with manufacturers.

          - NEMA 250, [Type 1] [Type 12] <Insert type> enclosure with hinged door and grounding lug, mounted on pump.

          - Combination magnetic starter with fused disconnect for each pump, and cover interlock.

          - Factory wired between pumps and float switches, for single external electrical connection.

          - Provide fused, control-power transformer if exceeds 230 V ac.

          - Electrical pump alternator to operate pumps in lead-lag sequence and allow both pumps to operate on receiver high level.

          - Manual control to override electrical pump alternator and manually select the lead pump.

          - Hand-off-selector switch.

          - Momentary-contact "TEST" push button on cover for each pump.

          - Numbered terminal strip.

          - Disconnect switch.

If Project has more than one type or configuration of wet-pit-mounted duplex pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

          - Capacity, Each of Two Pumps:

            - Flow: <Insert gpm (L/s)>.

            - Discharge Head: <Insert psig (kPa)>.

            - Discharge Size: <Insert NPS (DN)>.

            - Speed: <Insert rpm>.

            - Motor Horsepower: <Insert value>.

          - Underground Basin:

            - Diameter: <Insert inches (mm)>.

            - Depth: <Insert inches (mm)>.

            - Inlet Size: <Insert NPS (DN)>.

            - Bottom to Centerline of Inlet: <Insert inches (mm)>.

          - Electrical Characteristics:

            - Volts: [120] [208] [230] [480] <Insert value>.

            - Phase: [Single] [Three].

            - Hertz: 60.

            - Full-Load Amperes: <Insert value> A.

            - Minimum Circuit Ampacity: <Insert value> A.

            - Maximum Overcurrent Protection: <Insert value> A.

      - PRESSURE-POWERED PUMPS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Factory-fabricated, [simplex] [duplex], pressure-powered pumps with float-operated valve controls, valves, piping connections, and accessories suitable for pumping steam condensate using [steam] [compressed air].

        - Pump Body: [Cast iron] [Welded steel], ASME rated to 125 psig (860 kPa).

        - Piping Connections: Threaded or flanged; for steam condensate, operating medium, vent, and indicated accessories.

        - Level Gauge: Glass site gauge with shutoff cocks.

        - Valves: Manufacturer's standard check valves on inlet and outlet.

        - Internal Parts: Stainless steel float, springs, and actuating mechanism.

        - Valve Seals: Replaceable from exterior.

Retain "Receiver" Paragraph below for pumps with receiver.

        - Receiver:

          - Factory skid-mounted on steel supports.

          - Material; [Cast iron] [Welded steel] [Type 316 stainless steel].

          - Threaded or flanged piping connections.

          - Water-level gauge and dial thermometer.

          - Pressure gauge at pump discharge.

          - Bronze fitting isolation valve between pump and receiver.

          - Lifting eyebolts.

          - Inlet vent and an overflow.

          - Cast-iron inlet strainer with vertical self-cleaning bronze screen and large dirt pocket.

Retain "Pipe" and "Fittings" paragraphs below for duplex pumps or for simplex pumps with receiver.

        - Pipe: ASTM A53/A53M, Type S, Grade B or ASTM A106/A106M; Schedule 80; seamless steel.

        - Fittings: Wrought steel, ASTM A234/A234M with wall thickness to match adjacent pipe or wrought cast- and forged-steel flanges and flanged fittings, ASME B16.5.

If Project has more than one type or configuration of pressure-powered steam condensate pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

        - Capacities and Characteristics:

          - Number of Pumps: <Insert number>.

          - Capacity, Each Pump:

            - Flow: <Insert gpm (L/s)>.

            - Discharge Head: <Insert psig (kPa)>.

            - Discharge Size: <Insert NPS (DN)>.

Retain "Operating Steam Pressure" and "Steam Consumption Rate" subparagraphs below for steam-powered pumps.

          - Operating Steam Pressure: <Insert psig (kPa)>.

          - Steam Consumption Rate: <Insert lb/1000 lb (kg/1000 kg)> of steam condensate.

Retain "Operating Compressed-Air Pressure" and "Compressed-Air Consumption Rate" subparagraphs below for compressed-air powered pumps.

          - Operating Compressed-Air Pressure: <Insert psig (kPa)>.

          - Compressed-Air Consumption Rate: <Insert cu. ft./1000 lb (L/1000 kg)> of steam condensate.

          - Receiver:

            - Capacity: <Insert gal. (L)>.

            - Inlet Size: <Insert NPS (DN)>.

            - Height to Inlet: <Insert inches (mm)>.

- EXECUTION

      - EXAMINATION

        - Examine equipment foundations and anchor-bolt locations for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

        - Examine roughing-in for piping systems to verify actual locations of piping connections before pump installation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

Delete first paragraph below for pressure-powered steam condensate pumps.

        - Install pumps to provide access for periodic maintenance including removing motors, impellers, couplings, and accessories.

        - Support pumps and piping separately so piping is not supported by pumps.

        - Install thermometers and pressure gauges.

        - Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

          - Install pumps on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases and foundations specified in Section 033000 "Cast-in-Place Concrete."

Retain one of two subparagraphs below if vibration isolation is required. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

          - Comply with requirements for vibration isolation and seismic-control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

          - Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

      - PIPING CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Comply with requirements for piping specified in Section 232213 "Steam and Condensate Piping" and Section 232216 "Steam and Condensate Piping Specialties."

        - Where installing piping adjacent to machine, allow space for service and maintenance.

Retain first paragraph for compressed-air powered pumps.

        - Install compressed-air supply for pressure-powered pumps as required in Section 221513 "General-Service Compressed-Air Piping."

        - Install a globe and check valve at inlet of each pump and a gate and check valve at pump outlet.

        - Install pressure gauge at each pump discharge.

        - Pipe drain to nearest floor drain for overflow and drain piping connections.

        - Install full-size vent piping to outdoors, terminating in 180-degree elbow.

      - ELECTRICAL CONNECTIONS

        - Connect wiring in accordance with Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

        - Ground equipment in accordance with Section 260526 "Grounding and Bonding for Electrical Systems."

        - Install nameplate for each electrical connection, indicating electrical equipment designation and circuit number feeding connection.

Retain one of two subparagraphs below. First subparagraph cross-references Section 260553 "Identification for Electrical Systems" and should be retained for consistent electrical identification. Second subparagraph is an abbreviated version of the product specified in Section 260553 "Identification for Electrical Systems."

          - Nameplate to be laminated acrylic or melamine plastic signs, as specified in Section 260553 "Identification for Electrical Systems."

          - Nameplate to be laminated acrylic or melamine plastic signs with a black background and engraved white letters at least 1/2 inch (13 mm) high.

      - CONTROL CONNECTIONS

        - Install control and electrical power wiring to field-mounted control devices.

        - Connect control wiring in accordance with Section 260523 "Control-Voltage Electrical Power Cables."

      - SYSTEM STARTUP

        - [Engage a factory-authorized service representative to perform] [Perform] startup service.

          - Complete installation and startup checks in accordance with manufacturer's written instructions.

          - Clean strainers.

          - Adjust steam condensate pump controls.

          - Adjust pump controls for automatic start, stop, and alarm operation.

          - Perform the following operational checks before starting:

            - Set float switches to operate at proper levels.

            - Check motors for proper rotation.

            - Test pump controls and demonstrate compliance with requirements.

            - Replace damaged or malfunctioning pump controls and equipment.

            - Verify that pump controls are correct for required application.

          - Start steam condensate pumps in accordance with manufacturer's written startup instructions.

      - DEMONSTRATION

        - [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain steam condensate pumps.

END OF SECTION 232223