Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 233600 - AIR TERMINAL UNITS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Bypass, single-duct air terminal units.

          - Modulating, single-duct air terminal units.

          - Parallel fan-powered air terminal units.

          - Series fan-powered air terminal units.

          - Dual-duct air terminal units.

          - Induction air terminal units.

          - Diffuser-type air terminal units.

          - Balancing terminal units.

          - Pressure-control terminal units.

          - Critical environment control valve.

          - Underfloor air distribution terminal units.

          - Exhaust single-duct terminal units.

          - DOAS, series, fan-powered air terminal units.

          - Casing liner.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data: For each type of air terminal unit.

          - Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for air terminal units.

          - Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

        - Sustainable Design Submittals:

          - <Double click to insert sustainable design text for adhesives.>

          - <Double click to insert sustainable design text for ASHRAE 62.1.>

        - Shop Drawings: For air terminal units.

          - Include plans, elevations, sections, and mounting details.

          - Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Retain first subparagraph below if equipment includes wiring.

          - Include diagrams for power, signal, and control wiring.

          - Hangers and supports, including methods for duct and building attachment[, seismic restraints,] and vibration isolation.

Retain "Delegated Design Submittal" Paragraph below if design services have been delegated to Contractor. If seismic restraints are not applicable, signing and sealing by professional engineer may not be required. Verify with authorities having jurisdiction.

        - Delegated Design Submittal: For vibration isolation[ and supports,] [, and seismic restraints] indicated to comply with performance requirements and design criteria, including analysis data[ signed and sealed by the qualified professional engineer responsible for their preparation].

          - Materials, fabrication, assembly, and spacing of hangers and supports.

          - Design Calculations: Calculate requirements for selecting vibration isolators[, supports,][ and seismic restraints].

      - INFORMATIONAL SUBMITTALS

Information submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Coordinate paragraph with other Sections specifying products listed below. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

        - Coordination Drawings: Floor plans and other details, or BIM model, drawn to scale, indicating the items described in this Section, and coordinated with all building trades.

Retain "Seismic Qualification Data" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 230548 "Vibration and Seismic Controls for HVAC." See ASCE/SEI 7 for certification requirements for equipment and components.

        - Seismic Qualification Data: For air terminal units, accessories, and components, from manufacturer.

          - Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

          - Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

          - Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

        - Field quality-control reports.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For air terminal units to include in emergency, operation, and maintenance manuals.

          - In addition to items specified in Section 017823 "Operation and Maintenance Data," include the following:

            - Instructions for resetting minimum and maximum air volumes.

            - Instructions for adjusting software set points.

      - MAINTENANCE MATERIAL SUBMITTALS

See Section 017700 "Closeout Procedures" for submission of maintenance material items.

        - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Fan-Powered-Unit Filters: Furnish [one] <Insert number> spare filter(s) for each filter installed.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - PERFORMANCE REQUIREMENTS

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a Qualified Electrical Testing Laboratory, and marked for intended location and application.

"ASHRAE 62.1 Compliance" Paragraph below may be required to comply with Project requirements or authorities having jurisdiction. Sustainable design systems require compliance with requirements in ASHRAE 62.1, including requirements for controls, surfaces in contact with airstream, particulate filtration, finned-tube coil selection and cleaning, and equipment access. Verify, with manufacturers, availability of units with components and features that comply with these requirements.

        - ASHRAE 62.1 Compliance: Applicable requirements in ASHRAE 62.1, Section 5 - "Systems and Equipment," and Section 7 - "Construction and System Start-up."

"ASHRAE/IES 90.1 Compliance" Paragraph below may be required to comply with Project requirements or authorities having jurisdiction. Sustainable design may require minimum efficiency equal to requirements in ASHRAE.IES 90.1.

        - ASHRAE/IES 90.1 Compliance: Applicable requirements in ASHRAE/IES 90.1, "Section 6 - Heating, Ventilating, and Air Conditioning."

Retain "Delegated Design" Paragraph below if Contractor is required to assume responsibility for design.

In "Delegated Design" Paragraph, if seismic restraints are not applicable on Project, the option to engage a professional engineer may not be required. Verify with authorities having jurisdiction.

        - Delegated Design: [Engage a qualified professional engineer, as defined in Section 014000 "Quality Requirements," to] design vibration isolation[, supports,][ and seismic restraints], including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

Retain "Seismic Performance" Paragraph below with "Seismic Qualification Data" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Delete paragraph below if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

        - Seismic Performance: Air terminal units shall withstand the effects of earthquake motions determined in accordance with [ASCE/SEI 7] <Insert requirement>. See Section 230548 "Vibration and Seismic Controls for HVAC."

Retain first subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

          - The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

For life-safety components required to function after an earthquake (such as fire-sprinkler systems, components that contain hazardous content, and storage racks in structures open to the public), the Component Importance Factor is 1.5. For other components, the Component Importance Factor is 1.0 unless the structure is in Seismic Use Group III and component is necessary for continued operation of facility or failure of component could impair continued operation of facility, in which case the Component Importance Factor is 1.5.

          - Component Importance Factor: [1.5] [1.0].

See ASCE/SEI 7, Coefficients for Architectural Component Table and Seismic Coefficients for Mechanical and Electrical Components Table, for requirements to be inserted in subparagraph below.

          - <Insert requirements for Component Amplification Factor and Component Response Modification Factor>.

      - BYPASS, SINGLE-DUCT AIR TERMINAL UNITS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Pressure-dependent, diverting-damper assembly inside unit casing with control components inside a protective metal shroud. Configuration enables variable volume airflow to individual zones while bypassing the unneeded air to the ceiling plenum for recirculation.

In "Casing" Paragraph below, not all manufacturers offer each casing thickness option. Coordinate availability with manufacturers.

        - Casing: Minimum [20-gauge-] [22-gauge-] <Insert dimension> thick galvanized steel.

Verify, with air terminal unit manufacturer, availability of casing liner.

          - Casing Liner: Comply with requirements in "Casing Liner" Article below for ["Casing Liner, Fibrous Glass" Paragraph] ["Casing Liner, Flexible Elastomeric" Paragraph] [with "Antimicrobial Erosion-Resistant Coating" Subparagraph] [with "Foil-Faced Liner" Subparagraph] [with "Solid Metal Liner" Subparagraph] [with "Perforated Metal Liner" Subparagraph] [with "Specialty Liner" Subparagraph].

        - Diverter Assembly:

          - Damper, shaft, and heavy-duty self-lubricating bearings.

        - Attenuator Section: Casing material and thickness matching associated air terminal unit casing. Provide [absorptive] [packless] attenuator integral with the air terminal unit, with noise transmission loss performance as required in schedules on Drawings.

Retain "Hydronic Heating Coils" or "Electric-Resistance Heating Coils" Paragraph below if heating coil is required. Coordinate retained coils with manufacturers.

        - Hydronic Heating Coils: Copper tube, with mechanically bonded aluminum fins spaced no closer than [0.1 inch (2.5 mm)] [0.08 inch (2.0 mm)]. Include manual air vent and drain valve. Provide hydronic heating coils for air terminal units scheduled on Drawings.

        - Electric-Resistance Heating Coils: Nickel-chromium heating wire, free of expansion noise and hum, mounted in ceramic inserts in a galvanized-steel housing; with primary automatic, and secondary manual, reset thermal cutouts. Terminate elements in stainless steel, machine-staked terminals secured with stainless steel hardware. Provide electric-resistance heating coils for air terminal units scheduled on Drawings.

Retain one of first two subparagraphs below.

          - Stage(s): [One] [Two] [Three].

          - SCR controlled.

          - Access door interlocked disconnect switch.

          - Downstream air temperature sensor with local connection to override discharge-air temperature to not exceed a maximum temperature set point (adjustable).

Subparagraphs below are optional features.

          - Nickel chrome 80/20 heating elements.

          - Airflow switch for proof of airflow.

          - Fuses in terminal box for overcurrent protection (for coils of more than 48 A).

          - Pneumatic-electric switches and relays.

          - Magnetic contactor for each step of control (for three-phase coils).

Retain "Electric Controls" or "Electronic Controls" Paragraph below, or delete both if controls are specified in Section 230923 "Direct Digital Control (DDC) System for HVAC."

        - Electric Controls:

          - Electric Damper Actuator: 24 V, [spring-return open] [spring-return closed] [fail in last position] [, with microswitch to enable heating control circuit].

          - Electric Thermostat: Wall-mounted electric type with temperature display in Fahrenheit and Celsius, and space temperature set point.

          - Air Volume Controls: Pressure-dependent volume controls with field-adjustable minimum and maximum position stops.

        - Electronic Controls:

          - Electronic Damper Actuator: 24 V, [spring-return open] [spring-return closed] [capacitor-discharge-return open] [capacitor-discharge-return closed] [fail in last position].

          - Electronic Thermostat: Wall-mounted electronic type with temperature display in Fahrenheit and Celsius, and space temperature set point.

          - Electronic Air Volume Controls: Pressure-dependent volume controls with field-adjustable minimum and maximum position stops.

        - Direct Digital Controls:

Retain "Terminal Unit Controller" and "Room Sensor" and delete "Terminal Unit Controller, Section 230923" subparagraphs below if controllers and room sensor are to be furnished by air terminal unit manufacturer. Delete "Terminal Unit Controller" and "Room Sensor" and retain "Terminal Unit Controller, Section 230923" subparagraphs if controllers and sensors are provided under Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Terminal Unit Controller: Pressure-independent, VAV controller and integrated actuator, and electronic airflow transducer with multipoint velocity sensor at air inlet, factory calibrated to minimum and maximum air volumes.

First four subparagraphs below are optional features.

            - Occupied and unoccupied operating mode.

            - Remote reset of airflow or temperature set points.

            - Adjusting and monitoring with portable terminal.

            - Communication with temperature-control system specified in Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Room Sensor: Wall mounted with temperature set-point adjustment and access for connection of portable operator terminal.

          - Terminal Unit Controller, Section 230923: Controller is to be factory mounted and wired by air terminal manufacturer; unit controller, actuators, and room sensors are to be furnished under Section 230923 "Direct Digital Control (DDC) System for HVAC."

        - Control Sequence: See [Section 230993.11 "Sequence of Operation for HVAC"] [Drawings].

      - MODULATING, SINGLE-DUCT AIR TERMINAL UNITS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Volume-damper assembly inside unit casing with control components inside a protective metal shroud.

        - Casing: Minimum [20-gauge-] [22-gauge-] thick galvanized steel.

Verify, with air terminal unit manufacturer, availability of casing liner.

          - Casing Liner: Comply with requirements in "Casing Liner" Article below for ["Casing Liner, Fibrous Glass" Paragraph] ["Casing Liner, Flexible Elastomeric" Paragraph] [with "Antimicrobial Erosion-Resistant Coating" Subparagraph] [with "Foil-Faced Liner" Subparagraph] [with "Solid Metal Liner" Subparagraph] [with "Perforated Metal Liner" Subparagraph] [with "Specialty Liner" Subparagraph].

          - Air Inlet: Round stub connection or S-slip and drive connections for duct attachment.

          - Air Outlet: S-slip and drive connections[, size matching inlet size].

          - Access: Removable panels for access to parts requiring service, adjustment, or maintenance; with airtight gasket.

        - Volume Damper: Galvanized steel with peripheral gasket and self-lubricating bearings.

Leakage rates in "Maximum Damper Leakage" Subparagraph below vary among manufacturers and with pressure rating.

          - Maximum Damper Leakage: AHRI 880 rated, [1] [2] percent of nominal airflow at [3-inch wg (750-Pa)] <Insert value> inlet static pressure.

        - Velocity Sensors: Multipoint array with velocity inlet sensors.

        - Attenuator Section: Casing material and thickness matching associated air terminal unit casing. Provide [absorptive] [packless] attenuator integral with the air terminal unit, with noise transmission loss performance as required in schedules on Drawings.

Retain "Hydronic Heating Coils" or "Electric-Resistance Heating Coils" Paragraph below if heating coil is required. Coordinate retained coils with manufacturers.

        - Hydronic Heating Coils: Copper tube, with mechanically bonded aluminum fins spaced no closer than [0.1 inch (2.5 mm)] [0.08 inch (2.0 mm)]. Include manual air vent and drain valve. Provide hydronic heating coils for air terminal units scheduled on Drawings.

        - Electric-Resistance Heating Coils: Nickel-chromium heating wire, free of expansion noise and hum, mounted in ceramic inserts in a galvanized-steel housing; with primary automatic, and secondary manual, reset thermal cutouts. Terminate elements in stainless steel, machine-staked terminals secured with stainless steel hardware. Provide electric-resistance heating coils for air terminal units scheduled on Drawings.

Retain one of first two subparagraphs below.

          - Stage(s): [One] [Two] [Three].

          - SCR controlled.

          - Access door interlocked disconnect switch.

          - Downstream air temperature sensor with local connection to override discharge-air temperature to not exceed a maximum temperature set point (adjustable).

Retain applicable subparagraphs below.

          - Nickel chrome 80/20 heating elements.

          - Airflow switch for proof of airflow.

          - Fan interlock contacts.

          - Fuses in terminal box for overcurrent protection (for coils of more than 48 A).

          - Pneumatic-electric switches and relays.

          - Magnetic contactor for each step of control (for three-phase coils).

        - Electric Controls:

          - Electric Damper Actuator: 24 V, [spring-return open] [spring-return closed] [fail in last position].

          - Electric Thermostat: Wall-mounted electronic type with clock display, temperature display in Fahrenheit and Celsius, and space temperature set point.

          - Air Volume Controls: Pressure-dependent volume controls with field-adjustable minimum and maximum position stops.

        - Electronic Controls:

          - Electronic Damper Actuator: 24 V, [spring-return open] [spring-return closed] [capacitor-discharge-return open] [capacitor-discharge-return closed] [fail in last position].

          - Electronic Thermostat: Wall-mounted electronic type with temperature set-point display in Fahrenheit and Celsius.

          - Electronic Air Volume Controller: Pressure-independent analog electronic controller, factory calibrated and field adjustable to minimum and maximum air volumes; provides consistent airflow to the space in response to electronic thermostat signal while compensating for inlet static-pressure variations of up to 4 inches wg (1000 Pa); includes a multipoint velocity sensor at air inlet.

        - Pneumatic Controls:

          - Pneumatic Damper Actuator: [0 to 13 psig (0 to 90 kPa)] <Insert range> spring range.

If retaining both direct- and reverse-acting thermostats, indicate location of each type on Drawings.

          - Pneumatic Thermostat: Wall-mounted pneumatic type [direct acting] [and] [reverse acting] with appropriate mounting hardware.

          - Pneumatic Air Volume Controller: Factory calibrated and field adjustable to minimum and maximum air volumes; provides consistent airflow to the space in response to pneumatic thermostat signal while compensating for inlet static-pressure variations of up to 4 inches wg (1000 Pa); includes a multipoint velocity sensor at air inlet.

        - Direct Digital Controls:

Retain "Terminal Unit Controller" and "Room Sensor" and delete "Terminal Unit Controller, Section 230923" subparagraphs below if controllers and room sensors are to be furnished by the air terminal unit manufacturer. Delete "Terminal Unit Controller" and "Room Sensor" and retain "Terminal Unit Controller, Section 230923" subparagraphs if controllers and sensors are provided under Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Terminal Unit Controller: Pressure-independent, VAV controller and integrated actuator, and electronic airflow transducer with multipoint velocity sensor at air inlet, factory calibrated to minimum and maximum air volumes.

Fist four subparagraphs below are optional features.

            - Occupied and unoccupied operating mode.

            - Remote reset of airflow or temperature set points.

            - Adjusting and monitoring with portable terminal.

            - Communication with temperature-control system specified in Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Room Sensor: Wall mounted with [temperature set-point adjustment and ]access for connection of portable operator terminal.

          - Terminal Unit Controller, Section 230923: Controller is to be factory mounted and wired by air terminal manufacturer; unit controllers, integrated actuators, and room sensors to be furnished under Section 230923 "Direct Digital Controls (DDC) for HVAC."

        - Control Sequence: See [Section 230993.11 "Sequence of Operation for HVAC"] [Drawings] for control sequences.

      - PARALLEL FAN-POWERED AIR TERMINAL UNITS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Volume-damper assembly and centrifugal fan in parallel arrangement inside unit casing with control components inside a protective metal shroud[; low-profile design].

        - Casing: Minimum [20-gauge-] [22-gauge-] thick galvanized steel.

Verify, with air terminal unit manufacturer, availability of casing liner.

          - Casing Liner: Comply with requirements in "Casing Liner" Article below for ["Casing Liner, Fibrous Glass" Paragraph] ["Casing Liner, Flexible Elastomeric" Paragraph] [with "Antimicrobial Erosion-Resistant Coating" Subparagraph] [with "Foil-Faced Liner" Subparagraph] [with "Solid Metal Liner" Subparagraph] [with "Perforated Metal Liner" Subparagraph] [with "Specialty Liner" Subparagraph].

          - Air Inlets: Round stub connections or S-slip and drive connections for duct attachment.

          - Air Outlet: S-slip and drive connections.

          - Access: Removable panels for access to parts requiring service, adjustment, or maintenance; with airtight gasket and quarter-turn latches.

          - Fan: Forward-curved centrifugal, located at plenum air inlet.

        - Volume Damper: Galvanized steel with flow-sensing ring and peripheral gasket and self-lubricating bearings.

Leakage rates in "Maximum Damper Leakage" Subparagraph below vary among manufacturers and with pressure rating. Verify with manufacturers.

          - Maximum Damper Leakage: AHRI 880 rated, [1] [2] percent of nominal airflow at [3-inch wg (750-Pa)] <Insert value> inlet static pressure.

        - Velocity Sensors: Multipoint array with velocity inlet sensors.

        - Fan Motor:

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Type: [Permanent-split capacitor with SCR for speed adjustment] [Electronically commutated motor].

          - Fan-Motor Assembly Isolation: Rubber isolators.

          - Enclosure: [Open dripproof] [Totally enclosed, fan cooled] <Insert type>.

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from equipment manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements. Verify enclosure types with manufacturer of specified equipment.

          - Enclosure Materials: [Cast iron] <Insert material>.

          - Motor Bearings: <Insert requirements>.

          - Unusual Service Conditions:

            - Ambient Temperature: <Insert deg F (deg C)>.

            - Altitude: <Insert feet (m)> above sea level.

Retain first subparagraph below if application requires this rating.

            - High humidity.

            - <Insert conditions>.

          - Efficiency: Premium efficient as defined in NEMA MG-1.

          - NEMA Design: <Insert designation>.

          - Service Factor: <Insert value>.

          - Motor Speed: [Single speed] [Variable speed].

            - Speed Control: Infinitely adjustable with pneumatic-electric and electronic controls.

Retain "Electrical Characteristics" Subparagraph below if characteristics are not indicated on Drawings.

          - Electrical Characteristics:

            - Horsepower: <Insert horsepower>.

            - Volts: [120] [208] [230] [460] <Insert value>.

            - Phase: [Single] [Poly].

            - Hertz: 60.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

        - Filters:

Retain "Polyurethane Foam" or "(Flat, Nonpleated) (Pleated) Glass Fiber" Subparagraph below, or both. Indicate filter type in an Air Terminal Unit Schedule on Drawings if all units are not filtered identically. LEED 2009 IEQ Prerequisite 1 and LEED v4 EQ Prerequisite "Minimum Indoor Air Quality Performance" require compliance with ASHRAE 62.1 (2007 and 2010 versions, respectively), which requires a MERV rating of 6 or higher for service to occupied spaces. LEED 2009 IEQ Credit 5 and LEED v4 IEQ Credit "Enhanced Indoor Air Quality Strategies" require MERV 13 or higher. Confirm availability with manufacturers. Not all manufacturers offer each option.

          - Polyurethane Foam: [MERV 3] <Insert value>. Minimum efficiency reporting value and average arrestance is in accordance with ASHRAE 52.2.

          - [Flat, Nonpleated] [Pleated] Glass Fiber: Factory-fabricated, self-supported disposable air filter with holding frames. Provide [MERV 6] [MERV 13] <Insert value> filter with minimum efficiency reporting value is to be in accordance with ASHRAE 52.2.

        - Attenuator Section: Casing material and thickness matching associated air terminal unit casing. Provide [absorptive] [packless] attenuator integral with the [plenum inlet] [and] [discharge outlet] of the air terminal unit, of noise transmission loss performance as required in schedules on Drawings.

Retain "Hydronic Heating Coils" or "Electric-Resistance Heating Coils" Paragraph below if heating coil is required. Verify coil location availability with manufacturer. Electric coils are typically only located in the discharge-air outlet airstream while hydronic heating coils may be located in either the plenum air inlet or discharge-air outlet airstreams. Coordinate retained coils with manufacturers.

        - Hydronic Heating Coils: Copper tube, with mechanically bonded aluminum fins spaced no closer than [0.1 inch (2.5 mm)] [0.08 inch (2.0 mm)]. Include manual air vent and drain valve. Locate coil in [plenum air inlet] [discharge-air outlet] airstream. Provide hydronic heating coils for air terminal units scheduled on Drawings.

        - Electric-Resistance Heating Coils: Nickel-chromium heating wire, free of expansion noise and hum, mounted in ceramic inserts in a galvanized-steel housing; with primary automatic, and secondary manual, reset thermal cutouts. Terminate elements in stainless steel, machine-staked terminals secured with stainless steel hardware. Locate coil in discharge-air outlet airstream. Provide electric-resistance heating coils for air terminal units scheduled on Drawings.

Retain one of first two subparagraphs below.

          - Stage(s): [One] [Two] [Three].

          - SCR controlled.

          - Access door interlocked disconnect switch.

          - Downstream air temperature sensor with local connection to override discharge-air temperature to not exceed a maximum temperature set point (adjustable).

Retain applicable subparagraphs below.

          - Nickel chrome 80/20 heating elements.

          - Airflow switch for proof of airflow.

          - Fan interlock contacts.

          - Fuses in terminal box for overcurrent protection (for coils of more than 48 A).

          - Pneumatic-electric switches and relays.

          - Magnetic contactor for each step of control (for three-phase coils).

        - Factory-Mounted and -Wired Controls: Electrical components mounted in control box with removable cover. Incorporate single-point electrical connection to power source.

          - Control Transformer: Factory mounted for control voltage on electric and electronic control units with terminal strip in control box for field wiring of thermostat and power source.

          - Wiring Terminations: Fan and controls to terminal strip. Terminal lugs will match quantities, sizes, and materials of branch-circuit conductors. Enclose terminal lugs in terminal box that is sized in accordance with NFPA 70.

          - Disconnect Switch: Factory-mounted fuse type.

        - Control Panel Enclosure: NEMA 250, Type 1, with access panel sealed from airflow and mounted on side of unit.

        - Electric Controls:

          - Electric Damper Actuator: 24 V, [spring-return open] [spring-return closed] [fail in last position].

          - Electric Thermostat: Wall-mounted electronic type with clock display, temperature display in Fahrenheit and Celsius, and space temperature set point.

          - Air Volume Controls: Pressure-dependent volume controls with field-adjustable minimum and maximum position stops.

        - Electronic Controls:

          - Electronic Damper Actuator: 24 V, [spring-return open] [spring-return closed] [capacitor-discharge-return open] [capacitor-discharge-return closed] [fail in last position].

          - Electronic Thermostat: Wall-mounted electronic type with temperature set-point display in Fahrenheit and Celsius.

          - Electronic Air Volume Controller: Pressure-independent analog electronic controller, factory calibrated and field adjustable to minimum and maximum air volumes; provides consistent airflow to the space in response to electronic thermostat signal while compensating for inlet static-pressure variations of up to 4 inches wg (1000 Pa); includes a multipoint velocity sensor at air inlet.

        - Pneumatic Controls:

          - Pneumatic Damper Actuator: [0 to 13 psig (0 to 90 kPa)] <Insert range> spring range.

          - Pneumatic Thermostat: Wall-mounted pneumatic-type, [direct acting] [reverse acting] [direct or reverse acting as indicated on Drawings], with appropriate mounting hardware.

          - Pneumatic Air Volume Controller: Factory calibrated and field adjustable to minimum and maximum air volumes; provides consistent airflow to the space in response to pneumatic thermostat signal while compensating for inlet static-pressure variations of up to 4 inches wg (1000 Pa); includes a multipoint velocity sensor at air inlet.

        - Direct Digital Controls:

Retain "Terminal Unit Controller" and "Room Sensor" and delete "Terminal Unit Controller, Section 230923" subparagraphs below if controllers and room sensors are to be furnished by the air terminal unit manufacturer. Delete "Terminal Unit Controller" and "Room Sensor" and retain "Terminal Unit Controller, Section 230923" subparagraphs if controllers, actuators, and sensors are provided under Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Terminal Unit Controller: Pressure-independent, VAV controller with integrated actuator and electronic airflow transducer with multipoint velocity sensor at air inlet, factory calibrated to minimum and maximum air volumes.

First four subparagraphs below are optional features.

            - Occupied and unoccupied operating mode.

            - Remote reset of airflow or temperature set points.

            - Adjusting and monitoring with portable terminal.

            - Communication with temperature-control system specified in Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Room Sensor: Wall mounted with[ temperature set-point adjustment and] access for connection of portable operator terminal.

          - Terminal Unit Controller, Section 230923: Controller is to be factory mounted and wired by air terminal manufacturer; unit controllers, actuators, and room sensors are to be furnished under Section 230923 "Direct Digital Control (DDC) System for HVAC."

        - Control Sequence: See [Section 230993.11 "Sequence of Operation for HVAC"] [Drawings] for control sequences.

      - SERIES FAN-POWERED AIR TERMINAL UNITS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Volume-damper assembly and centrifugal fan in series arrangement inside unit casing with control components inside a protective metal shroud.

Subparagraphs below are optional features. If retaining either or both options, indicate location of each configuration on Drawings or in schedule on Drawings.

          - Designed for quiet operation.

          - Low-profile design.

        - Casing: Minimum [20-gauge-] [22-gauge-] thick galvanized steel.

Verify, with air terminal unit manufacturer, availability of casing liner.

          - Casing Liner: Comply with requirements in "Casing Liner" Article below for ["Casing Liner, Fibrous Glass" Paragraph] ["Casing Liner, Flexible Elastomeric" Paragraph] [with "Antimicrobial Erosion-Resistant Coating" Subparagraph] [with "Foil-Faced Liner" Subparagraph] [with "Solid Metal Liner" Subparagraph] [with "Perforated Metal Liner" Subparagraph] [with "Specialty Liner" Subparagraph].

          - Air Inlets: Round stub connections or S-slip and drive connections for duct attachment.

          - Air Outlet: S-slip and drive connections.

          - Access: Removable panels for access to parts requiring service, adjustment, or maintenance; with airtight gasket and quarter-turn latches.

          - Fan: Forward-curved centrifugal.

        - Volume Damper: Galvanized steel with flow-sensing ring and peripheral gasket and self-lubricating bearings.

Leakage rates in "Maximum Damper Leakage" Subparagraph below vary among manufacturers and with pressure rating. Verify with manufacturers.

          - Maximum Damper Leakage: AHRI 880 rated, [1] [2] percent of nominal airflow at [3-inch wg (750-Pa)] <Insert value> inlet static pressure.

        - Velocity Sensors: Multipoint array with velocity sensors in air inlet.

        - Fan Motor:

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Type: [Permanent-split capacitor with SCR for speed adjustment] [Electronically commutated motor].

          - Fan-Motor Assembly Isolation: Rubber isolators.

          - Enclosure: [Open dripproof] [Totally enclosed, fan cooled] <Insert type>.

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design" and "Service Factor" subparagraphs below if options are available from equipment manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements. Verify enclosure types with manufacturer of specified equipment.

          - Enclosure Materials: [Cast iron] <Insert material>.

          - Motor Bearings: <Insert requirements>.

          - Unusual Service Conditions:

            - Ambient Temperature: <Insert deg F (deg C)>.

            - Altitude: <Insert feet (m)> above sea level.

Retain first subparagraph below if application requires this rating.

            - High humidity.

            - <Insert conditions>.

          - Efficiency: Premium efficient as defined by NEMA MG-1.

          - NEMA Design: <Insert designation>.

          - Service Factor: <Insert value>.

          - Motor Speed: [Single speed] [Variable speed].

            - Speed Control: Infinitely adjustable with pneumatic-electric and electronic controls.

Retain "Electrical Characteristics" Subparagraph below if characteristics are not indicated on Drawings.

          - Electrical Characteristics:

            - Horsepower: <Insert horsepower>.

            - Volts: [120] [208] [230] [460] <Insert value>.

            - Phase: [Single] [Poly].

            - Hertz: 60.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

        - Filters:

Retain "Polyurethane Foam" or "(Flat, Nonpleated) (Pleated) Glass Fiber" Subparagraph below, or both. Indicate filter type in an Air Terminal Unit Schedule on Drawings if all units are not filtered identically. Two-inch- (50-mm-) thick foam is unavailable. LEED 2009 IEQ Prerequisite 1 and LEED v4 EQ Prerequisite "Minimum Indoor Air Quality Performance" require compliance with ASHRAE 62.1 (2007 and 2010 versions, respectively), which requires a MERV rating of 6 or higher for service to occupied spaces. LEED 2009 IEQ Credit 5 and LEED v4 IEQ Credit "Enhanced Indoor Air Quality Strategies" require MERV 13 or higher. Insert values appropriate to Project sustainability goals.

          - Polyurethane Foam: [MERV 3] <Insert value>. Minimum efficiency reporting value and average arrestance in accordance with ASHRAE 52.2.

          - [Flat, Nonpleated] [Pleated] Glass Fiber: Factory-fabricated, self-supported disposable air filter with holding frames. Provide [MERV 6] [MERV 13] <Insert value> filters with minimum efficiency reporting value is to be in accordance with ASHRAE 522.

        - Attenuator Section: Casing material and thickness matching associated air terminal unit casing. Provide [absorptive] [packless] attenuator integral with the [plenum inlet] [and] [discharge outlet] of the air terminal unit, of noise transmission loss performance as required in schedules on Drawings.

Retain "Hydronic Heating Coils" or "Electric-Resistance Heating Coils" Paragraph below if heating coil is required. Coordinate retained coils with manufacturers.

        - Hydronic Heating Coils: Copper tube, with mechanically bonded aluminum fins spaced no closer than [0.1 inch (2.5 mm)] [0.08 inch (2.0 mm)]. Include manual air vent and drain valve. Locate coil in discharge outlet airstream. Provide hydronic heating coils for air terminal units scheduled on Drawings.

        - Electric-Resistance Heating Coils: Nickel-chromium heating wire, free of expansion noise and hum, mounted in ceramic inserts in a galvanized-steel housing; with primary automatic, and secondary manual, reset thermal cutouts. Terminate elements in stainless steel, machine-staked terminals secured with stainless steel hardware. Locate coil in discharge outlet airstream. Provide electric-resistance heating coils for air terminal units scheduled on Drawings.

Retain one of first two subparagraphs below.

          - Stage(s): [One] [Two] [Three].

          - SCR controlled.

          - Access door interlocked disconnect switch.

          - Downstream air temperature sensor with local connection to override discharge-air temperature to not exceed a maximum temperature set point (adjustable).

Retain applicable subparagraphs below.

          - Nickel chrome 80/20 heating elements.

          - Airflow switch for proof of airflow.

          - Fan interlock contacts.

          - Fuses in terminal box for overcurrent protection (for coils of more than 48 A).

          - Pneumatic-electric switches and relays.

          - Magnetic contactor for each step of control (for three-phase coils).

        - Factory-Mounted and -Wired Controls: Electrical components mounted in control box with removable cover. Incorporate single-point electrical connection to power source.

          - Control Transformer: Factory mounted for control voltage on electric and electronic control units with terminal strip in control box for field wiring of thermostat and power source.

          - Wiring Terminations: Fan and controls to terminal strip. Terminal lugs to match quantities, sizes, and materials of branch-circuit conductors. Enclose terminal lugs in terminal box that is sized in accordance with NFPA 70.

          - Disconnect Switch: Factory-mounted fuse type.

        - Control Panel Enclosure: NEMA 250, Type 1, with access panel sealed from airflow and mounted on side of unit.

        - Electric Controls:

          - Electric Damper Actuator: 24 V, [spring-return open] [spring-return closed] [fail in last position].

          - Electric Thermostat: Wall-mounted electronic type with clock display, temperature display in Fahrenheit and Celsius[, and space temperature set point].

          - Air Volume Controls: Pressure-dependent volume controls with field-adjustable minimum and maximum position stops.

        - Electronic Controls:

          - Electronic Damper Actuator: 24 V, [spring-return open] [spring-return closed] [capacitor-discharge-return open] [capacitor-discharge-return closed] [fail in last position].

          - Electronic Thermostat: Wall-mounted electronic type with temperature display in Fahrenheit and Celsius.

          - Electronic Air Volume Controller: Pressure-independent analog electronic controller, factory calibrated and field adjustable to minimum and maximum air volumes; provides consistent airflow to the space in response to electronic thermostat signal while compensating for inlet static-pressure variations of up to 4 inches wg (1000 Pa); includes a multipoint velocity sensor at air inlet.

        - Pneumatic Controls:

          - Pneumatic Damper Actuator: [0 to 13 psig (0 to 90 kPa)] <Insert range> spring range.

          - Pneumatic Thermostat: Wall-mounted, pneumatic type, [direct acting] [and] [reverse acting], with appropriate mounting hardware.

          - Pneumatic Air Volume Controller: Factory calibrated and field adjustable to minimum and maximum air volumes; provides consistent airflow to the space in response to pneumatic thermostat while compensating for inlet static-pressure variations of up to 4 inches wg (1000 Pa); includes a multipoint velocity sensor at air inlet.

        - Direct Digital Controls:

Retain "Terminal Unit Controller" and "Room Sensor" and delete "Terminal Unit Controller, Section 230923" subparagraphs below if controllers and room sensors are to be furnished by the air terminal unit manufacturer. Delete "Terminal Unit Controller" and "Room Sensor" and retain "Terminal Unit Controller, Section 230923" subparagraphs if controllers, actuators, and sensors are provided under Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Terminal Unit Controller: Pressure-independent, VAV controller and integrated actuator, and electronic airflow transducer with multipoint velocity sensor at air inlet, factory calibrated to minimum and maximum air volumes.

Retain applicable subparagraphs below.

            - Occupied and unoccupied operating mode.

            - Remote reset of airflow or temperature set points.

            - Adjusting and monitoring with portable terminal.

            - Communication with temperature-control system specified in Section 230923 "Instrumentation and Control for HVAC."

          - Room Sensor: Wall mounted with[ temperature set-point adjustment and] access for connection of portable operator terminal.

          - Terminal Unit Controller, Section 230923: Controller is to be factory mounted and wired by air terminal unit manufacturer; unit controller, actuators, and room sensors are to be furnished under Section 230923 "Direct Digital Control (DDC) for HVAC".

        - Control Sequence: See [Section 230993.11 "Sequence of Operation for HVAC"] [Drawings] for control sequences.

      - DUAL-DUCT AIR TERMINAL UNITS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: [Mixing] [and] [nonmixing] with two volume dampers inside unit casing with mixing attenuator section and control components inside a protective metal shroud.

        - Casing: Minimum [20-gauge-] [22-gauge-] thick galvanized steel.

Verify, with air terminal unit manufacturer, availability of casing liner.

          - Casing Liner: Comply with requirements in "Casing Liner" Article below for ["Casing Liner, Fibrous Glass" Paragraph] ["Casing Liner, Flexible Elastomeric" Paragraph] [with "Antimicrobial Erosion-Resistant Coating" Subparagraph] [with "Foil-Faced Liner" Subparagraph] [with "Solid Metal Liner" Subparagraph] [with "Perforated Metal Liner" Subparagraph] [with "Specialty Liner" Subparagraph].

          - Air Inlets: Round stub connections or S-slip and drive connections for duct attachment.

          - Air Outlet: S-slip and drive connections.

          - Access: Removable panels for access to parts requiring service, adjustment, or maintenance; with airtight gasket.

        - Volume Damper: Galvanized steel with peripheral gasket and self-lubricating bearings.

Leakage rates in "Maximum Damper Leakage" Subparagraph below vary widely among manufacturers and with pressure rating. Insert values based on availability of manufacturer products.

          - Maximum Damper Leakage: AHRI 880 rated, <Insert number> percent of nominal airflow at [3-inch wg (750-Pa)] <Insert value> inlet static pressure.

        - Velocity Sensors: Multipoint array with velocity sensors in each air inlet and air outlet.

        - Attenuator Section: Casing material and thicknesses matching associated air terminal unit casing. Provide [absorptive] [packless] attenuator integral with the air terminal unit, of noise transmission loss performance as required in schedules on Drawings.

        - Electric Controls:

          - Electric Damper Actuator, Hot Deck: 24 V, [spring-return open] [spring-return closed] [fail in last position].

          - Electric Damper Actuator, Cold Deck: 24 V, [spring-return open] [spring-return closed] [fail in last position].

          - Electric Thermostat: Wall-mounted electronic type with clock display, temperature display in Fahrenheit and Celsius, and space temperature set point.

          - Air Volume Controls: Pressure-dependent volume controls with field-adjustable minimum and maximum position stops.

        - Electronic Controls:

          - Electronic Damper Actuator, Hot Deck: 24 V, [spring-return open] [spring-return closed] [capacitor-discharge-return open] [capacitor-discharge-return closed] [fail in last position].

          - Electronic Damper Actuator, Cold Deck: 24 V, [spring- return open] [spring- return closed] [capacitor- discharge- return open] [capacitor- discharge- return closed] [fail in last position].

          - Electronic Thermostat: Wall-mounted electronic type with temperature set-point display in Fahrenheit and Celsius.

          - Electronic Air Volume Controller: Pressure-independent analog electronic controller, factory calibrated and field adjustable to minimum and maximum air volumes; provides consistent airflow to the space in response to electronic thermostat signal while compensating for inlet static-pressure variations of up to 4 inches wg (1000 Pa); includes a multipoint velocity sensor at each air inlet.

        - Pneumatic Controls:

          - Pneumatic Damper Actuator: [0 to 13 psig (0 to 90 kPa)] <Insert range> spring range.

          - Pneumatic Thermostat: Wall-mounted pneumatic type with appropriate mounting hardware.

          - Pneumatic Air Volume Controller: Factory calibrated and field adjustable to minimum and maximum air volumes; provides consistent airflow to the space in response to pneumatic thermostat signal while compensating for inlet static-pressure variations of up to 4 inches wg (1000 Pa); includes a multipoint velocity sensor at each air inlet.

Retain "Terminal Unit Controller" and "Room Sensor" and delete "Terminal Unit Controller, Section 230923" subparagraphs below if controllers and room sensor are to be furnished by the air terminal unit manufacturer. Delete "Terminal Unit Controller" and "Room Sensor" and retain "Terminal Unit Controller, Section 230923" subparagraphs if controllers and sensors are provided under Section 230923 "Direct Digital Control (DDC) System for HVAC."

        - Terminal Unit Controller: Pressure-independent, VAV controller with electronic airflow transducer with multipoint velocity sensor at air inlet, factory calibrated to minimum and maximum air volumes.

Subparagraphs below are optional features.

          - Occupied and unoccupied operating mode.

          - Remote reset of airflow or temperature set points.

          - Adjusting and monitoring with portable terminal.

          - Communication with temperature-control system specified in Section 230923 "Direct Digital Control (DDC) System for HVAC."

        - Room Sensor: Wall mounted with [temperature set-point adjustment and ]access for connection of portable operator terminal.

        - Terminal Unit Controller, Section 230923: Controllers and actuators are to be factory mounted and wired by air terminal manufacturer; unit controller, actuators, and room sensors are to be furnished under Section 230923 "Direct Digital Control (DDC) System for HVAC."

        - Control Sequence: See [Section 230993.11 "Sequence of Operation for HVAC"] [Drawings] for control sequences.

      - INDUCTION AIR TERMINAL UNITS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Primary volume-damper and venturi assembly inside unit casing with mechanical induction damper mounted on casing and control components inside a protective metal shroud.

        - Casing: Minimum 22-gauge-thick galvanized steel.

Verify, with air terminal unit manufacturer, availability of casing liner.

          - Casing Liner: Comply with requirements in "Casing Liner" Article below for ["Casing Liner, Fibrous Glass" Paragraph] ["Casing Liner, Flexible Elastomeric" Paragraph] [with "Antimicrobial Erosion-Resistant Coating" Subparagraph] [with "Foil-Faced Liner" Subparagraph] [with "Solid Metal Liner" Subparagraph] [with "Perforated Metal Liner" Subparagraph] [with "Specialty Liner" Subparagraph].

          - Air Inlet: Round stub connection for duct attachment.

          - Air Outlet: S-slip and drive connections[, size matching inlet size].

          - Access: Removable panels for access to parts requiring service, adjustment, or maintenance; with airtight gasket.

          - Fan: Forward-curved centrifugal.

        - Primary Volume Damper: Galvanized steel with peripheral gasket and self-lubricating bearings.

Leakage rates in "Maximum Damper Leakage" Subparagraph below vary among manufacturers and with pressure rating. Insert values based on availability of manufacturer products.

          - Maximum Damper Leakage: AHRI 880 rated, <Insert number> percent of nominal airflow at [3-inch wg (750-Pa)] <Insert value> inlet static pressure.

        - Induction Damper: Galvanized-steel, multiblade assembly with self-lubricating bearings.

Retain "Hydronic Heating Coils" or "Electric-Resistance Heating Coils" Paragraph below if heating coil is required. Manufacturers do not offer each option. Confirm availability with manufacturers.

        - Hydronic Heating Coils: Copper tube, with mechanically bonded aluminum fins spaced no closer than [0.1 inch (2.5 mm)] [0.08 inch (2.0 mm)]. Include manual air vent and drain valve. Provide hydronic heating coils for air terminal units scheduled on Drawings.

        - Electric-Resistance Heating Coils: Nickel-chromium heating wire, free of expansion noise and hum, mounted in ceramic inserts in a galvanized-steel housing; with primary automatic, and secondary manual, reset thermal cutouts. Terminate elements in stainless steel, machine-staked terminals secured with stainless steel hardware. Provide electric-resistance heating coils for air terminal units scheduled on Drawings.

Retain one of first two subparagraphs below.

          - Stage(s): [One] [Two] [Three].

          - SCR controlled.

          - Access door interlocked disconnect switch.

          - Downstream air temperature sensor with local connection to override discharge-air temperature to not exceed a maximum temperature set point (adjustable).

Retain applicable subparagraphs below.

          - Nickel chrome 80/20 heating elements.

          - Airflow switch for proof of airflow.

          - Fan interlock contacts.

          - Fuses in terminal box for overcurrent protection (for coils of more than 48 A).

          - Pneumatic-electric switches and relays.

          - Magnetic contactor for each step of control (for three-phase coils).

        - Electric Controls:

          - Electric Damper Actuator: 24 V, [spring-return open] [spring-return closed] [fail in last position].

          - Electric Thermostat: Wall-mounted electronic type with clock display, temperature display in Fahrenheit and Celsius[, and space temperature set point].

          - Air Volume Controls: Pressure-dependent volume controls with field-adjustable minimum and maximum position stops.

        - Electronic Controls:

          - Electronic Damper Actuator: 24 V, powered open, [spring-return open] [spring-return closed] [capacitor-discharge-return open] [capacitor-discharge-return closed] [fail in last position].

          - Electronic Thermostat: Wall-mounted electronic type with temperature set-point display in Fahrenheit and Celsius.

          - Electronic Air Volume Controller: Pressure-independent analog electronic controller, factory calibrated and field adjustable to minimum and maximum air volumes; provides consistent airflow to the space in response to electronic thermostat signal while compensating for inlet static-pressure variations of up to 4 inches wg (1000 Pa); includes a multipoint velocity sensor at air inlet.

        - Pneumatic Controls:

          - Pneumatic Damper Actuator: [0 to 13 psig (0 to 90 kPa)] <Insert range> spring range.

          - Pneumatic Thermostat: Wall-mounted pneumatic type, [direct acting] [reverse acting] [direct or reverse acting as indicated on Drawings], with appropriate mounting hardware.

          - Pneumatic Air Volume Controller: Factory calibrated and field adjustable to minimum and maximum air volumes; provides consistent airflow to the space in response to pneumatic thermostat while compensating for inlet static-pressure variations of up to 4 inches wg (1000 Pa); includes a multipoint velocity sensor at air inlet.

        - Direct Digital Controls:

Retain "Terminal Unit Controller" and "Room Sensor" and delete "Terminal Unit Controller, Section 230923" subparagraphs below if controllers and room sensor are to be furnished by the air terminal unit manufacturer. Delete "Terminal Unit Controller" and "Room Sensor" and retain "Terminal Unit Controller, Section 230923" subparagraphs if controllers and sensors are provided under Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Terminal Unit Controller: Pressure-independent, VAV controller with integrated actuator, and electronic airflow transducer with multipoint velocity sensor at air inlet, factory calibrated to minimum and maximum air volumes.

First four subparagraphs below are optional features.

            - Occupied and unoccupied operating mode.

            - Remote reset of airflow or temperature set points.

            - Adjusting and monitoring with portable terminal.

            - Communication with temperature-control system specified in Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Room Sensor: Wall mounted with temperature set-point adjustment and access for connection of portable operator terminal.

          - Terminal Unit Controller, Section 230923: Controller and actuators are to be factory mounted and wired by air terminal unit manufacturer; unit controller, actuator, and room sensors are to be furnished under Section 230923 "Direct Digital Control (DDC) System for HVAC."

        - Control Sequence: See [Section 230993.11 "Sequence of Operation for HVAC"] [Drawings] for control sequences.

      - DIFFUSER-TYPE AIR TERMINAL UNITS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

In "Description" Paragraph below, a limited number of manufacturers offer the electric heater option. Confirm availability with manufacturers.

        - Description: Volume-damper, diffuser, controller assembly[ and inlet electric heater] and wall-mounted temperature-sensing device[ with master-drone capability].

        - Volume Damper: [Galvanized steel] <Insert material> with peripheral gasket and self-lubricating bearings.

In "Diffuser" Paragraph below, not all manufacturers offer each material or finish options indicated. Confirm availability with manufacturers.

        - Diffuser: [Galvanized steel] [Aluminum] <Insert material> with [white] [powder coat] [or] [baked-enamel finish] <Insert color and finish>.

In "Wall-Mounted Temperature Sensor/Controller" Paragraph below, some manufacturers use wireless radio frequency technology; some use wired technology; and some offer both.

        - Wall-Mounted Temperature Sensor/Controller:

          - Digital display LCD wall-mounted controller.

          - Intuitive user operation.

          - Controller settings retained during power loss.

In "Communication Interface" Subparagraph below, manufacturers generally do not offer all options. Confirm availability with manufacturers.

          - Communication Interface: [BACnet] [Modbus] <Insert protocol> compatible for integration with building automation system.

          - Operational features:

            - Set-point indication.

            - Set-point adjustment.

Retain first subparagraph below for heating and cooling units.

            - Changeover temperature indication.

            - Changeover temperature set-point adjustment.

            - Minimum damper position adjustment for ventilation air.

Availability of items in "Accessories" Paragraph below varies with manufacturer. Confirm availability with manufacturers.

        - Accessories:

          - Modular plenum-rated plug-in cables for interconnecting master-drone diffusers.

          - Blank-off panels.

          - Pressure-relief ring.

          - 24 V ac transformer/power supply for master-drone configurations.

          - Plenum-rated, plug-in, diffuser interconnection cables for master-drone configurations.

          - Diffuser back-pan insulation.

          - T-bar mounting frame.

          - Plaster ceiling frame.

        - Control Sequence: See [Section 230993.11 "Sequence of Operation for HVAC"] [Drawings] for control sequences.

      - BALANCING TERMINAL UNITS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Manually operated volume-damper assembly with locking mechanism inside unit casing with multipoint, center-averaging velocity sensors[ for installation above a ceiling].

        - Casing: Minimum 22-gauge-thick galvanized steel.

          - Leakage: Maximum 2 percent of nominal airflow at 1.5-inch wg (375-Pa) static pressure.

          - Air Inlet: Round stub connection for duct attachment.

          - Air Outlet: S-slip and drive connections.

Verify, with air terminal unit manufacturer, availability of casing liner.

          - Casing Liner: Comply with requirements in "Casing Liner" Article below for ["Casing Liner, Fibrous Glass" Paragraph] ["Casing Liner, Flexible Elastomeric" Paragraph] [with "Antimicrobial Erosion-Resistant Coating" Subparagraph] [with "Foil-Faced Liner" Subparagraph] [with "Solid Metal Liner" Subparagraph] [with "Perforated Metal Liner" Subparagraph] [with "Specialty Liner" Subparagraph].

        - Volume Damper: Galvanized steel with peripheral gasket and self-lubricating bearings.

Leakage rates in "Maximum Damper Leakage" Subparagraph below vary among manufacturers and with pressure rating.

          - Maximum Damper Leakage: AHRI 880 rated, [2] <Insert number> percent of nominal airflow at [3-inch wg (750-Pa)] <Insert value> inlet static pressure.

      - PRESSURE-CONTROL TERMINAL UNITS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Volume-damper assembly inside unit casing with control components inside a protective metal shroud, designed to regulate duct pressure via throttling to control discharge pressure in a variable volume system.

        - Casing: Minimum 22-gauge-thick galvanized steel.

Verify, with air terminal unit manufacturer, availability of casing liner.

          - Casing Liner: Comply with requirements in "Casing Liner" Article below for ["Casing Liner, Fibrous Glass" Paragraph] ["Casing Liner, Flexible Elastomeric" Paragraph] [with "Antimicrobial Erosion-Resistant Coating" Subparagraph] [with "Foil-Faced Liner" Subparagraph] [with "Solid Metal Liner" Subparagraph] [with "Perforated Metal Liner" Subparagraph] [with "Specialty Liner" Subparagraph].

          - Air Inlet: Round stub connection for duct attachment.

          - Air Outlet: S-slip and drive connections.

          - Access: Removable panels for access to diverting damper and other parts requiring service, adjustment, or maintenance; with airtight gasket.

Retain "Diverter Assembly" Subparagraph below for units with pneumatic volume regulators.

          - Damper Assembly: Damper, shaft, and heavy-duty self-lubricating bearings.

        - Attenuator Section: Construction materials and thicknesses matching associated air terminal unit casing. Provide [absorptive] [packless] attenuator integral with the air terminal unit, of noise transmission loss performance as required in schedules on Drawings.

        - Direct Digital Controls:

Retain "Terminal Unit Controller" and "Discharge Static Pressure Sensor" and delete "Terminal Unit Controller, Section 230923" subparagraphs below if controllers and actuators are to be furnished by the air terminal unit manufacturer. Delete "Terminal Unit Controller" and retain "Terminal Unit Controller, Section 230923" subparagraphs if controllers and actuators are provided under Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Terminal Unit Controller: Pressure-independent controller and integrated [spring-return open] [spring-return closed] [capacitor-discharge-return open] [capacitor-discharge-return closed] [fail-in-last-position] actuator, and electronic airflow transducer with multipoint velocity sensor at air inlet, factory calibrated to minimum and maximum discharge pressures.

First four subparagraphs below are optional features.

            - Occupied and unoccupied operating mode.

            - Remote reset of discharge pressure set points.

            - Adjusting and monitoring with portable terminal.

            - Communication with temperature-control system specified in Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Discharge Static Pressure Sensor: Discharge static pressure sensor to maintain constant static pressure within [5] <Insert number> percent of set point.

          - Terminal Unit Controller and Discharge Static Pressure Sensor, Section 230923: Controller, actuator, and sensor to be factory mounted and wired by air terminal manufacturer; unit controller, actuator, and sensor are to be furnished under Section 230923 "Direct Digital Control (DDC) System for HVAC."

        - Control Sequence: See [Section 230993.11 "Sequence of Operation for HVAC"] [Drawings] for control sequences.

      - CRITICAL ENVIRONMENT CONTROL VALVE

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Volume-damper or venturi assembly inside a unit casing with control components inside a protective metal shroud, for general exhaust applications or for exhaust applications where pressurization control via exhaust and supply airflow control is desired and airstream corrosion and contamination may be a concern.

        - Casing:

Not all manufacturers offer each type of material in "Material" Subparagraph below. Also, manufacturers may use other materials for surfaces outside of contact with the airstream. Materials listed below are for those in contact with airstream. Confirm availability with manufacturers.

          - Material: [Type 304 stainless steel] [or] [Type 316 stainless steel] [Minimum 22-gauge galvanized steel with phenolic coating] <Insert material>.

Retain first two paragraphs below, depending on selected manufacturers. Confirm availability with manufacturers. Phoenix uses the approach in first paragraph below. Anemostat, Price, and Tuttle & Bailey use the approach in second paragraph below. Retain both paragraphs to allow either approach.

        - [Airflow Metering, Option: Calibrated shaft position with self-adjusting, spring-loaded cone.]

        - [Sensors, Option: Multipoint,] [Type 316 stainless steel] <Insert material> [, removable].

        - Direct Digital Controls:

          - Terminal Unit Controller, Section 230923: Controller is to be factory mounted and wired by air terminal manufacturer; unit controller, actuators, and room sensors are to be furnished under Section 230923 "Direct Digital Control (DDC) System for HVAC."

        - Control Sequence: See [Section 230993.11 "Sequence of Operation for HVAC"] [Drawings] for control sequences.

      - UNDERFLOOR AIR DISTRIBUTION TERMINAL UNITS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Volume-damper assembly and fan in series arrangement inside low-profile unit casing with control components inside a protective metal shroud within a raised access floor. Design configuration for [pressurized floor cavity supply] [and] [ducted air supply].

        - Casing: Minimum [20-gauge-] [22-gauge-] thick galvanized steel.

          - Integral floor discharge diffusers.

          - Mixing damper.

          - VAV throttling damper.

          - Leveling feet.

Verify, with air terminal unit manufacturer, availability of casing liner.

          - Casing Liner: Comply with requirements in "Casing Liner" Article below for ["Casing Liner, Fibrous Glass" Paragraph] ["Casing Liner, Flexible Elastomeric" Paragraph] [with "Antimicrobial Erosion-Resistant Coating" Subparagraph] [with "Foil-Faced Liner" Subparagraph] [with "Solid Metal Liner" Subparagraph] [with "Perforated Metal Liner" Subparagraph] [with "Specialty Liner" Subparagraph].

          - Air Outlet: S-slip and drive connections.

          - Access: Removable panels on top of casing, for access to parts requiring service, adjustment, or maintenance; with airtight gasket and quarter-turn latches.

Not all manufacturers offer the options indicated in "Fan" Subparagraph below. Confirm availability with manufacturers.

          - Fan: Forward-curved centrifugal [in double blower configuration] [with double blowers as scheduled].

        - Volume Damper: Galvanized steel with flow-sensing ring and peripheral gasket and self-lubricating bearings.

Leakage rates in "Maximum Damper Leakage" Subparagraph below vary among manufacturers and with pressure rating. Confirm availability with manufacturers.

          - Maximum Damper Leakage: AHRI 880 rated, [1] [2] percent of nominal airflow at [3-inch wg (750-Pa)] <Insert value> inlet static pressure.

          - Damper Position: Normally [open] [closed].

        - Velocity Sensors: Multipoint array with velocity sensors in air inlets.

        - Motor:

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Type: [Permanent-split capacitor with SCR for speed adjustment] [Electronically commutated motor].

          - Fan-Motor Assembly Isolation: Rubber isolators.

          - Enclosure: [Open dripproof] [Totally enclosed, fan cooled] <Insert type>.

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from equipment manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements. Verify enclosure types with manufacturer of specified equipment.

          - Enclosure Materials: [Cast iron] <Insert material>.

          - Motor Bearings: <Insert requirements>.

          - Unusual Service Conditions:

            - Ambient Temperature: <Insert deg F (deg C)>.

            - Altitude: <Insert feet (m)> above sea level.

Retain first subparagraph below if application requires this rating.

            - High humidity.

            - <Insert conditions>.

          - Efficiency: Premium efficient.

          - NEMA Design: <Insert designation>.

          - Service Factor: <Insert value>.

          - Motor Speed: [Single speed] [Variable speed].

Retain "Electrical Characteristics" Subparagraph below if characteristics are not indicated on Drawings.

          - Electrical Characteristics:

            - Horsepower: <Insert horsepower>.

            - Volts: [120] [208] [230] [460] <Insert value>.

            - Phase: [Single] [Poly].

            - Hertz: 60.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

Retain "Hydronic Heating Coils" or "Electric-Resistance Heating Coils" Paragraph below if heating coil is required. Confirm availability with manufacturers.

        - Hydronic Heating Coils: Copper tube, with mechanically bonded aluminum fins spaced no closer than [0.1 inch (2.5 mm)] [0.08 inch (2.0 mm)]. Include manual air vent and drain valve. Locate coil in discharge outlet airstream. Provide hydronic heating coils for air terminal units scheduled on Drawings.

        - Electric-Resistance Heating Coils: Nickel-chromium heating wire, free of expansion noise and hum, mounted in ceramic inserts in a galvanized-steel housing; with primary automatic, and secondary manual, reset thermal cutouts. Terminate elements in stainless steel, machine-staked terminals secured with stainless steel hardware. Locate coil in discharge outlet airstream. Provide electric-resistance heating coils for air terminal units scheduled on Drawings.

Retain one of first two subparagraphs below.

          - Stage(s): [One] [Two] [Three].

          - SCR controlled.

          - Access door interlocked disconnect switch.

          - Downstream air temperature sensor with local connection to override discharge-air temperature to not exceed a maximum temperature set point (adjustable).

Retain applicable subparagraphs below.

          - Nickel chrome 80/20 heating elements.

          - Airflow switch for proof of airflow.

          - Fan interlock contacts.

          - Fuses in terminal box for overcurrent protection (for coils of more than 48 A).

          - Pneumatic-electric switches and relays.

          - Magnetic contactor for each step of control (for three-phase coils).

        - Factory-Mounted and -Wired Controls: Electrical components mounted in control box with removable cover. Incorporate single-point electrical connection to power source.

          - Control Transformer: Factory mounted for control voltage on electric and electronic control units with terminal strip in control box for field wiring of thermostat and power source.

          - Wiring Terminations: Fan and controls to terminal strip. Verify terminal lugs match quantities, sizes, and materials of branch-circuit conductors. Enclose terminal lugs in terminal box that is sized in accordance with NFPA 70.

          - Disconnect Switch: Factory-mounted fuse type.

        - Control Panel Enclosure: NEMA 250, Type 1, with access panel sealed from airflow and mounted on side of unit.

Retain "Electronic Controls" or "Direct Digital Controls" Paragraphs below.

        - Electronic Controls:

          - Electronic Damper Actuator: 24 V, [spring-return open] [spring-return closed] [capacitor-discharge-return open] [capacitor-discharge-return closed] [fail in last position].

          - Electronic Thermostat: Wall-mounted electronic type with temperature set-point display in Fahrenheit and Celsius.

          - Electronic Air Volume Controller: Pressure-independent analog electronic controller, factory calibrated and field adjustable to minimum and maximum air volumes; provides consistent airflow to the space in response to electronic thermostat signal while compensating for inlet static-pressure variations of up to 4 inches wg (1000 Pa); includes a multipoint velocity sensor at air inlet.

        - Direct Digital Controls:

Retain "Terminal Unit Controller" and "Room Sensor" and delete "Terminal Unit Controller, Section 230923" subparagraphs below if controllers and room sensors are to be furnished by the air terminal unit manufacturer. Delete "Terminal Unit Controller" and "Room Sensor" and retain "Terminal Unit Controller, Section 230923" subparagraphs if controllers and sensors are provided under Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Terminal Unit Controller: Pressure-independent, VAV controller with integrated actuator and electronic airflow transducer with multipoint velocity sensor at air inlet, factory calibrated to minimum and maximum air volumes.

First four subparagraphs below are optional features.

            - Occupied and unoccupied operating mode.

            - Remote reset of airflow or temperature set points.

            - Adjusting and monitoring with portable terminal.

            - Communication with temperature-control system specified in Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Room Sensor: Set-point adjustment and access for connection of portable operator terminal.

          - Terminal Unit Controller, Section 230923: Controller is to be factory mounted and wired by air terminal manufacturer; unit controller, actuators, and room sensors are to be furnished under Section 230923 "Direct Digital Control (DDC) System for HVAC."

        - Control Sequence: See [Section 230993.11 "Sequence of Operation for HVAC"] [Drawings] for control sequences.

      - EXHAUST SINGLE-DUCT TERMINAL UNITS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Volume-damper assembly inside unit casing with control components inside a protective metal shroud, for exhaust applications where pressurization control via exhaust and supply airflow control is desired.

        - Casing: Minimum [22-gauge-] [20-gauge-] <Insert value> thick galvanized steel.

          - Air Inlet: Round stub connection or S-slip and drive connections for duct attachment.

          - Air Outlet: S-slip and drive connections[, size matching inlet size].

          - Access: Removable panels for access to parts requiring service, adjustment, or maintenance; with airtight gasket.

        - Volume Damper: Galvanized steel with peripheral gasket and self-lubricating bearings.

Leakage rates in "Maximum Damper Leakage" Subparagraph below vary among manufacturers and with pressure rating.

          - Maximum Damper Leakage: AHRI 880 rated, [1] [2] percent of nominal airflow at [3-inch wg (750-Pa)] <Insert value> inlet static pressure.

        - Attenuator Section: Casing material and thickness matching associated air terminal unit casing. Provide [absorptive] [packless] attenuator integral with the air terminal unit, of noise transmission loss performance as required in schedules on Drawings.

        - Electric Controls:

          - Damper Actuator: 24 V, [spring-return open] [spring-return closed] [fail in last position].

          - Air Volume Controls: Pressure-dependent volume controls with field-adjustable minimum and maximum position stops.

          - Differential Pressure Sensor: Wall-mounted type with set point.

        - Electronic Controls:

          - Damper Actuator: 24 V, [spring-return open] [spring-return closed] [capacitor-discharge-return open] [capacitor-discharge-return closed] [fail in last position].

          - Electronic Air Volume Controller: Pressure-independent analog electronic controller, factory calibrated and field adjustable to minimum and maximum air volumes; provides consistent airflow to the space in response to electronic thermostat signal while compensating for inlet static-pressure variations of up to 4 inches wg (1000 Pa); includes a multipoint velocity sensor at air inlet.

          - Differential Pressure Sensor: Wall-mounted electronic type with set-point display.

        - Direct Digital Controls:

Retain "Terminal Unit Controller" and "Room Sensor" and delete "Terminal Unit Controller, Section 230923" subparagraphs below if controllers and room sensor are to be furnished by the air terminal unit manufacturer. Delete "Terminal Unit Controller" and "Room Sensor" and retain "Terminal Unit Controller, Section 230923" subparagraphs if controllers and sensors are provided under Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Terminal Unit Controller: Pressure-independent, controller and integrated [spring-return open] [spring-return closed] [capacitor-discharge open] [capacitor-discharge-return closed] [fail-in-last-position] actuator, and electronic airflow transducer with multipoint velocity sensor at air inlet, factory calibrated to minimum and maximum air volumes.

First four subparagraphs below are optional features.

            - Occupied and unoccupied operating mode.

            - Remote reset of airflow or temperature set points.

            - Adjusting and monitoring with portable terminal.

            - Communication with temperature-control system specified in Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Room Sensor: Wall mounted with differential pressure set-point adjustment[ and access for connection of portable operator terminal].

          - Terminal Unit Controller, Section 230923: Controller is to be factory mounted and wired by air terminal manufacturer; unit controller, actuators, and room sensors are to be furnished under Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Damper Actuator: 24 V, [spring-return open] [spring-return closed] [capacitor-discharge-return open] [capacitor-discharge-return closed] [fail in last position].

        - Control Sequence: See [Section 230993.11 "Sequence of Operation for HVAC"] [Drawings] for control sequences.

      - DOAS, SERIES, FAN-POWERED AIR TERMINAL UNITS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Primary outside-air volume-damper assembly and fan in series arrangement inside unit casing, with control components inside a protective metal shroud, with chilled-water coil for sensible cooling.

In "Casing" Paragraph below, not all manufacturers offer each option. Confirm availability with manufacturers.

        - Casing: Minimum [20-gauge-] [22-gauge-] thick galvanized steel.

Verify, with air terminal unit manufacturer, availability of casing liner.

          - Casing Liner: Comply with requirements in "Casing Liner" Article below for ["Casing Liner, Fibrous Glass" Paragraph] ["Casing Liner, Flexible Elastomeric" Paragraph] [with "Antimicrobial Erosion-Resistant Coating" Subparagraph] [with "Foil-Faced Liner" Subparagraph] [with "Solid Metal Liner" Subparagraph] [with "Perforated Metal Liner" Subparagraph] [with "Specialty Liner" Subparagraph].

          - Air Inlet: Round stub connection or S-slip and drive connections for duct attachment.

          - Air Outlet: S-slip and drive connections[, size matching inlet size].

          - Access: Removable panels for access to parts requiring service, adjustment, or maintenance; with airtight gasket.

        - Volume Damper: Galvanized steel with peripheral gasket and self-lubricating bearings.

Leakage rates in "Maximum Damper Leakage" Subparagraph below vary among manufacturers and with pressure rating.

          - Maximum Damper Leakage: AHRI 880 rated, [1] [2] percent of nominal airflow at [3-inch wg (750-Pa)] <Insert value> inlet static pressure.

        - Velocity Sensors: Multipoint array with velocity inlet sensors.

        - Fan Motor:

          - Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

          - Type: [Permanent-split capacitor with SCR for speed adjustment] [Electronically commutated motor].

          - Fan-Motor Assembly Isolation: Rubber isolators.

          - Enclosure: [Open dripproof] [Totally enclosed, fan cooled] <Insert type>.

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from equipment manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements. Verify enclosure types with manufacturer of specified equipment.

          - Enclosure Materials: [Cast iron] <Insert material>.

          - Motor Bearings: <Insert requirements>.

          - Unusual Service Conditions:

            - Ambient Temperature: <Insert deg F (deg C)>.

            - Altitude: <Insert feet (m)> above sea level.

Retain first subparagraph below if application requires this rating.

            - High humidity.

            - <Insert conditions>.

          - Efficiency: Premium efficient as defined in NEMA MG-1.

          - NEMA Design: <Insert designation>.

          - Service Factor: <Insert value>.

          - Motor Speed: [Single speed] [Variable speed].

            - Speed Control: Infinitely adjustable with pneumatic-electric and electronic controls.

Retain "Electrical Characteristics" Subparagraph below if characteristics are not indicated on Drawings.

          - Electrical Characteristics:

            - Horsepower: <Insert horsepower>.

            - Volts: [120] [208] [230] [460] <Insert value>.

            - Phase: [Single] [Poly].

            - Hertz: 60.

            - Full-Load Amperes: <Insert value>.

            - Minimum Circuit Ampacity: <Insert value>.

            - Maximum Overcurrent Protection: <Insert amperage>.

        - Filters:

Retain "Polyurethane Foam," "(Flat, Nonpleated) (Pleated) Glass Fiber," or both subparagraphs below. Indicate filter type in an Air Terminal Unit Schedule on Drawings if all units are not filtered identically. LEED 2009 IEQ Prerequisite 1 and LEED v4 EQ Prerequisite "Minimum Indoor Air Quality Performance, require compliance with ASHRAE 62.1 (2007 and 2010 versions, respectively), which requires a MERV rating of 6 or higher for service to occupied spaces. LEED 2009 IEQ Credit 5 and LEED v4 IEQ Credit "Enhanced Indoor Air Quality Strategies" require MERV 13 or higher. Confirm availability with manufacturers. Not all manufacturers offer each option.

          - Polyurethane Foam: [MERV 3] <Insert value>. Minimum efficiency reporting value and average arrestance in accordance with ASHRAE 52.2.

          - [Flat, Nonpleated] [Pleated] Glass Fiber: Factory-fabricated, self-supported disposable air filter with holding frames. Provide [MERV 6] [MERV 13] <Insert value> filter with minimum efficiency reporting value in accordance with ASHRAE 52.2.

        - Attenuator Section: Casing material and thickness matching associated air terminal unit casing. Provide [absorptive] [packless] attenuator integral with the air terminal unit, of noise transmission loss performance as required in schedules on Drawings.

Retain "Hydronic Heating Coils" or "Electric-Resistance Heating Coils" Paragraph below if heating coil is required. Confirm availability with manufacturers.

        - Hydronic Heating Coils: Copper tube, with mechanically bonded aluminum fins spaced no closer than [0.1 inch (2.5 mm)] [0.08 inch (2.0 mm)]. Include manual air vent and drain valve. Provide hydronic heating coils for air terminal units scheduled on Drawings.

        - Electric-Resistance Heating Coils: Nickel-chromium heating wire, free of expansion noise and hum, mounted in ceramic inserts in a galvanized-steel housing; with primary automatic, and secondary manual, reset thermal cutouts. Terminate elements in stainless steel, machine-staked terminals secured with stainless steel hardware. Provide electric-resistance heating coils for air terminal units scheduled on Drawings.

Retain one of first two subparagraphs below.

          - Stage(s): [One] [Two] [Three].

          - SCR controlled.

          - Access door interlocked disconnect switch.

          - Downstream air temperature sensor with local connection to override discharge-air temperature to not exceed a maximum temperature set point (adjustable).

Retain applicable subparagraphs below.

          - Nickel chrome 80/20 heating elements.

          - Airflow switch for proof of airflow.

          - Fan interlock contacts.

          - Fuses in terminal box for overcurrent protection (for coils of more than 48 A).

          - Pneumatic-electric switches and relays.

          - Magnetic contactor for each step of control (for three-phase coils).

In "Hydronic Cooling Coils" Paragraph below, only some manufacturers offer moisture sensor option.

        - Hydronic Cooling Coils: Copper tube, with mechanically bonded aluminum fins spaced no closer than [0.1 inch (2.5 mm)] [0.08 inch (2.0 mm)]. Include manual air vent and drain valve. Locate cooling coils at plenum air inlet. Include galvanized-steel factory-installed drip tray [and moisture sensor ]for safety in cases where cooling coil temporarily experiences nondesign conditions.

        - Factory-Mounted and -Wired Controls: Electrical components mounted in control box with removable cover. Incorporate single-point electrical connection to power source.

          - Control Transformer: Factory mounted for control voltage on electric and electronic control units with terminal strip in control box for field wiring of thermostat and power source.

          - Wiring Terminations: Fan and controls to terminal strip. Terminal lugs to match quantities, sizes, and materials of branch-circuit conductors. Enclose terminal lugs in terminal box that is sized in accordance with NFPA 70.

          - Disconnect Switch: Factory-mounted fuse type.

        - Control Panel Enclosure: NEMA 250, Type 1, with access panel sealed from airflow and mounted on side of unit.

        - Electric Controls:

          - Electric Damper Actuator: 24 V, [spring-return open] [spring-return closed] [fail in last position].

          - Electric Thermostat: Wall-mounted electronic type with clock display, temperature display in Fahrenheit and Celsius, and space temperature set point.

          - Air Volume Controls: Pressure-dependent volume controls with field-adjustable minimum and maximum position stops.

        - Electronic Controls:

          - Electronic Damper Actuator: 24 V, [spring-return open] [spring-return closed] [capacitor-discharge-return open] [capacitor-discharge-return closed] [fail in last position].

          - Electronic Thermostat: Wall-mounted electronic type with temperature display in Fahrenheit and Celsius.

          - Electronic Air Volume Controller: Pressure-independent analog electronic controller, factory calibrated and field adjustable to minimum and maximum air volumes; provides consistent airflow to the space in response to electronic thermostat signal while compensating for inlet static-pressure variations of up to 4 inches wg (1000 Pa); includes a multipoint velocity sensor at air inlet.

        - Pneumatic Controls:

          - Pneumatic Damper Actuator: [0 to 13 psig (0 to 90 kPa)] <Insert range> spring range.

If retaining both direct- and reverse-acting thermostats, indicate location of each type on Drawings.

          - Pneumatic Thermostat: Wall-mounted, pneumatic type, [direct acting] [and] [reverse acting], with appropriate mounting hardware.

          - Pneumatic Air Volume Controller: Factory calibrated and field adjustable to minimum and maximum air volumes; provides consistent airflow to the space in response to pneumatic thermostat signal while compensating for inlet static-pressure variations of up to 4 inches wg (1000 Pa); includes a multipoint velocity sensor at air inlet.

        - Direct Digital Controls:

Retain "Terminal Unit Controller" and "Room Sensor" and delete "Terminal Unit Controller, Section 230923" subparagraphs below if controllers and room sensors are to be furnished by the air terminal unit manufacturer. Delete "Terminal Unit Controller" and "Room Sensor" and retain "Terminal Unit Controller, Section 230923" subparagraphs if controllers and sensors are provided under Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Terminal Unit Controller: Pressure-independent, VAV controller with integrated actuator and electronic airflow transducer with multipoint velocity sensor at air inlet, factory calibrated to minimum and maximum air volumes.

First four subparagraphs below are optional features.

            - Occupied and unoccupied operating mode.

            - Remote reset of airflow or temperature set points.

            - Adjusting and monitoring with portable terminal.

            - Communication with temperature-control system specified in Section 230923 "Direct Digital Control (DDC) System for HVAC."

          - Room Sensor: Wall mounted with temperature set-point adjustment and access for connection of portable operator terminal.

          - Terminal Unit Controller, Section 230923: Controller is to be factory mounted and wired by air terminal manufacturer; unit controller, actuators, and room sensors are to be furnished under Section 230923 "Direct Digital Control (DDC) System for HVAC."

Only some manufacturers offer sensors in "Cooling Coil Drip Pan Sensor" Subparagraph below Confirm availability with manufacturers.

          - Cooling Coil Drip Pan Sensor: Shuts off fan upon detection of moisture in drip pan.

        - Control Sequence: See [Section 230993.11 "Sequence of Operation for HVAC"] [Drawings] for control sequences.

      - CASING LINER

See Section 230713 "Duct Insulation" for applicable duct insulation and installation requirements for air terminal device application.

Sustainable design systems and compliance with ASHRAE/IES 90.1 require that duct insulation R-value comply with ASHRAE/IES 90.1 tables titled "Minimum Duct Insulation R-Value, Cooling and Heating Only Supply Ducts and Return Ducts" and "Minimum Duct Insulation R-Value, Combined Heating and Cooling Supply Ducts and Return Ducts." If using liner alone to suit thermal requirements, verify that material selected is available in thickness needed to provide thermal performance without jeopardizing other requirements.

Retain "Casing Liner, Fibrous Glass" or "Casing Liner, Flexible Elastomeric" Paragraph below.

        - Casing Liner, Fibrous Glass: Fibrous-glass duct liner, complying with ASTM C1071, NFPA 90A or NFPA 90B, and with NAIMA AH124.

          - Minimum Thickness: [1/2 inch (13 mm)] [3/4 inch (19 mm)] [1 inch (25 mm)].

Retain "Maximum Thermal Conductivity" Subparagraph below to require thermal conductivity exceeding the minimum requirements in ASTM C1071. Retaining subparagraph may create a restrictive proprietary specification.

            - Maximum Thermal Conductivity:

Option for thermal conductivity in first two subparagraphs below exceeds the values in ASTM C1071. If retaining, verify availability of performance with duct liner manufacturers.

              - Type I, Flexible: [0.27 Btu x in./h x sq. ft. x deg F (0.039 W/m x K)] <Insert value> at 75 deg F (24 deg C) mean temperature.

              - Type II, Rigid: [0.23 Btu x in./h x sq. ft. x deg F (0.033 W/m x K)] <Insert value> at 75 deg F (24 deg C) mean temperature.

Coating in "Antimicrobial Erosion-Resistant Coating" Subparagraph below is an optional feature for duct liners.

          - Antimicrobial Erosion-Resistant Coating: Apply to surface of liner that will form interior surface of duct to act as a moisture repellent and erosion-resistant coating. Antimicrobial compound is to be tested for efficacy by an NRTL and registered by the EPA for use in HVAC systems.

First three subparagraphs below are optional treatments for fibrous-glass-lined casings, providing various ways to separate fibrous glass from direct contact with the airstream. Some manufacturers also have specialty/trademarked types of liners. Confirm availability with manufacturers.

          - Foil-Faced Liner: Minimum 0.001-inch (0.03-mm) reinforced, nonporous aluminum foil applied to matted insulation airstream face. [Encapsulate all insulation edges with sheet metal angles and channels, or tape.]

          - Solid Metal Liner: Solid [galvanized sheet metal] <Insert material> encapsulating matted insulation face from airstream.

          - Perforated Metal Liner: Perforated [galvanized sheet metal] <Insert material> encapsulating matted insulation face from airstream.

          - Specialty Liner: <Insert specialty liner in coordination with manufacturers>.

          - [Solvent] [Water]-Based Liner Adhesive: Comply with NFPA 90A or NFPA 90B and with ASTM C916.

            - <Double click to insert sustainable design text for adhesive.>

            - <Double click to insert sustainable design text for adhesive.>

Flexible elastomeric duct liner in "Casing Liner, Flexible Elastomeric" Paragraph below is unsuitable for temperatures higher than 220 deg F (104 deg C).

        - Casing Liner, Flexible Elastomeric: Flexible elastomeric duct liner fabricated of preformed, cellular, closed-cell, sheet materials complying with ASTM C534/C534M, Type II, Grade 1; and with NFPA 90A or NFPA 90B.

Available thicknesses for flexible elastomeric duct liner vary depending on the manufacturer. Indicate thickness on Drawings.

Surface-burning characteristics in "Minimum Thickness" Subparagraph below are available in limited thicknesses. Verify maximum thickness with manufacturers.

          - Minimum Thickness: [1/2 inch (13 mm)] <Insert dimension>.

          - Surface-Burning Characteristics: Maximum flame-spread index of 25 and maximum smoke-developed index of 50 when tested in accordance with UL 723; certified by an NRTL.

          - Liner Adhesive: As recommended by insulation manufacturer and complying with NFPA 90A or NFPA 90B.

            - <Double click to insert sustainable design text for adhesive.>

            - <Double click to insert sustainable design text for adhesive.>

      - SOURCE QUALITY CONTROL

Retain first or second paragraph below. AHRI certification may not be available from all manufacturers. Some manufacturers indicate that they test and rate units in accordance with AHRI 880, but their units are not certified or labeled by AHRI. AHRI certification program is not yet available for DOAS, series, air terminal units (with sensible chilled-water coil); however, many manufacturers test and rate in accordance with the standard. Confirm availability with manufacturers.

        - [AHRI 880 Certification: Test, rate, and label assembled air terminal units in accordance with AHRI 880.]

        - [AHRI 880: Test and rate assembled air terminal units in accordance with AHRI 880.]

        - Water Coils: Factory pressure test to 300 psig (2070 kPa) in accordance with AHRI 410 and ASHRAE 33.

- EXECUTION

      - INSTALLATION, GENERAL

        - Comply with Section 230529 "Hangers and Supports for HVAC Piping and Equipment" and Section 233113 "Metal Ducts" for hangers and supports.

        - Install air terminal units according to NFPA 90A.

        - Install air terminal units level and plumb. Maintain sufficient clearance for normal service and maintenance.

Delete paragraph below if thermostats are specified in Section 230923 "Direct Digital Control (DDC) System for HVAC."

        - Install wall-mounted thermostats.

      - PIPING CONNECTIONS

        - Where installing piping adjacent to air terminal unit, allow space for service and maintenance.

Retain options in "Hot-Water (and) (Chilled-Water) Piping" Paragraph below if DOAS, series fan-powered air terminal units with chilled-water coils are retained in Part 2.

        - Hot-Water [and] [Chilled-Water] Piping: Comply with requirements in Section 232113 "Hydronic Piping" and Section 232116 Hydronic Piping Specialties," and connect heating [and] [cooling] coils to supply piping with shutoff valve, strainer, control valve, and union or flange; and to return piping with balancing valve and union or flange.

      - DUCTWORK CONNECTIONS

        - Comply with requirements in [Section 233113 "Metal Ducts"] [Section 233116 "Nonmetal Ducts"] for connecting ducts to air terminal units.

Coordinate duct installations and specialty arrangements with Drawings.

        - Make connections to air terminal units with flexible connectors complying with requirements in Section 233300 "Air Duct Accessories."

      - ELECTRICAL CONNECTIONS

        - Install field power to each air terminal unit electrical power connection. Coordinate with air terminal unit manufacturer and installers.

        - Connect wiring in accordance with Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

        - Ground equipment in accordance with Section 260526 "Grounding and Bonding for Electrical Systems."

        - Install electrical devices furnished by manufacturer, but not factory mounted, in accordance with NFPA 70 and NECA 1.

        - Install nameplate for each electrical connection, indicating electrical equipment designation and circuit number feeding connection.

Retain one of two subparagraphs below. First subparagraph cross-references Section 260553 "Identification for Electrical Systems" and should be retained for consistent electrical identification. Second is an abbreviated version of the product specified in Section 260553 "Identification for Electrical Systems."

          - Nameplate shall be laminated acrylic or melamine plastic signs, as specified in Section 260553 "Identification for Electrical Systems."

          - Nameplate shall be laminated acrylic or melamine plastic signs with a black background and engraved white letters at least [1/2 inch (13 mm)] <Insert dimension> high.

      - CONTROL CONNECTIONS

        - Install control and electrical power wiring to field-mounted control devices.

        - Connect control wiring in accordance with Section 260523 "Control-Voltage Electrical Power Cables."

      - IDENTIFICATION

        - Label each air terminal unit with drawing designation, nominal airflow, maximum and minimum factory-set airflows[, and coil type]. Comply with requirements in Section 230553 "Identification for HVAC Piping and Equipment" for equipment labels and warning signs and labels.

      - STARTUP SERVICE

        - [Engage a factory-authorized service representative to perform] [Perform] startup service.

          - Complete installation and startup checks in accordance with manufacturer's written instructions.

          - Verify that inlet duct connections are as recommended by air terminal unit manufacturer to achieve proper performance.

          - Verify that controls and control enclosure are accessible.

          - Verify that control connections are complete.

          - Verify that nameplate and identification tag are visible.

          - Verify that controls respond to inputs as specified.

          - <Insert startup steps if any>.

      - ADJUSTING

        - Comply with requirements in Section 230593 "Testing, Adjusting, and Balancing for HVAC" for air terminal unit testing, adjusting, and balancing.

      - FIELD QUALITY CONTROL

Retain one of first three paragraphs below. Retain first option in "Testing Agency" Paragraph below if Owner will hire an independent testing agency.

        - Testing Agency: [Owner] [Contractor] will engage a qualified testing agency to perform tests and inspections.

Retain "Manufacturer's Field Service" Paragraph below to require a factory-authorized service representative to perform tests and inspections.

        - Manufacturer's Field Service: Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

        - Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

          - After installing air terminal units and after electrical circuitry has been energized, test for compliance with requirements.

Retain "Leak Test" Subparagraph below for air terminal units with hot-water coils.

          - Leak Test: After installation, fill water coils and test for leaks. Repair leaks and retest until no leaks exist.

          - Operational Test: After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

          - Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Air terminal unit will be considered defective if it does not pass tests and inspections.

        - Prepare test and inspection reports.

      - DEMONSTRATION

        - [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain air terminal units.

END OF SECTION 233600