Copyright 2013 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 235123 - GAS VENTS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Listed double-wall vents.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 235113.11 "Draft Control Fans" for draft inducer fans, venturi-draft inducer fans, mechanical-draft vent fans, vent exhaust fans, and combustion-air fans.

          - Section 235113.16 "Vent Dampers" for motorized and barometric dampers.

          - Section 235116 "Fabricated Breechings and Accessories" for listed, refractory-lined metal breechings and field-fabricated metal breechings.

          - Section 235133 "Insulated Sectional Chimneys" for listed chimney liners; listed building-heating-appliance chimneys; listed, refractory-lined metal chimneys; and field-fabricated chimneys.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

          - Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for product.

        - Shop Drawings: For vents.

          - Include plans, elevations, sections, and attachment details.

          - Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

          - Detail fabrication and assembly of hangers and seismic restraints.

      - INFORMATIONAL SUBMITTALS

Retain "Welding certificates" Paragraph below if retaining "Welding Qualifications" Paragraph in "Quality Assurance" Article.

        - Welding certificates.

        - Sample Warranty: For special warranty.

      - QUALITY ASSURANCE

Retain "Welding Qualifications" Paragraph below if shop or field welding is required. If retaining, also retain "Welding certificates" Paragraph in "Informational Submittals" Article. The American Welding Society (AWS) states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

        - Welding Qualifications: Qualify procedures and personnel according to the following:

          - AWS D1.1/D1.1M, "Structural Welding Code - Steel," for hangers and supports.

          - AWS D9.1/D9.1M, "Sheet Metal Welding Code," for shop and field welding of joints and seams in vents.

        - Certified Sizing Calculations: Manufacturer shall certify venting system sizing calculations.

- PRODUCTS

Manufacturers and products listed in SpecAgent and Masterworks Paragraph Builder are neither recommended nor endorsed by the AIA or Deltek. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - LISTED TYPE B AND BW VENTS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Double-wall metal vents tested according to UL 441 and rated for 480 deg F (248 deg C) continuously for Type B or 550 deg F (288 deg C) continuously for Type BW; with neutral or negative flue pressure complying with NFPA 211.

        - Construction: Inner shell and outer jacket separated by at least a 1/4-inch (6-mm) airspace.

        - Inner Shell: [ASTM B209 (ASTM B209M), Type 1100 aluminum] [ASTM B209 (ASTM B209M), Type 3003 aluminum] [ASTM B209 (ASTM B209M), Type 3105 aluminum] [ASTM A666, Type 430 stainless steel].

        - Outer Jacket: [Galvanized] [Aluminized] steel.

        - Accessories: Tees, elbows, increasers, draft-hood connectors, terminations, adjustable roof flashings, storm collars, support assemblies, thimbles, firestop spacers, and fasteners; fabricated from similar materials and designs as vent-pipe straight sections; all listed for same assembly.

Retain one of first four "Termination" subparagraphs below or insert type to suit Project. Use caution because many systems are tested with specific terminations.

          - Termination: Stack cap designed to exclude minimum 90 percent of rainfall.

          - Termination: Round chimney top designed to exclude minimum 98 percent of rainfall.

          - Termination: Exit cone with drain section incorporated into riser.

          - Termination: Antibackdraft.

          - Termination: <Insert termination>.

      - LISTED TYPE L VENTS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Double-wall metal vents tested according to UL 641 and rated for 570 deg F (300 deg C) continuously or 1700 deg F (926 deg C) for 10 minutes; with neutral or negative flue pressure complying with NFPA 211.

        - Construction: Inner shell and outer jacket separated by at least a [1/4-inch (6-mm)] [1-inch (25-mm)] [2-inch (50-mm)] [4-inch (100-mm)] airspace filled with high-temperature, [ceramic-fiber] [mineral-wool] insulation.

        - Inner Shell: ASTM A666, [Type 304] [Type 316] stainless steel.

        - Outer Jacket: [Galvanized] [Aluminized] [Stainless] steel.

        - Accessories: Tees, elbows, increasers, draft-hood connectors, terminations, adjustable roof flashings, storm collars, support assemblies, thimbles, firestop spacers, and fasteners; fabricated from similar materials and designs as vent-pipe straight sections; all listed for same assembly.

Retain one of first three "Termination" subparagraphs below or insert type to suit Project. Use caution because many systems are tested with specific terminations.

          - Termination: Stack cap designed to exclude 90 percent of rainfall.

          - Termination: Round chimney top designed to exclude 98 percent of rainfall.

          - Termination: Exit cone with drain section incorporated into riser.

          - Termination: <Insert termination>.

      - LISTED SPECIAL GAS VENTS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Double-wall metal vents tested according to UL 1738 and rated for 480 deg F (248 deg C) continuously, with positive or negative flue pressure complying with NFPA 211.

        - Construction: Inner shell and outer jacket separated by at least a 1/2-inch (13-mm) airspace.

        - Inner Shell: ASTM A959, Type 29-4C stainless steel.

        - Outer Jacket: [Aluminized] [Stainless] steel.

        - Accessories: Tees, elbows, increasers, draft-hood connectors, terminations, adjustable roof flashings, storm collars, support assemblies, thimbles, firestop spacers, and fasteners; fabricated from similar materials and designs as vent-pipe straight sections; all listed for same assembly.

Retain one of first three "Termination" subparagraphs below or insert type to suit Project. Use caution because many systems are tested with specific terminations.

          - Termination: Stack cap designed to exclude minimum 90 percent of rainfall.

          - Termination: Round chimney top designed to exclude minimum 98 percent of rainfall.

          - Termination: Exit cone with drain section incorporated into riser.

          - Termination: <Insert termination>.

- EXECUTION

      - EXAMINATION

        - Examine areas and conditions for compliance with requirements for installation tolerances and other conditions affecting performance of work.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - APPLICATION

        - Listed Type B and BW Vents: Vents for certified gas appliances.

        - Listed Type L Vent: Vents for low-heat appliances.

        - Listed Special Gas Vent: Condensing gas appliances.

      - INSTALLATION OF LISTED VENTS

        - Coordinate installation of roof curbs, equipment supports, and roof penetrations. These items are specified in Section 077200 "Roof Accessories."

        - Comply with minimum clearances from combustibles and minimum termination heights according to product listing or NFPA 211, whichever is most stringent.

Retain first paragraph below if specifying positive-pressure vents.

        - Seal between sections of positive-pressure vents according to manufacturer's written installation instructions, using sealants recommended by manufacturer.

        - Support vents at intervals recommended by manufacturer to support weight of vents and all accessories, without exceeding appliance loading.

        - Lap joints in direction of flow.

      - CLEANING

        - After completing system installation, including outlet fittings and devices, inspect exposed finish. Remove burrs, dirt, and construction debris, and repair damaged finishes.

END OF SECTION 235123