Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 260533.23 - SURFACE RACEWAYS FOR ELECTRICAL SYSTEMS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED 2009, LEED v4, LEED v4.1, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using the hypertext links.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Surface metal raceways and fittings.

          - Surface nonmetallic raceways.

          - Strut-type channel raceways and fittings.

          - Wireways and auxiliary gutters.

        - Products Installed, but Not Furnished, under This Section:

          - See Section 260553 "Identification for Electrical Systems" for electrical equipment labels.

        - Related Requirements:

Always retain two subparagraphs below.

          - Section 260010 "Supplemental Requirements for Electrical" for additional abbreviations, definitions, submittals, qualifications, testing agencies, and other Project requirements applicable to Work specified in this Section.

          - Section 260011 "Facility Performance Requirements for Electrical" for seismic-load, wind-load, acoustical, and other field conditions applicable to Work specified in this Section.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

Retain one or more of four subparagraphs below as needed to verify compliance of Work with Project requirements.

          - Surface metal raceways and fittings.

          - Surface nonmetallic raceways.

          - Strut-type channel raceways and fittings.

          - Wireways and auxiliary gutters.

Retain "Samples" Paragraph below if products have critical features needing hands-on appraisal.

        - Samples:

Retain one or more of four subparagraphs below as needed to verify compliance of Work with Project requirements.

          - Surface metal raceway nonmetallic cover samples for initial selection.

          - Surface nonmetallic raceway samples for initial selection.

          - Strut-type channel raceway nonmetallic covers for initial selection.

          - Nonmetallic wireway and auxiliary gutter samples for initial selection.

Retain paragraph below if required to attain sustainability rating or to track sustainability submittals.

        - Sustainable design submittals.

Retain one or more of four subparagraphs below as needed to verify compliance of Work with Project requirements.

          - Surface metal raceways and fittings.

          - Surface nonmetallic raceways.

          - Strut-type channel raceways and fittings.

          - Wireways and auxiliary gutters.

      - INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

        - Manufacturers' Published Instructions:

Retain one or more of four subparagraphs below as needed to verify compliance of Work with Project requirements.

          - Surface metal raceways and fittings.

          - Surface nonmetallic raceways.

          - Strut-type channel raceways and fittings.

          - Wireways and auxiliary gutters.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - SURFACE METAL RACEWAYS AND FITTINGS

        - Performance Criteria:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

          - Listing Criteria: UL CCN RJBT; including UL 5.

        - Source Quality Control:

Coordinate "Product Data" Subparagraph below with "Action Submittals" Article.

          - Product Data: Prepare and submit catalog cuts, brochures, and performance data illustrating size, physical appearance, and other characteristics of product.

Retain "Sustainable Design Submittals" Subparagraph below if required to attain sustainability rating or to track sustainability submittals.

          - Sustainable Design Submittals: Prepare and submit the following documentation for adhesives and solvents used with nonmetallic components:

            - <Double click to insert sustainable design text for Conduit VOC Content>

Retain "Manufacturer's Published Instructions" Subparagraph below when execution requirements state "in accordance with manufacturer's published instructions," especially if those instructions may require preinstallation review and coordination with Construction Documents to verify constructability and commissioning requirements. Coordinate subparagraph with "Informational Submittals" Article.

          - Manufacturer's Published Instructions: Prepare and submit installation, testing, and operating instructions for product.

          - Samples:

            - Surface Metallic Raceway Nonmetallic Cover Samples for Initial Selection: Manufacturer's standard color sheets, showing full range of available colors for each type, [12 inch (300 mm)] <Insert dimension> long.

        - UL RJBT - Surface Metal Raceways and Fittings with Metal Covers:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - [Galvanized steel] [Aluminum] base with snap-on covers.

Insert requirements for finish-coat paint color, if applicable, in first subparagraph below. See painting Sections for optional field-finish coats.

            - [Manufacturer's standard enamel finish in color selected by Architect] [Prime coated, ready for field painting].

            - Wiring Channels: [Single] [Dual] [Triple]. Multiple channels must be capable of housing a standard 20 to 30 A device flush within the raceway.

        - UL RJBT - Surface Metal Raceways and Fittings with Nonmetallic Covers:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Additional Characteristics: UL 94, V-0 requirements for self-extinguishing characteristics.

          - Options:

            - [Galvanized steel] [Aluminum] base with snap-on covers.

            - Provide texture and color selected by Architect from [manufacturer's standard] [custom] colors.

            - Wiring Channels: [Single] [Dual] [Triple]. Multiple channels must be capable of housing a standard 20 to 30 A device flush within the raceway.

      - SURFACE NONMETALLIC RACEWAYS

        - Performance Criteria:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

          - Listing Criteria:

            - UL CCN RJTX; including UL 5A.

            - UL 94, V-0 requirements for self-extinguishing characteristics.

        - Source Quality Control:

Coordinate "Product Data" Subparagraph below with "Action Submittals" Article.

          - Product Data: Prepare and submit catalog cuts, brochures, and performance data illustrating size, physical appearance, and other characteristics of product.

Retain "Sustainable Design Submittals" Subparagraph below if required to attain sustainability rating or to track sustainability submittals.

          - Sustainable Design Submittals: Prepare and submit the following documentation for adhesives and solvents:

            - <Double click to insert sustainable design text for Conduit VOC Content>

Retain "Manufacturer's Published Instructions" Subparagraph below when execution requirements state "in accordance with manufacturer's published instructions," especially if those instructions may require preinstallation review and coordination with Construction Documents to verify constructability and commissioning requirements. Coordinate subparagraph with "Informational Submittals" Article.

          - Manufacturer's Published Instructions: Prepare and submit installation, testing, and operating instructions for product.

          - Samples:

            - Surface Nonmetallic Raceway Samples for Initial Selection: Manufacturer's standard color sheets, showing full range of available colors for each type, [12 inch (300 mm)] <Insert dimension> long.

        - UL RJTX - Surface Nonmetallic Raceways and Fittings with Nonmetallic Covers:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Provide texture and color selected by Architect from [manufacturer's standard] [custom] colors.

            - Wiring Channels: [Single] [Dual]. Multiple channels must be capable of housing a standard 20 to 30 A device flush within the raceway.

        - UL RJTX - Surface Nonmetallic Raceways and Fittings with Metallic Covers:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Insert requirements for finish-coat paint color, if applicable, in first subparagraph below. See painting Sections for optional field-finish coats.

            - [Manufacturer's standard enamel finish in color selected by Architect] [Prime coated, ready for field painting].

            - Wiring Channels: [Single] [Dual]. Multiple channels must be capable of housing a standard 20 to 30 A device flush within the raceway.

      - STRUT-TYPE CHANNEL RACEWAYS AND FITTINGS

        - Performance Criteria:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

          - Listing Criteria:

            - UL CCN RIUU; including UL 5B.

            - UL 94, V-0 requirements for self-extinguishing characteristics.

        - Source Quality Control:

Coordinate "Product Data" Subparagraph below with "Action Submittals" Article.

          - Product Data: Prepare and submit catalog cuts, brochures, and performance data illustrating size, physical appearance, and other characteristics of product.

Retain "Sustainable Design Submittals" Subparagraph below if required to attain sustainability rating or to track sustainability submittals.

          - Sustainable Design Submittals: Prepare and submit the following documentation for adhesives and solvents used with nonmetallic components:

            - <Double click to insert sustainable design text for Conduit VOC Content>

Retain "Manufacturer's Published Instructions" Subparagraph below when execution requirements state "in accordance with manufacturer's published instructions," especially if those instructions may require preinstallation review and coordination with Construction Documents to verify constructability and commissioning requirements. Coordinate subparagraph with "Informational Submittals" Article.

          - Manufacturer's Published Instructions: Prepare and submit installation, testing, and operating instructions for product.

          - Samples:

            - Strut-Type Channel Raceway Nonmetallic Covers for Initial Selection: Manufacturer's standard color sheets, showing full range of available colors for each type, [12 inch (300 mm)] <Insert dimension> long.

        - UL RIUU - Strut-Type Channel Raceways and Fittings with Metallic Covers:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Insert requirements for finish-coat paint color, if applicable, in subparagraph below. See painting Sections for optional field-finish coats.

            - [Manufacturer's standard enamel finish in color selected by Architect] [Prime coated, ready for field painting].

        - UL RIUU - Strut-Type Channel Raceways and Fittings with Nonmetallic Covers:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Additional Characteristics: UL 94, V-0 requirements for self-extinguishing characteristics.

          - Options:

            - Provide texture and color selected by Architect from [manufacturer's standard] [custom] colors.

      - WIREWAYS AND AUXILIARY GUTTERS

        - Performance Criteria:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

          - Listing Criteria:

            - UL CCN ZOYX; including UL 870.

            - UL 94, V-0 requirements for self-extinguishing characteristics.

        - Source Quality Control:

Coordinate "Product Data" Subparagraph below with "Action Submittals" Article.

          - Product Data: Prepare and submit catalog cuts, brochures, and performance data illustrating size, physical appearance, and other characteristics of product.

Retain "Sustainable Design Submittals" Subparagraph below if required to attain sustainability rating or to track sustainability submittals.

          - Sustainable Design Submittals: Prepare and submit the following documentation for adhesives and solvents used with nonmetallic components:

            - <Double click to insert sustainable design text for Conduit VOC Content>

Retain "Manufacturer's Published Instructions" Subparagraph below when execution requirements state "in accordance with manufacturer's published instructions," especially if those instructions may require preinstallation review and coordination with Construction Documents to verify constructability and commissioning requirements. Coordinate subparagraph with "Informational Submittals" Article.

          - Manufacturer's Published Instructions: Prepare and submit installation, testing, and operating instructions for product.

          - Samples:

            - Nonmetallic Wireway and Auxiliary Gutter Samples for Initial Selection: Manufacturer's standard color sheets, showing full range of available colors for each type, [12 inch (300 mm)] <Insert dimension> long.

        - UL ZOYX - Metal Wireways and Auxiliary Gutters:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Additional Characteristics:

            - Fittings and Accessories: Include covers, couplings, offsets, elbows, expansion joints, adapters, hold-down straps, end caps, and other fittings to match and mate with wireways as required for complete system.

            - Finish: Manufacturer's standard enamel finish.

          - Options:

Retain one or more options in "Degree of Protection" Subparagraph below. If retaining more than one type, indicate locations of each type on Drawings.

            - Degree of Protection: [Type 1] [Type 3R] [Type 4] [Type 12] <Insert type> unless otherwise indicated.

Retain one or more options in "Wireway Covers" Subparagraph below. If retaining more than one type, indicate locations of each type on Drawings.

            - Wireway Covers: [Hinged type] [Screw-cover type] [Flanged-and-gasketed type] unless otherwise indicated.

        - UL ZOYX - Nonmetallic Wireways and Auxiliary Gutters:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Additional Characteristics:

            - Fittings and Accessories: Couplings, offsets, elbows, expansion joints, adapters, hold-down straps, end caps, and other fittings must match and mate with wireways as required for complete system.

            - PVC Solvents and Adhesives: As recommended by wireway manufacturer.

          - Options:

            - Material:

Retain one of two subparagraphs below.

              - Fiberglass polyester, extruded and fabricated to required size and shape, without holes or knockouts. Cover must be gasketed with oil-resistant gasket material and fastened with captive screws treated for corrosion resistance. Connections must be flanged and have stainless steel screws and oil-resistant gaskets.

              - PVC, extruded and fabricated to required size and shape, and having snap-on cover, mechanically coupled connections, and plastic fasteners.

- EXECUTION

      - INSTALLATION OF SURFACE RACEWAYS FOR ELECTRICAL SYSTEMS

        - Comply with manufacturer's published instructions.

NFPA 70 and NECA NEIS 1 are already specified in Section 260010 "Supplemental Requirements for Electrical." Retain "Reference Standards for Installation" Paragraph below to specify other standards applicable to Work specified in this Section.

        - Reference Standards for Installation: Unless more stringent installation requirements are specified in Contract Documents or manufacturers' published instructions, comply with the following:

          - Auxiliary Gutters: Article 366 of NFPA 70.

          - Surface Metal Raceway: Article 386 of NFPA 70.

          - Surface Nonmetallic Raceway: Article 388 of NFPA 70.

          - Consult Architect for resolution of conflicting requirements.

        - Special Installation Techniques:

          - Install surface raceways only where indicated on Drawings.

          - Install surface raceway with a minimum 2 inch (50 mm) radius control at bend points.

          - Secure surface raceway with screws or other anchor-type devices at intervals not exceeding 48 inch (1200 mm) and with no less than two supports per straight raceway section. Support surface raceway in accordance with manufacturer's published instructions. Tape and glue are unacceptable support methods.

          - Identification: Provide labels for surface raceways and associated electrical equipment.

            - Identify field-installed conductors, interconnecting wiring, and components.

            - Provide warning signs.

          - <Insert more stringent installation requirements that supplement or supersede listed standards and manufacturers' published instructions>.

        - Interfaces with Other Work:

          - Coordinate installation of new products for <Insert system or product family/category> with existing conditions.

            - <Insert requirements for transition between new and existing>.

          - Coordinate with <Insert Section number and title> for <Insert description of interfacing related Work>.

            - <Insert requirements for transition between this Section and related Work>.

      - CLEANING

        - Remove construction dust and debris from surface raceways before installing covers.

      - PROTECTION

        - After installation, protect surface raceways from construction activities. Remove and replace items that are contaminated, defaced, damaged, or otherwise caused to be unfit for use prior to acceptance by Owner.

END OF SECTION 260533.23