Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 260544 - SLEEVES AND SLEEVE SEALS FOR ELECTRICAL RACEWAYS AND CABLING

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED 2009, LEED v4, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using the hypertext links.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Round sleeves.

          - Rectangular sleeves.

          - Sleeve-seal systems.

          - Sleeve-seal fittings.

          - Grout.

          - Pourable sealants.

          - Foam sealants.

        - Related Requirements:

          - Section 260010 "Supplemental Requirements for Electrical" for additional abbreviations, definitions, submittals, qualifications, testing agencies, and other Project requirements applicable to Work specified in this Section.

          - Section 260011 "Facility Performance Requirements for Electrical" for seismic-load, wind-load, acoustical, and other field conditions applicable to Work specified in this Section.

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 078413 "Penetration Firestopping" for penetration firestopping installed in fire-resistance-rated walls, horizontal assemblies, and smoke barriers, with and without penetrating items.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

        - Sustainable Design Submittals:

          - <Double click to insert sustainable design text for sealants.>

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - ROUND SLEEVES

Retain "Steel Wall Sleeves" or "Cast-Iron Wall Sleeves" Paragraph below for penetrations through exterior walls above and below grade when placing sleeve during wall construction. If sleeves are required for penetrations of existing walls, consider use of non-flanged pipe sleeves made of standard Schedule 40 conduit cut flush at both sides of the wall.

        - Steel Wall Sleeves:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - General Characteristics: ASTM A53/A53M, Type E, Grade B, Schedule 40, zinc coated, plain ends and integral waterstop.

        - Cast-Iron Wall Sleeves:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - General Characteristics: Cast or fabricated "wall pipe," equivalent to ductile-iron pressure pipe, with plain ends and integral waterstop.

"PVC Pipe Sleeves" Paragraph below may be prohibited by authorities having jurisdiction. These flanged sleeves are for penetrations through walls above and below grade when placing sleeve during wall construction. If sleeves are required for penetrations of existing walls, consider use of non-flanged pipe sleeves made of standard Schedule 40 conduit cut flush at both sides of the wall.

        - PVC Pipe Sleeves:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - General Characteristics: ASTM D1785, Schedule 40.

PVC molded sleeves are extensions of the concrete form used to form holes through the concrete structure. They should be removed after the concrete is set. They can be cut flush at both sides of the structure and left in place only if the PVC sleeves are permitted by the authorities having jurisdiction. Because concrete does not adhere to the sleeves, they can be removed and reused.

        - PVC Molded Sleeves:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - General Characteristics: With nailing flange for attaching to wooden forms.

PE or PP molded sleeves are extensions of the concrete form used to form holes through the concrete structure. They should be removed after the concrete is set. They can be cut flush at both sides of the structure and left in place only if the PE or PP sleeves are permitted by authorities having jurisdiction. Because concrete does not adhere to the sleeves, they can be removed and reused.

        - PE or PP Molded Sleeves:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - General Characteristics: Removable, tapered-cup shaped, and smooth outer surface with nailing flange for attaching to wooden forms.

Retain "Round, Galvanized-Steel, Sheet Metal Sleeves" Paragraph below when required by authorities having jurisdiction for conduits penetrating non-fire-rated wall assemblies. NFPA 70 does not contain requirements for sleeves; IBC, Section 712, "Penetrations," does.

        - Round, Galvanized-Steel, Sheet Metal Sleeves:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - General Characteristics: Galvanized-steel sheet; thickness not less than 0.0239 inch (0.6 mm); round tube closed with welded longitudinal joint, with tabs for screw-fastening the sleeve to the board.

      - RECTANGULAR SLEEVES

        - Rectangular, Galvanized-Steel, Sheet Metal Sleeves:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - General Characteristics:

            - Material: Galvanized sheet steel.

            - Minimum Metal Thickness:

              - For sleeve cross-section rectangle perimeter less than 50 inch (1270 mm) and with no side larger than 16 inch (400 mm), thickness must be 0.052 inch (1.3 mm).

              - For sleeve cross-section rectangle perimeter not less than 50 inch (1270 mm) or with one or more sides larger than 16 inch (400 mm), thickness must be 0.138 inch (3.5 mm).

      - SLEEVE-SEAL SYSTEMS

Sleeve-seal systems in this article are used for conduit penetrations in slabs-on-grade and in below-grade exterior walls.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - General Characteristics: Modular sealing device, designed for field assembly, to fill annular space between sleeve and raceway or cable or between raceway and cable.

        - Options:

Retain first option in "Sealing Elements" Subparagraph below unless Nitrile (Buna N) rubber gasket material is required because hydrocarbons are present in the soil.

          - Sealing Elements: [EPDM] [Nitrile (Buna N)] rubber interlocking links shaped to fit surface of pipe. Include type and number required for pipe material and size of pipe.

          - Pressure Plates: [Carbon steel] [Fiber-reinforced plastic] [Stainless steel].

          - Connecting Bolts and Nuts: [Carbon steel, with corrosion-resistant coating,] [Stainless steel] of length required to secure pressure plates to sealing elements.

      - SLEEVE-SEAL FITTINGS

Sleeve-seal fittings in this article are used for conduit penetrations in slabs-on-grade and in exterior walls. These fittings are made to match conduit OD, so they must be selected to match the penetrating conduit size. They are available for conduit sizes metric designators 15 to 150 (trade sizes 1/2 to 6).

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - General Characteristics: Manufactured plastic, sleeve-type, waterstop assembly made for embedding in concrete slab or wall. Unit must have plastic or rubber waterstop collar with center opening to match piping OD.

      - GROUT

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - General Characteristics: Nonshrink; recommended for interior and exterior sealing openings in non-fire-rated walls or floors.

          - Standard: ASTM C1107/C1107M, Grade B, post-hardening and volume-adjusting, dry, hydraulic-cement grout.

          - Design Mix: 5000 psi (34.5 MPa), 28-day compressive strength.

          - Packaging: Premixed and factory packaged.

      - POURABLE SEALANTS

Retain this article when use of pourable sealants is permitted as an alternative to grout in sealing of conduit or cable penetrations.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Performance Criteria:

          - General Characteristics: Single-component, neutral-curing elastomeric sealants of grade indicated below.

            - Grade: Pourable (self-leveling) formulation for openings in floors and other horizontal surfaces that are not fire rated.

          - Sustainability Characteristics:

            - <Double click to insert sustainable characteristics for sleeve sealants>

      - FOAM SEALANTS

Retain this article when use of foam sealants is permitted as an alternative to grout in sealing of conduit or cable penetrations.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Performance Criteria:

          - General Characteristics: Multicomponent, liquid elastomers that, when mixed, expand and cure in place to produce a flexible, nonshrinking foam. Foam expansion must not damage cables or crack penetrated structure.

          - Sustainability Characteristics:

            - <Double click to insert sustainable characteristics for sleeve sealants>

- EXECUTION

      - INSTALLATION OF SLEEVES FOR NON-FIRE-RATED ELECTRICAL PENETRATIONS

        - Sleeves for Conduits Penetrating Above-Grade, Non-Fire-Rated, Concrete and Masonry-Unit Floors and Walls:

          - Interior Penetrations of Non-Fire-Rated Walls and Floors:

            - Seal space outside of sleeves with mortar or grout. Pack sealing material solidly between sleeve and wall or floor so no voids remain. Tool exposed surfaces smooth; protect material while curing.

            - Seal annular space between sleeve and raceway or cable, using joint sealant appropriate for size, depth, and location of joint. Comply with requirements in Section 079200 "Joint Sealants."

          - Use pipe sleeves unless penetration arrangement requires rectangular sleeved opening.

Retain last option in first subparagraph below when Project has stringent seismic requirements.

          - Size pipe sleeves to provide [1/4 inch (6.4 mm)] <Insert dimension> annular clear space between sleeve and raceway or cable, unless sleeve-seal system is to be installed[ or seismic criteria require different clearance].

          - Install sleeves for wall penetrations unless core-drilled holes or formed openings are used. Install sleeves during erection of walls. Cut sleeves to length for mounting flush with both surfaces of walls. Deburr after cutting.

Retain subparagraph below when unsleeved core-drilled openings in concrete floors are not allowed.

          - Install sleeves for floor penetrations. Extend sleeves installed in floors [2 inch (50 mm)] <Insert dimension> above finished floor level. Install sleeves during erection of floors.

        - Sleeves for Conduits Penetrating Non-Fire-Rated Wall Assemblies:

          - Use circular metal sleeves unless penetration arrangement requires rectangular sleeved opening.

          - Seal space outside of sleeves with approved joint compound for wall assemblies.

        - Roof-Penetration Sleeves: Seal penetration of individual raceways and cables with flexible boot-type flashing units applied in coordination with roofing work.

        - Aboveground, Exterior-Wall Penetrations: Seal penetrations using [steel] [cast-iron] pipe sleeves and mechanical sleeve-seal systems. Size sleeves to allow for 1 inch (25 mm) annular clear space between pipe and sleeve for installing mechanical sleeve seals.

        - Underground, Exterior-Wall and Floor Penetrations:

Retain first subparagraph below if new walls or floors are being constructed below ground and the sleeves can be placed during construction.

          - Install [steel] [cast-iron] pipe sleeves with integral waterstops. Size sleeves to allow for 1 inch (25 mm) annular clear space between raceway or cable and sleeve for installing sleeve-seal system. Install sleeve during construction of floor or wall.

Retain subparagraph below if existing walls or floors are below ground and penetrations will be core drilled.

          - Install steel pipe sleeves. Size sleeves to allow for 1 inch (25 mm) annular clear space between raceway or cable and sleeve for installing sleeve-seal system. Grout sleeve into wall or floor opening.

      - INSTALLATION OF RECTANGULAR SLEEVES AND SLEEVE SEALS

Rectangular sleeves are used where multiple conduits penetrate a wall at one location. The only practical way of sealing around the conduits inside the sleeve, other than fireproof systems specified in Section 078413 "Penetration Firestopping," is with expanding foam. Install sleeves in new walls as they are constructed.

        - Install sleeves in existing walls without compromising structural integrity of walls. Do not cut structural elements without reinforcing the wall to maintain the designed weight bearing and wall stiffness.

        - Install conduits and cable with no crossings within the sleeve.

        - Fill opening around conduits and cables with expanding foam without leaving voids.

        - Provide metal sheet covering at both wall surfaces and finish to match surrounding surfaces. Metal sheet must be same material as sleeve.

      - INSTALLATION OF SLEEVE-SEAL SYSTEMS

Sleeve-seal systems in this article are used in slabs-on-grade and in below-grade exterior concrete walls for a watertight seal around service-piping entries into the building. These systems require installation in a sleeve for proper operation.

        - Install sleeve-seal systems in sleeves in exterior concrete walls and slabs-on-grade at raceway entries into building.

        - Install type and number of sealing elements recommended by manufacturer for raceway or cable material and size. Position raceway or cable in center of sleeve. Assemble mechanical sleeve seals and install in annular space between raceway or cable and sleeve. Tighten bolts against pressure plates that cause sealing elements to expand and make watertight seal.

END OF SECTION 260544