Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 262716 - ELECTRICAL CABINETS AND ENCLOSURES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED 2009, LEED v4, LEED v4.1, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using the hypertext links.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Cabinets and cutout boxes.

          - Termination boxes.

          - Miscellaneous enclosures.

          - Rack or frame systems.

          - Enclosure-mounted relocatable power taps.

        - Products Installed, but Not Furnished, under This Section:

          - See Section 260553 "Identification for Electrical Systems" for equipment labels.

        - Related Requirements:

Always retain two subparagraphs below.

          - Section 260010 "Supplemental Requirements for Electrical" for additional abbreviations, definitions, submittals, qualifications, testing agencies, and other Project requirements applicable to Work specified in this Section.

          - Section 260011 "Facility Performance Requirements for Electrical" for seismic-load, wind-load, acoustical, and other field conditions applicable to Work specified in this Section.

      - DEFINITIONS

Do not duplicate common acronyms, abbreviations, and terms defined in Section 260010 "Supplemental Requirements for Electrical."

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - RBB: Rack bonding busbar, located in equipment cabinets and racks.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

Retain one or more of five subparagraphs below as needed to verify compliance of Work with Project requirements.

          - Cabinets and cutout boxes.

          - Termination boxes.

          - Miscellaneous enclosures.

          - Rack or frame systems.

          - Enclosure-mounted relocatable power taps.

        - Shop Drawings:

Retain one or more of two subparagraphs below as needed to verify compliance of Work with Project requirements.

          - Shop drawings for custom enclosures and cabinets.

          - Shop drawings for racks or frames.

      - INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

        - Manufacturers' Published Instructions:

Retain one or more of five subparagraphs below as needed to verify compliance of Work with Project requirements.

          - Cabinets and cutout boxes.

          - Termination boxes.

          - Miscellaneous enclosures.

          - Rack or frame systems.

          - Enclosure-mounted relocatable power taps.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - CABINETS AND CUTOUT BOXES

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

            - <Insert requirements>.

          - Listing Criteria:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - UL CCN CYIV.

            - Non-Environmental Characteristics: UL 50.

            - Environmental Characteristics: UL 50E.

        - Source Quality Control:

Coordinate "Product Data" Subparagraph below with "Action Submittals" Article.

          - Product Data: Prepare and submit catalog cuts, brochures, and performance data illustrating size, physical appearance, and other characteristics of product.

Retain "Manufacturer's Published Instructions" Subparagraph below when execution requirements state "in accordance with manufacturer's published instructions," especially if those instructions may require preinstallation review and coordination with Construction Documents to verify constructability and commissioning requirements. Coordinate subparagraph with "Informational Submittals" Article.

          - Manufacturer's Published Instructions: Prepare and submit installation, testing, and operating instructions for product.

Copy and revise first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - UL CYIV - Indoor Sheet Metal Cabinets <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - General Characteristics: Enclosure provided with frame, mat, or trim in which swinging door or doors are or can be hung.

Retain "Options" Subparagraph below to require all products to be same degree of protection. To permit different degrees of protection for different applications or locations, specify type on Drawings or specify selection criteria in Part 3.

          - Options:

            - Degree of Protection: [Type 1] [Type 2] [Type 5] [Type 12] [Type 12K] [Type 13].

Copy and revise first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - UL CYIV - Indoor Sheet Metal Cutout Boxes <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - General Characteristics: Enclosure that has swinging doors or covers secured directly to and telescoping with walls of enclosure.

Retain "Options" Subparagraph below to require all products to be same degree of protection. To permit different degrees of protection for different applications or locations, specify type on Drawings or specify selection criteria in Part 3.

          - Options:

            - Degree of Protection: [Type 1] [Type 2] [Type 5] [Type 12] [Type 12K] [Type 13].

Copy and revise first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - UL CYIV - Outdoor Sheet Metal Cabinets <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - General Characteristics: Enclosure provided with frame, mat, or trim in which swinging door or doors are or can be hung.

Retain "Options" Subparagraph below to require all products to be same degree of protection. To permit different degrees of protection for different applications or locations, specify type on Drawings or specify selection criteria in Part 3.

          - Options:

            - Degree of Protection: [Type 3] [Type 3X] [Type 3R] [Type 3RX] [Type 3S] [Type 3SX] [Type 4] [Type 4X] [Type 6] [Type 6P].

Copy and revise paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - UL CYIV - Outdoor Sheet Metal Cutout Boxes <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - General Characteristics: Enclosure that has swinging doors or covers secured directly to and telescoping with walls of enclosure.

Retain "Options" Subparagraph below to require all products to be same degree of protection. To permit different degrees of protection for different applications or locations, specify type on Drawings or specify selection criteria in Part 3.

          - Options:

            - Degree of Protection: [Type 3] [Type 3X] [Type 3R] [Type 3RX] [Type 3S] [Type 3SX] [Type 4] [Type 4X] [Type 6] [Type 6P].

      - TERMINATION BOXES

        - Description: Enclosure for termination base consisting of lengths of bus bars, terminal strips, or terminal blocks with provision for wire connectors to accommodate incoming or outgoing conductors or both.

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - Listing Criteria:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - UL CCN XCKT; including UL 1773.

            - Non-Environmental Characteristics: UL 50.

            - Environmental Characteristics: UL 50E.

        - Source Quality Control:

Coordinate "Product Data" Subparagraph below with "Action Submittals" Article.

          - Product Data: Prepare and submit catalog cuts, brochures, and performance data illustrating size, physical appearance, and other characteristics of product.

Retain "Manufacturer's Published Instructions" Subparagraph below when execution requirements state "in accordance with manufacturer's published instructions," especially if those instructions may require preinstallation review and coordination with Construction Documents to verify constructability and commissioning requirements. Coordinate subparagraph with "Informational Submittals" Article.

          - Manufacturer's Published Instructions: Prepare and submit installation, testing, and operating instructions for product.

Copy and revise first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - UL XCKT - Termination Boxes and Termination Bases for Installation on Line Side of Service Equipment <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Additional Characteristics: Listed and labeled for installation on line side of service equipment.

Retain "Options" Subparagraph below to require all products to be same degree of protection. To permit different degrees of protection for different applications or locations, specify type on Drawings or specify selection criteria in Part 3.

          - Options:

            - Indoor Degree of Protection: [Type 1] [Type 2] [Type 5] [Type 12] [Type 12K] [Type 13].

            - Outdoor Degree of Protection: [Type 3] [Type 3X] [Type 3R] [Type 3RX] [Type 3S] [Type 3SX] [Type 4] [Type 4X] [Type 6] [Type 6P].

Copy and revise paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - UL XCKT - Termination Boxes and Termination Bases for Installation on Load Side of Service Equipment <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Additional Characteristics: Listed and labeled for installation on load side of service equipment.

Retain "Options" Subparagraph below to require all products to be same degree of protection. To permit different degrees of protection for different applications or locations, specify type on Drawings or specify selection criteria in Part 3.

          - Options:

            - Indoor Degree of Protection: [Type 1] [Type 2] [Type 5] [Type 12] [Type 12K] [Type 13].

            - Outdoor Degree of Protection: [Type 3] [Type 3X] [Type 3R] [Type 3RX] [Type 3S] [Type 3SX] [Type 4] [Type 4X] [Type 6] [Type 6P].

      - MISCELLANEOUS ENCLOSURES

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - Listing Criteria:

Retain first subparagraph below to require enclosures to be listed and labeled as termination boxes suitable for field-installed termination bases. UL 1773 is technically not required, but there is no other UL category control number for evaluating miscellaneous enclosures.

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - UL CCN XCKT; including UL 1773.

            - Non-Environmental Characteristics: UL 50.

            - Environmental Characteristics: UL 50E.

        - Source Quality Control:

Coordinate "Product Data" Subparagraph below with "Action Submittals" Article.

          - Product Data: Prepare and submit catalog cuts, brochures, and performance data illustrating size, physical appearance, and other characteristics of product.

Retain "Manufacturer's Published Instructions" Subparagraph below when execution requirements state "in accordance with manufacturer's published instructions," especially if those instructions may require preinstallation review and coordination with Construction Documents to verify constructability and commissioning requirements. Coordinate subparagraph with "Informational Submittals" Article.

          - Manufacturer's Published Instructions: Prepare and submit installation, testing, and operating instructions for product.

Copy and revise first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - UL XCKT - Indoor Sheet Metal Miscellaneous Enclosures <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Options" Subparagraph below to require all products to be same degree of protection. To permit different degrees of protection for different applications or locations, specify type on Drawings or specify selection criteria in Part 3.

          - Options:

            - Degree of Protection: [Type 1] [Type 2] [Type 5] [Type 12] [Type 12K] [Type 13].

Copy and revise paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - UL XCKT - Outdoor Sheet Metal Miscellaneous Enclosures <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Options" Subparagraph below to require all products to be same degree of protection. To permit different degrees of protection for different applications or locations, specify type on Drawings or specify selection criteria in Part 3.

          - Options:

            - Degree of Protection: [Type 3] [Type 3X] [Type 3R] [Type 3RX] [Type 3S] [Type 3SX] [Type 4] [Type 4X] [Type 6] [Type 6P].

      - RACK OR FRAME SYSTEMS

        - Description: This category covers rack or frame systems that are not complete but include components and assemblies that are intended to power, protect, heat, cool, or otherwise support electrical or electronic equipment that will be installed at a later time.

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - Listing Criteria:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - UL CCN NWIN; including UL 2416.

            - Non-Environmental Characteristics: UL 50.

            - Environmental Characteristics: UL 50E or UL 2416.

        - Source Quality Control:

Coordinate "Product Data" Subparagraph below with "Action Submittals" Article.

          - Product Data: Prepare and submit catalog cuts, brochures, and performance data illustrating size, physical appearance, and other characteristics of product.

Retain "Manufacturer's Published Instructions" Subparagraph below when execution requirements state "in accordance with manufacturer's published instructions," especially if those instructions may require preinstallation review and coordination with Construction Documents to verify constructability and commissioning requirements. Coordinate subparagraph with "Informational Submittals" Article.

          - Manufacturer's Published Instructions: Prepare and submit installation, testing, and operating instructions for product.

Retain "19 Inch Open Equipment Rack" Paragraph below to specify floor- and wall-mounted equipment racks that are not enclosed. To specify enclosed cabinets, retain "19 Inch Enclosed Equipment Rack" Paragraph.

Copy and revise first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - UL NWIN - 19 Inch Open Equipment Rack <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - General Characteristics:

            - Threaded rails designed for mounting telecommunications equipment.

            - Width: Compatible with EIA/ECIA 310-E, 19 inch (482.6 mm) equipment mounting with an opening of 17.72 inch (450 mm) between rails.

            - Frames: Modular units designed for telecommunications terminal support and coordinated with dimensions of units to be supported.

            - Finish: Manufacturer's standard, baked-polyester powder coat.

            - Cable Management:

              - Metal, with integral wire retaining fingers.

              - Baked-polyester powder coat finish.

              - Vertical cable management panels have front and rear channels with covers.

              - Horizontal crossover cable manager at top of each relay rack, with minimum height of two rack units each.

          - Options:

            - Configuration: [Two-post] [and] [four-post].

            - Material: [Extruded steel] [Extruded aluminum] [Sheet steel] [Sheet aluminum].

            - Color: [Black] <Insert color>.

Verify options in "Floor-Mounted Racks" Subparagraph below with rack manufacturer.

            - Floor-Mounted Racks:

              - Overall Height: [72 inch (1828.8 mm)] [84 inch (2133.6 mm)] [As indicated on Drawings] <Insert value>.

              - Overall Depth: [23 inch (584.2 mm)] [29 inch (736.6 mm)] <Insert value>.

              - Rail Depth: [3 inch (76.2 mm)] [6 inch (152.4 mm)] <Insert value>.

              - Two-Post Load Rating: [200 lb (91 kg)] [400 lb (181 kg)] <Insert value>.

              - Four-Post Load Rating: [1000 lb (454 kg)] [2000 lb (907 kg)] <Insert value>.

              - Number of Rack Units per Rack: [38] [42] [45] [52] [58] [As indicated on Drawings] <Insert number>.

"Numbering" Subparagraph below may describe a feature not available from all manufacturers.

                - Numbering: [Every] [Every five] rack unit(s), on interior of rack.

              - Threads: [10-32] [12-24] [Universal square].

              - Vertical and horizontal cable management channels, top and bottom cable troughs, grounding lug[, and a power strip].

              - Base must have minimum four mounting holes for permanent attachment to floor.

              - Top must have provisions for attaching to cable tray or ceiling.

              - Self-leveling.

Verify options in "Wall-Mounted Racks" Subparagraph below with rack manufacturer.

            - Wall-Mounted Racks:

              - Height: [18 inch (457.2 mm)] [22 inch (558.8 mm)] [As indicated on Drawings] <Insert value>.

              - Depth: [23 inch (584.2 mm)] [29 inch (736.6 mm)] <Insert value>.

              - Load Rating: [150 lb (65 kg)] [200 lb (91 kg)] <Insert value>.

              - Number of Rack Units per Rack: [8] [12] [22] [As indicated on Drawings] <Insert number>.

              - Threads: [10-32] [12-24] [Universal square].

              - Wall Attachment: Four pre-punched mounting holes.

"Equipment Access" Subparagraph below is for an option that may not be available from all manufacturers.

              - Equipment Access: Integral swing.

Copy and revise first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - UL NWIN - 19 Inch Enclosed Equipment Rack <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - General Characteristics:

            - Manufacturer-assembled four-post frame enclosed by side and top panels and front and rear doors, designed for mounting telecommunications equipment.

            - Threaded rails designed for mounting telecommunications equipment.

            - Width: Compatible with EIA/ECIA 310-E, 19 inch (482.6 mm) equipment mounting with an opening of 17.72 inch (450 mm) between rails.

            - Frames: Modular units designed for telecommunications terminal support and coordinated with dimensions of units to be supported.

            - Finish: Manufacturer's standard, baked-polyester powder coat.

            - Cable Management:

              - Metal, with integral wire retaining fingers.

              - Baked-polyester powder coat finish.

              - Vertical cable management panels have front and rear channels with covers.

              - Horizontal crossover cable manager at top of each relay rack, with minimum height of two rack units each.

          - Options:

            - Material: [Extruded steel] [Extruded aluminum] [Sheet steel] [Sheet aluminum].

            - Color: [Black] <Insert color>.

            - Modular Freestanding Cabinets:

              - Overall Height: [72 inch (1828.8 mm)] [84 inch (2133.6 mm)] [As indicated on Drawings] <Insert value>.

              - Overall Depth: [23 inch (584.2 mm)] [29 inch (736.6 mm)] <Insert value>.

              - Load Rating: [3000 lb (1362 kg)] <Insert value>.

              - Number of Rack Units: [38] [42] [45] [52] [58] [As indicated on Drawings] <Insert number>.

"Numbering" Subparagraph below may describe a feature not available from all manufacturers.

                - Numbering: [Every] [Every five] rack unit(s), on interior of rack.

              - Threads: [10-32] [12-24] [Universal square].

              - Removable and lockable side and top panels.

              - Hinged and lockable front and rear doors.

              - Adjustable feet for leveling.

              - Screened ventilation openings in roof and rear door.

              - Cable access provisions in roof and base.

              - RBB.

              - [Rack] [Roof]-mounted, 550 cfm (260 L/s) fan with filter.

              - Power strip.

              - All cabinets keyed alike.

            - Modular Wall Cabinets:

              - Height: [18 inch (457.2 mm)] [22 inch (558.8 mm)] [As indicated on Drawings] <Insert value>.

              - Depth: [23 inch (584.2 mm)] [29 inch (736.6 mm)] <Insert value>.

              - Load Rating: [150 lb (65 kg)] [200 lb (91 kg)] <Insert value>.

              - Number of Rack Units: [8] [12] [22] [As indicated on Drawings] <Insert number>.

              - Threads: [10-32] [12-24] [Universal square].

              - Lockable front[ and rear] doors.

              - Louvered side panels.

              - Cable access provisions top and bottom.

              - Grounding lug.

              - [Rack] [Roof]-mounted, 250 cfm (118 L/s) fan.

              - Power strip.

              - All cabinets keyed alike.

Retain "UL NWIN - 23 Inch Open Equipment Rack" Paragraph below to specify floor- and wall-mounted equipment racks that are not enclosed. To specify enclosed cabinets, retain "UL NWIN - 23 Inch Enclosed Equipment Rack" Paragraph.

Copy and revise first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - UL NWIN - 23 Inch Open Equipment Rack <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - General Characteristics:

            - Threaded rails designed for mounting telecommunications equipment.

            - Width: Compatible with 23 inch (584.2 mm) equipment mounting.

            - Frames: Modular units designed for telecommunications terminal support and coordinated with dimensions of units to be supported.

            - Finish: Manufacturer's standard, baked-polyester powder coat.

            - Cable Management:

              - Metal, with integral wire retaining fingers.

              - Baked-polyester powder coat finish.

              - Vertical cable management panels have front and rear channels with covers.

              - Horizontal crossover cable manager at top of each relay rack, with minimum height of two rack units each.

          - Options:

            - Configuration: [Two post] [and] [four post].

            - Material: [Extruded steel] [Extruded aluminum] [Sheet steel] [Sheet aluminum].

            - Color: [Black] <Insert color>.

Verify options in "Floor-Mounted Racks" Subparagraph below with rack manufacturer.

            - Floor-Mounted Racks:

              - Overall Height: [72 inch (1828.8 mm)] [84 inch (2133.6 mm)] [As indicated on Drawings] <Insert value>.

              - Overall Depth: [23 inch (584.2 mm)] [29 inch (736.6 mm)] <Insert value>.

              - Rail Depth: [3 inch (76.2 mm)] [6 inch (152.4 mm)] <Insert value>.

              - Two-Post Load Rating: [200 lb (91 kg)] [400 lb (181 kg)] <Insert value>.

              - Four-Post Load Rating: [1000 lb (454 kg)] [2000 lb (907 kg)] <Insert value>.

              - Number of Rack Units per Rack: [38] [42] [45] [52] [58] [As indicated on Drawings] <Insert number>.

"Numbering" Subparagraph below may describe a feature not available from all manufacturers.

                - Numbering: [Every] [Every five] rack unit(s), on interior of rack.

              - Threads: [10-32] [12-24] [Universal square].

              - Vertical and horizontal cable management channels, top and bottom cable troughs, grounding lug[, and a power strip].

              - Base must have minimum four mounting holes for permanent attachment to floor.

              - Top must have provisions for attaching to cable tray or ceiling.

              - Self-leveling.

Verify options in "Wall-Mounted Racks" Subparagraph below with rack manufacturer.

            - Wall-Mounted Racks:

              - Height: [18 inch (457.2 mm)] [22 inch (558.8 mm)] [As indicated on Drawings] <Insert value>.

              - Depth: [23 inch (584.2 mm)] [29 inch (736.6 mm)] <Insert value>.

              - Load Rating: [150 lb (65 kg)] [200 lb (91 kg)] <Insert value>.

              - Number of Rack Units per Rack: [8] [12] [22] [As indicated on Drawings] <Insert number>.

              - Threads: [10-32] [12-24] [Universal square].

              - Wall Attachment: Four pre-punched mounting holes.

"Equipment Access" Subparagraph below is for an option that may not be available from all manufacturers.

              - Equipment Access: Integral swing.

Copy and revise first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - UL NWIN - 23 Inch Enclosed Equipment Rack <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - General Characteristics:

            - Manufacturer-assembled four-post frame enclosed by side and top panels and front and rear doors, designed for mounting telecommunications equipment.

            - Threaded rails designed for mounting telecommunications equipment.

            - Width: Compatible with 23 inch (584.2 mm) equipment mounting.

            - Frames: Modular units designed for telecommunications terminal support and coordinated with dimensions of units to be supported.

            - Finish: Manufacturer's standard, baked-polyester powder coat.

            - Cable Management:

              - Metal, with integral wire retaining fingers.

              - Baked-polyester powder coat finish.

              - Vertical cable management panels have front and rear channels with covers.

              - Horizontal crossover cable manager at top of each relay rack, with minimum height of two rack units each.

          - Options:

            - Material: [Extruded steel] [Extruded aluminum] [Sheet steel] [Sheet aluminum].

            - Color: [Black] <Insert color>.

            - Modular Freestanding Cabinets:

              - Overall Height: [72 inch (1828.8 mm)] [84 inch (2133.6 mm)] [As indicated on Drawings] <Insert value>.

              - Overall Depth: [23 inch (584.2 mm)] [29 inch (736.6 mm)] <Insert value>.

              - Load Rating: [3000 lb (1362 kg)] <Insert value>.

              - Number of Rack Units: [38] [42] [45] [52] [58] [As indicated on Drawings] <Insert number>.

"Numbering" Subparagraph below may describe a feature not available from all manufacturers.

                - Numbering: [Every] [Every five] rack unit(s), on interior of rack.

              - Threads: [10-32] [12-24] [Universal square].

              - Removable and lockable side and top panels.

              - Hinged and lockable front and rear doors.

              - Adjustable feet for leveling.

              - Screened ventilation openings in roof and rear door.

              - Cable access provisions in roof and base.

              - RBB.

              - [Rack] [Roof]-mounted, 550 cfm (260 L/s) fan with filter.

              - Power strip.

              - All cabinets keyed alike.

            - Modular Wall Cabinets:

              - Height: [18 inch (457.2 mm)] [22 inch (558.8 mm)] [As indicated on Drawings] <Insert value>.

              - Depth: [23 inch (584.2 mm)] [29 inch (736.6 mm)] <Insert value>.

              - Load Rating: [150 lb (65 kg)] [200 lb (91 kg)] <Insert value>.

              - Number of Rack Units: [8] [12] [22] [As indicated on Drawings] <Insert number>.

              - Threads: [10-32] [12-24] [Universal square].

              - Lockable front[ and rear] doors.

              - Louvered side panels.

              - Cable access provisions top and bottom.

              - Grounding lug.

              - [Rack] [Roof]-mounted, 250 cfm (118 L/s) fan.

              - Power strip.

              - All cabinets keyed alike.

      - ENCLOSURE-MOUNTED RELOCATABLE POWER TAPS

        - Description: This category covers relocatable power taps rated 250 V(ac) or less, 20 A or less, and intended to supply power to cord-and-plug-connected electrical utilization equipment located inside cabinets, enclosures, and racks.

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

          - Listing Criteria: UL CCN XBYS; including UL 1363.

        - Source Quality Control:

Coordinate "Product Data" Subparagraph below with "Action Submittals" Article.

          - Product Data: Prepare and submit catalog cuts, brochures, and performance data illustrating size, physical appearance, and other characteristics of product.

Retain "Manufacturer's Published Instructions" Subparagraph below when execution requirements state "in accordance with manufacturer's published instructions," especially if those instructions may require preinstallation review and coordination with Construction Documents to verify constructability and commissioning requirements. Coordinate subparagraph with "Informational Submittals" Article.

          - Manufacturer's Published Instructions: Prepare and submit installation, testing, and operating instructions for product.

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - UL XBYS - Enclosure-Mounted Relocatable Power Tap <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - General Characteristics:

            - Rocker-type on-off switch, illuminated when in on position.

            - LED indicator lights for power and protection status.

            - LED indicator lights for reverse polarity and open outlet ground.

          - Options:

            - Wiring Devices: [Six] <Insert quantity> [5-15R] [5-20R] <Insert type> receptacles.

            - Circuit Breaker and Thermal Fusing: [When protection is lost, circuit opens and cannot be reset] [Unit continues to supply power if protection is lost].

            - Cord Length: [Close-coupled, direct plug-in] [15 ft (4.5 m)].

            - Surge Protection: Type 3 SPDs.

Retain subparagraphs below if power strips contain surge protection. In first subparagraph, retain first option for high exposure and cost, second option for medium exposure and cost, and third option for low exposure and cost.

              - Peak Single-Impulse Surge Current Rating: [33] [26] [13] kA per phase.

              - Protection modes must be line to neutral, line to ground, and neutral to ground. UL 1449 clamping voltage for all three modes may not be more than [330 V] <Insert value>.

- EXECUTION

      - PREPARATION

Coordinate "Shop Drawings" Paragraph below with "Action Submittals" Article. Shop drawings may include multi-system and interdisciplinary coordination drawings.

        - Shop Drawings: Prepare and submit the following:

Retain "Shop Drawings for Custom Enclosures and Cabinets" Subparagraph below for custom enclosures and where location of floor boxes is critical.

          - Shop Drawings for Custom Enclosures and Cabinets: Include plans, elevations, sections, and attachment details.

          - Shop Drawings for Racks or Frames:

            - Include plans, elevations, sections, details, and attachments to other work.

            - Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

            - Include workspace requirements and access for cable connections.

            - Grounding: Indicate location of RBB and its mounting detail showing standoff insulators and wall-mounting brackets.

      - SELECTION OF ELECTRICAL CABINETS AND ENCLOSURES

        - Unless more stringent requirements are specified in Contract Documents or manufacturers' written instructions, comply with NFPA 70 for selection of electrical cabinets and enclosures. Consult Architect for resolution of conflicting requirements.

Retain "Degree of Protection" Paragraph below if information is not specified on Drawings or in Part 2. Revise options as necessary to limit freedom of Contractor to select available products to suit Project.

        - Degree of Protection:

See NFPA 70, Paragraph 110.28; UL 50; and UL 50E for additional information on degree of protection types for enclosures. Most-readily available enclosure types are Types 1, 4, 4X, and dual-rated 3R/12; however, all types are available.

          - Outdoors:

Types 3, 3S, 3SX, 3X, 4*, 4X*, 5, 6*, 6P*, 12, 12K, and 13 can be marked "Dusttight." (*The optional marking for these types is new for the 2020 edition of NFPA 70 and has not yet been incorporated into UL 50 and UL 50E.)

Retain Type 4 or Type 3 option in first subparagraph below if Project site is subject to windblown dust. Type 3R is rainproof; Type 4 is watertight; Type 3 is raintight.

            - [Type 3R] [Type 4] [Type 3] unless otherwise indicated.

            - Locations Exposed to Hosedown: [Type 4] [Type 6] [Type 6P].

            - Locations Subject to Potential Flooding: Type 6P.

            - Locations Aboveground Where Mechanism Must Operate When Ice Covered: Type 3S.

            - Locations in-Ground or Exposed to Corrosive Agents: [Type 4X] [Type 6P] [Type 3RX].

            - Locations in-Ground or Exposed to Corrosive Agents Where Mechanism Must Operate When Ice Covered: Type 3SX.

          - Indoors:

            - Type 1 unless otherwise indicated.

            - Damp or Dusty Locations: [Type 12] [Type 2] [Type 4] [Type 5].

            - Surface Mounted in Kitchens and Other Locations Exposed to Oil or Coolants: Type 12.

            - Flush Mounted in Kitchens and Other Locations Exposed to Oil or Coolants: [Type 12] [Type 12K].

            - Locations Exposed to Airborne Dust, Lint, Fibers, or Flyings: [Type 4] [Type 6].

            - Locations Exposed to Hosedown: [Type 4] [Type 6] [Type 6P].

            - Locations Exposed to Brief Submersion: [Type 6] [Type 6P].

            - Locations Exposed to Prolonged Submersion: Type 6P.

            - Locations Exposed to Corrosive Agents: [Type 4X] [Type 6P].

            - Locations Exposed to Spraying Oil or Coolants: Type 13.

      - INSTALLATION ELECTRICAL CABINETS AND ENCLOSURES

        - Comply with manufacturer's published instructions.

NFPA 70 and NECA NEIS 1 are already specified in Section 260010 "Supplemental Requirements for Electrical." Retain "Reference Standards for Installation" Paragraph below to specify other standards applicable to Work specified in this Section.

        - Reference Standards for Installation: Unless more stringent installation requirements are specified in Contract Documents or manufacturers' published instructions, comply with the following:

          - Cabinets and Cutout Boxes: Article 312 of NFPA 70.

          - Consult Architect for resolution of conflicting requirements.

        - Special Installation Techniques:

          - Mount cabinets and enclosures at heights indicated on Drawings. If mounting heights of boxes are not individually indicated, give priority to ADA requirements. Install boxes with height measured to [center] [top] [bottom] of box unless otherwise indicated.

          - Do not install cabinets, enclosures, or fittings in contact with concrete or earth.

          - Do not rely on locknuts to penetrate nonconductive coatings on enclosures. Remove coatings in the locknut area prior to assembling conduit to enclosure to ensure a continuous ground path.

          - Identification: Provide labels for cabinets, enclosures, racks and associated electrical equipment.

            - Identify field-installed conductors, interconnecting wiring, and components.

            - Provide warning signs.

            - Label each cabinet, enclosure, and rack with engraved metal or laminated-plastic nameplate.

        - Interfaces with Other Work:

          - Coordinate installation of new products for <Insert system or product family/category> with existing conditions.

            - <Insert requirements for transition between new and existing>.

          - Coordinate with Section 078413 "Penetration Firestopping" for installation of sealants.

          - Grounding and Bonding:

            - Cabinets, Enclosures, and Racks for Electrical Systems: Coordinate with Section 260526 "Grounding and Bonding for Electrical Systems" for grounding of RBBs.

            - Cabinets, Enclosures, and Racks for Communications Systems and Electronic Safety and Security Systems: Coordinate with Section 270526 "Grounding and Bonding for Communications Systems" for grounding of RBBs.

          - Coordinate with Section 260573.13 "Short-Circuit Studies" for determining available fault current on input feeder.

          - Coordinate with Section 260573.19 "Arc-Flash Hazard Analysis" for determining arc-flash hazard on input feeder.

          - Coordinate with <Insert Section number and title> for <Insert description of interfacing related Work>.

            - <Insert requirements for transition between this Section and related Work>.

      - CLEANING

        - Remove construction dust and debris from cabinets, enclosures, and racks.

      - PROTECTION

        - Protect coatings and finishes of cabinets, enclosures, and racks from damage and deterioration.

          - Repair damage to galvanized finishes with zinc-rich paint recommended by manufacturer.

          - Repair damage to PVC coatings or paint finishes with matching touchup coating recommended by manufacturer.

END OF SECTION 262716