Copyright 2022 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 262726.11 - GENERAL-USE SWITCHES, DIMMER SWITCHES, AND FAN-SPEED CONTROLLER SWITCHES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED 2009, LEED v4, LEED v4.1, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using the hypertext links.

- GENERAL

      - SUMMARY

        - Section Includes:

          - General-use switches.

          - General-use dimmer switches.

          - General-use fan-speed controller switches.

        - Related Requirements:

Always retain first two subparagraphs below.

          - Section 260010 "Supplemental Requirements for Electrical" for additional abbreviations, definitions, submittals, qualifications, testing agencies, and other Project requirements applicable to Work specified in this Section.

          - Section 260011 "Facility Performance Requirements for Electrical" for seismic-load, wind-load, acoustical, and other field conditions applicable to Work specified in this Section.

Retain subparagraph(s) below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 260923 "Lighting Control Devices" for occupancy sensors, timers, control-voltage switches, and control-voltage dimmers.

          - Section 260936 "Modular Dimming Controls" for multiscene and multipreset dimming controls.

          - Section 260943.16 "Addressable Luminaire Lighting Controls" for network lighting control solid-state devices.

          - Section 260943.23 "Relay-Based Lighting Controls" for network lighting control relay devices.

      - ALLOWANCES

Retain this article if products and Work included in this Section are covered by lump-sum, unit-cost, quantity, or testing and inspection allowances.

        - See Section 012100 "Allowances" for description of allowances affecting items specified in this Section.

      - UNIT PRICES

Retain this article if products and Work specified in this Section are measured and paid for under the provisions of unit prices.

        - See Section 012200 "Unit Prices" for description of unit prices affecting items specified in this Section.

      - ALTERNATES

Retain this article if products and Work specified in this Section are proposed to be added to or deducted from the base bid amount under the provisions of alternates.

        - See Section 012300 "Alternates" for description of alternates affecting items specified in this Section.

      - DEFINITIONS

Do not duplicate common acronyms, abbreviations, and terms defined in Section 260010 "Supplemental Requirements for Electrical."

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - UL 1472 Type I Dimmer: Dimmer in which air-gap switch is used to energize preset lighting levels.

        - UL 1472 Type II Dimmer: Dimmer with air-gap switch that opens and closes load circuit at minimum output voltage setting only.

        - UL 1472 Type IIa Dimmer: Dimmer with air-gap switch that opens and closes load circuit at maximum output voltage setting only.

        - UL 1472 Type III Dimmer: Dimmer incorporating solid-state components providing preestablished rectified output settings.

        - UL 1472 Type IV Dimmer: Dimmer not covered by UL 1472 Types I through III.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

          - General-use switches.

          - General-use dimmer switches.

          - General-use fan-speed controller switches.

Retain "Samples" Paragraph below if products have critical features needing hands-on appraisal.

        - Samples:

Retain one or more of seven subparagraphs below to suit Project.

          - One for each kind of toggle switch[ and cover plate accessory] specified, in each finish and color specified.

          - One for each kind of key lock switch[ and cover plate accessory] specified, in each finish and color specified.

          - One for each kind of maintained-contact switch[ and cover plate accessory] specified, in each finish and color specified.

          - One for each kind of momentary-contact switch[ and cover plate accessory] specified, in each finish and color specified.

          - One for each kind of rocker switch[ and cover plate accessory] specified, in each finish and color specified.

          - One for each kind of dimmer switch[ and cover plate accessory] specified, in each finish and color specified.

          - One for each kind of fan-speed controller switch[ and cover plate accessory] specified, in each finish and color specified.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

      - INFORMATIONAL SUBMITTALS

Retain "Manufacturers' Instructions" Paragraph below when execution requirements state "in accordance with manufacturer's instructions," especially if those instructions may require preinstallation review and coordination with Construction Documents to verify constructability and commissioning requirements.

        - Manufacturers' Instructions: Record copy of official installation[ and testing] instructions issued to Installer by manufacturer for the following:

          - Dimmers.

          - Fan-speed controllers.

      - CLOSEOUT SUBMITTALS

Submittals for record documents, operation and maintenance data, software, and software documentation are specified in Section 260010 "Supplemental Requirements for Electrical."

        - Sustainable Design Closeout Documentation:

          - <Double click to insert sustainable design closeout text for switches and dimmers>

      - MAINTENANCE MATERIAL SUBMITTALS

See Section 017700 "Closeout Procedures" for submission of maintenance material items.

Extra stock items are replacement products.

        - Extra Stock Items: Furnish extra materials to Owner that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Extra Keys for Key Lock Switches: [One] <Insert number> of each kind.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - EXISTING PRODUCTS TO BE MODIFIED

        - Basis for Pricing: <Insert name of manufacturer; model number or series for existing product>.

        - Description: <Insert description of existing product, including special features, options, and finishes that may impact Work>.

        - Accessories: <Insert accessories included with existing product>.

      - EXISTING PRODUCTS TO BE REMOVED AND RE-INSTALLED

        - Basis for Pricing: <Insert name of manufacturer; model number or series for existing product>.

        - Description: <Insert description of existing product, including special features, options, and finishes that may impact Work>.

        - Accessories: <Insert accessories included with existing product>.

      - GENERAL-USE SWITCHES

        - Description: Snap switches intended for mounting in device boxes.

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

            - <Insert requirements>.

          - General Characteristics:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Reference Standards: UL CCN WMUZ and UL 20.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Toggle Switch <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration:

Retain one of first five subparagraphs below.

              - General-duty, 120-277 V, 15 A, [single pole] [double pole] [three way] [four way].

              - General-duty, 120-277 V, 20 A, [single pole] [double pole] [three way] [four way].

              - Extra-heavy-duty, 120-277 V, 15 A, [single pole] [double pole] [three way] [four way].

              - Extra-heavy-duty, 120-277 V, 20 A, [single pole] [double pole] [three way] [four way].

              - Extra-heavy-duty, 120-277 V, 30 A, [single pole] [double pole] [three way].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Toggle Switch with Pilot Light <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [Red] [Clear].

            - Configuration:

Retain one of first five subparagraphs below.

              - Illuminated when load off, 120-277 V, 15 A, [single pole] [three way].

              - Illuminated when load off, 120-277 V, 20 A, [single pole] [three way].

              - Illuminated when load on, 120-277 V, 15 A, [single pole] [double pole] [three way].

              - Illuminated when load on, 120-277 V, 20 A, [single pole] [double pole] [three way].

              - Illuminated when load on, 120-277 V, 30 A, [single pole] [double pole].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Toggle Switch with Forked Key Lock <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Black] [As indicated on architectural Drawings].

            - Configuration:

Retain one of three subparagraphs below.

              - 120-277 V, 15 A, [single pole] [double pole] [three way] [four way].

              - 120-277 V, 20 A, [single pole] [double pole] [three way] [four way].

              - 120-277 V, 30 A, [single pole] [double pole].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Toggle Switch with Barrel Key Lock <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Configuration: 120-277 V, 20 A, [single pole] [single pole, key removable in off position only] [double pole] [three way] [four way].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Maintained-Contact, Center-Off, Toggle Switch <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Brown] [As indicated on architectural Drawings].

            - Configuration:

Retain one of two subparagraphs below.

              - Single pole, double throw, 120-277 V, [15 A] [20 A].

              - Double pole, double throw, 120-277 V, [15 A] [20 A] [30 A].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Momentary-Contact, Center-Off, Toggle Switch <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration: Single pole, double throw, 120-277 V, [15 A] [20 A].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Momentary-Contact, Center-Off, Toggle Switch with Forked Key Lock <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration: Single pole, double throw, 120-277 V, [15 A] [20 A].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Rocker Switch <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration:

Retain one of first two subparagraphs below.

              - 120-277 V, 15 A, [single pole] [three way] [four way].

              - 120-277 V, 20 A, [single pole] [double pole] [three way] [four way].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Rocker Switch with Nightlight <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration: 120-277 V, 20 A, [single pole] [three way] [four way].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Rocker Switch with Pilot Light <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration:

Retain one of first two subparagraphs below.

              - Illuminated when load on, 120-277 V, 20 A, [single pole] [three way].

              - Illuminated when load off, 120-277 V, 20 A, [single pole].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

      - GENERAL-USE DIMMER SWITCHES

        - Description: Line-voltage dimmers intended for mounting in flush device boxes or on outlet box covers (wall box).

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - General Characteristics:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Reference Standards: UL CCN EOYX and UL 1472.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Type I Dimmer Switch <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Additional Characteristics: UL 1472 Type I dimmer.

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Switch Style: [Toggle] [Rocker] [Push-button].

            - Dimming Control Style: [Slide] [Rotary].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Type II Dimmer Switch <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Additional Characteristics:

            - UL 1472 Type II dimmer.

            - Switch Style: Air-gap switch at dimmer control end of travel at minimum output voltage.

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Dimming Control Style: [Slide] [Rotary].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Type IIa Dimmer Switch <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Additional Characteristics:

            - UL 1472 Type IIa dimmer.

            - Switch Style: Air-gap switch at dimmer control end of travel at maximum output voltage.

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Dimming Control Style: [Slide] [Rotary].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Type III Dimmer Switch <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Additional Characteristics: UL 1472 Type III dimmer.

          - Options:

Retain one or more of first four subparagraphs below to suit Project.

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Switch Style: [Momentary toggle] [Momentary rocker] [Push-button].

            - Dimming Control Style: [Momentary toggle] [Momentary rocker] [Push-button].

            - Network connection to provide programmable presets, scenes, and time-clock.

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Type IV Dimmer Switch <Insert drawing designation>:

          - Additional Characteristics: UL 1472 Type IV dimmer.

            - Switch Style: <Insert characteristics>.

            - Dimming Control Style: <Insert characteristics>.

            - <Insert other characteristics>.

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

      - GENERAL-USE FAN-SPEED CONTROLLER SWITCHES

        - Description: Semiconductor, capacitive-type, and inductive-type fan-speed controllers for regulating speed of fan motor, including starting and stopping of fan motor, intended for mounting in flush device boxes or on outlet box covers (wall box).

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - General Characteristics:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Reference Standards: UL CCN GQHG and UL 1917.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Air-Gap Fan-Speed Controller Switch <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Solid-State Fan-Speed Controller Switch <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

- EXECUTION

      - INSTALLATION

        - Comply with manufacturer's instructions.

NFPA 70 and NECA NEIS 1 are already specified in Section 260010 "Supplemental Requirements for Electrical." Retain "Reference Standards" Paragraph below to specify other standards applicable to Work specified in this Section.

        - Reference Standards:

          - Unless more stringent requirements are specified in Contract Documents or manufacturers' instructions, comply with installation instructions in NECA NEIS 130.

          - Mounting Heights: Unless otherwise indicated in Contract Documents, comply with mounting heights recommended in NECA NEIS 1.

          - Consult Architect for resolution of conflicting requirements.

        - Identification:

          - Identify cover or cover plate for device with panelboard identification and circuit number in accordance with Section 260553 "Identification for Electrical Systems."

Retain first subparagraph below if self-adhesive labels on cover or cover plate are unacceptable.

            - Mark cover or cover plate using hot, stamped, or engraved machine printing with [black] [white] [red]-filled lettering, and provide durable wire markers or tags inside device box or outlet box.

Retain "Healthcare Facilities" Subparagraph below to provide the distinctive color or marking required by Article 517 of NFPA 70 and NFPA 99.

            - Healthcare Facilities: Distinctively identify covers or cover plates of device boxes and outlet boxes that are supplied from life safety and critical branch power supplies following facility's standard practice.

        - Interfaces with Other Work:

          - Coordinate installation of new products for <Insert system or product group> with existing conditions.

            - <Insert requirements for transition between new and existing>.

          - Coordinate with <Insert Section number and title> for <Insert description of interfacing related Work>.

            - <Insert requirements for transition between this Section and related Work>.

      - FIELD QUALITY CONTROL

        - Acceptance Testing Preparation:

          - <Insert requirements>.

Retain first paragraph below to require that field quality-control tests be witnessed. Local ordinance or custom may require that authorities having jurisdiction witness the testing.

        - Field tests and inspections must be witnessed by [Architect] [Tenant] [authorities having jurisdiction] <Insert names or titles of witnesses>.

        - Tests and Inspections:

          - Perform tests and inspections in accordance with manufacturers' instructions.

          - <Insert tests and inspections>.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Nonconforming Work:

          - Unit will be considered defective if it does not pass tests and inspections.

          - Remove and replace defective units and retest.

        - Assemble and submit test and inspection reports.

Retain "Manufacturer Services" Paragraph below if manufacturer's representative is required to support or supervise the administrant specified in Section 260010 "Supplemental Requirements for Electrical" for field tests and inspections performed by Installer or third-party agencies.

        - Manufacturer Services:

Retain "supervise" option in subparagraph below when third-party tests and inspections must be witnessed and approved by factory-authorized service representative to satisfy special extended warranty requirements. In some cases, Installer may be factory authorized under warranty provisions to fulfill this role.

          - Engage factory-authorized service representative to [support] [supervise] field tests and inspections.

      - SYSTEM STARTUP

        - [Engage a factory-authorized service representative to perform] [Perform] startup service.

          - Complete installation and startup checks for momentary switches, dimmer switches, and fan-speed controller switches in accordance with manufacturer's instructions.

      - PROTECTION

        - Schedule and sequence installation to minimize risk of contamination of wires and cables, devices, device boxes, outlet boxes, covers, and cover plates by plaster, drywall joint compound, mortar, cement, concrete, dust, paint, and other materials.

        - After installation, protect wires and cables, devices, device boxes, outlet boxes, covers, and cover plates from construction activities. Remove and replace items that are contaminated, defaced, damaged, or otherwise caused to be unfit for use prior to acceptance by Owner.

END OF SECTION 262726.11