Copyright 2022 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 262726.33 - GENERAL-GRADE DUPLEX STRAIGHT-BLADE RECEPTACLES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED 2009, LEED v4, LEED v4.1, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using the hypertext links.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Duplex straight-blade receptacles.

          - Duplex straight-blade receptacles with integral switching means.

        - Related Requirements:

Always retain first two subparagraphs below.

          - Section 260010 "Supplemental Requirements for Electrical" for additional abbreviations, definitions, submittals, qualifications, testing agencies, and other Project requirements applicable to Work specified in this Section.

          - Section 260011 "Facility Performance Requirements for Electrical" for seismic-load, wind-load, acoustical, and other field conditions applicable to Work specified in this Section.

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 262726.31 "General-Grade Single Straight-Blade Receptacles" for single receptacles.

          - Section 262726.35 "Hospital-Grade Straight-Blade Receptacles" for hospital-grade receptacles.

          - Section 262726.37 "Receptacles with Arc-Fault and Ground-Fault Protective Devices" for AFCI and GFCI receptacles.

          - Section 262726.39 "Locking Receptacles" for twist-locking receptacles.

          - Section 262726.41 "Pin-and-Sleeve Receptacles" for pin-and-sleeve receptacles.

      - ALLOWANCES

Retain this article if products and Work included in this Section are covered by lump-sum, unit-cost, quantity, or testing and inspection allowances.

        - See Section 012100 "Allowances" for description of allowances affecting items specified in this Section.

      - UNIT PRICES

Retain this article if products and Work specified in this Section are measured and paid for under the provisions of unit prices.

        - See Section 012200 "Unit Prices" for description of unit prices affecting items specified in this Section.

      - ALTERNATES

Retain this article if products and Work specified in this Section are proposed to be added to or deducted from the base bid amount under the provisions of alternates.

        - See Section 012300 "Alternates" for description of alternates affecting items specified in this Section.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

          - Duplex straight-blade receptacles.

          - Duplex straight-blade receptacles with integral switching means.

        - Shop Drawings:

          - Wiring diagrams for duplex straight-blade receptacles with integral switching means.

Retain "Samples" Paragraph below if products have critical features needing hands-on appraisal.

        - Samples:

Retain one of two subparagraphs below, or both, to suit Project.

          - One for each kind of duplex straight-blade receptacle[ and cover plate accessory] specified, in each finish and color specified.

          - One for each kind of duplex straight-blade receptacle with integral switching means[ and cover plate accessory] specified, in each finish and color specified.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

      - INFORMATIONAL SUBMITTALS

Retain "Manufacturers' Instructions" Paragraph below when execution requirements state "in accordance with manufacturer's instructions," especially if those instructions may require preinstallation review and coordination with Construction Documents to verify constructability and commissioning requirements.

        - Manufacturers' Instructions: Record copy of official installation[ and testing] instructions issued to Installer by manufacturer for the following:

          - Duplex straight-blade receptacles.

          - Duplex straight-blade receptacles with integral switching means.

        - Sample warranties.

      - CLOSEOUT SUBMITTALS

Submittals for record documents, operation and maintenance data, software, and software documentation are specified in Section 260010 "Supplemental Requirements for Electrical."

        - Warranty documentation.

        - Sustainable Design Closeout Documentation:

          - <Double click to insert sustainable design closeout text for controlled receptacles>

      - MAINTENANCE MATERIAL SUBMITTALS

See Section 017700 "Closeout Procedures" for submission of maintenance material items.

Extra stock items are replacement products.

        - Extra Stock Items: Furnish extra materials to Owner that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - SPD Receptacles: Equal to [10] <Insert number> percent of quantity installed for each kind specified, but no fewer than [one] <Insert number> units.

          - Controlled Receptacles: Equal to [10] <Insert number> percent of quantity installed for each kind specified, but no fewer than [one] <Insert number> units.

Special tools are items that would not be available from a typical hardware store.

        - Special Tools: Proprietary equipment and software required to maintain, repair, adjust, or implement future changes to controlled receptacles.

      - WARRANTY

When warranties are required and available, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner, after one-year correction period specified in the Contract, under Contractor's general warranty and prevailing local laws.

Verify durations of extended warranty periods needed.

        - Special Manufacturer Extended Warranty: Manufacturer warrants that devices perform in accordance with specified requirements and agrees to provide repair or replacement of devices that fail to perform as specified within extended warranty period.

          - Initial Extended Warranty Period: [Three] [Four] [Five] <Insert number> years from date of Substantial Completion; [full] [prorated] coverage for labor, materials, and equipment.

Retain transient voltage surges option in "Follow-On Extended Warranty Period" Subparagraph below if device includes surge protection.

Retain "origin" option in subparagraph if recipient assumes ownership of goods when they are shipped. Retain "destination" option if seller retains ownership of goods until they are delivered. Damaged shipping containers labeled "FOB Origin" cannot be returned to sender, but carrier is liable to recipient for delay and damage claims.

          - Follow-On Extended Warranty Period: [Eight] <Insert number> years from date of Substantial Completion; [full] [prorated] coverage for materials[ that failed because of transient voltage surges] only, free on board [origin] [destination], freight prepaid.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - EXISTING PRODUCTS TO BE MODIFIED

        - Basis for Pricing: <Insert name of manufacturer; model number or series for existing product>.

        - Description: <Insert description of existing product, including special features, options, and finishes that may impact Work>.

        - Accessories: <Insert accessories included with existing product>.

      - EXISTING PRODUCTS TO BE REMOVED AND RE-INSTALLED

        - Basis for Pricing: <Insert name of manufacturer; model number or series for existing product>.

        - Description: <Insert description of existing product, including special features, options, and finishes that may impact Work>.

        - Accessories: <Insert accessories included with existing product>.

      - DUPLEX STRAIGHT-BLADE RECEPTACLES

        - Description: General-grade duplex receptacles for use in wiring systems recognized by NFPA 70.

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - General Characteristics:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Reference Standards:

              - UL CCN RTRT and UL 498.

              - Surge Protective Devices: UL 1449, Type 3.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Duplex Straight-Blade Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration:

Retain one of first 13 subparagraphs below.

              - General-duty, [NEMA 5-15R] [NEMA 5-20R].

              - General-duty, smooth face, [NEMA 5-15R] [NEMA 5-20R].

              - General-duty, [NEMA 6-15R] [NEMA 6-20R].

              - General-duty, smooth face, [NEMA 6-15R] [NEMA 6-20R].

              - Heavy-duty, [NEMA 5-15R] [NEMA 5-20R].

              - Heavy-duty, smooth face, [NEMA 5-15R] [NEMA 5-20R].

              - Heavy-duty, [NEMA 6-15R] [NEMA 6-20R].

              - Heavy-duty, smooth face, NEMA 6-15R.

              - Heavy-duty, NEMA 7-15R.

              - Extra-heavy-duty, [NEMA 5-15R] [NEMA 5-20R].

              - Extra-heavy-duty, smooth face, [NEMA 5-15R] [NEMA 5-20R].

              - Extra-heavy-duty, [NEMA 6-15R] [NEMA 6-20R].

              - Extra-heavy-duty, smooth face, [NEMA 6-15R] [NEMA 6-20R].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Nightlight-Type, Lighted Duplex Straight-Blade Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration: General-duty, [NEMA 5-15R] [NEMA 5-20R].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Tamper-Resistant Duplex Straight-Blade Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration:

Retain one of first five subparagraphs below.

              - General-duty, [NEMA 5-15R] [NEMA 5-20R].

              - General-duty, smooth face, [NEMA 5-15R] [NEMA 5-20R].

              - Heavy-duty, [NEMA 5-15R] [NEMA 5-20R].

              - Heavy-duty, smooth face, [NEMA 5-15R] [NEMA 5-20R].

              - Extra-heavy-duty, [NEMA 5-15R] [NEMA 5-20R].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Recessed, Tamper-Resistant Duplex Straight-Blade Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration:

Retain one of first two subparagraphs below.

              - General-duty, [NEMA 5-15R] [NEMA 5-20R].

              - General-duty, smooth face, [NEMA 5-15R] [NEMA 5-20R].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Weather-Resistant Duplex Straight-Blade Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration:

Retain one of first four subparagraphs below.

              - General-duty, [NEMA 5-15R] [NEMA 5-20R].

              - Heavy-duty, [NEMA 5-15R] [NEMA 5-20R].

              - Heavy-duty, smooth face, [NEMA 5-15R] [NEMA 5-20R].

              - Extra-heavy-duty, [NEMA 5-15R] [NEMA 5-20R].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Weather-Resistant, Tamper-Resistant Duplex Straight-Blade Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration:

Retain one of first three subparagraphs below.

              - General-duty, [NEMA 5-15R] [NEMA 5-20R].

              - General-duty, smooth face, [NEMA 5-15R] [NEMA 5-20R].

              - Heavy-duty, smooth face, [NEMA 5-15R] [NEMA 5-20R].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Isolated Ground Duplex Straight-Blade Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration:

Retain one of first six subparagraphs below.

              - General-duty, [NEMA 5-15R] [NEMA 5-20R].

              - General-duty, smooth face, [NEMA 5-15R] [NEMA 5-20R].

              - Heavy-duty, [NEMA 5-15R] [NEMA 5-20R].

              - Heavy-duty, smooth face, [NEMA 5-15R] [NEMA 5-20R].

              - Extra-heavy-duty, [NEMA 5-15R] [NEMA 5-20R].

              - Extra heavy-duty, [NEMA 6-15R] [NEMA 6-20R].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Tamper-Resistant, Isolated Ground Duplex Straight-Blade Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration:

Retain one of first two subparagraphs below.

              - Heavy-duty, [NEMA 5-15R] [NEMA 5-20R].

              - Heavy-duty, smooth face, [NEMA 5-15R] [NEMA 5-20R].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Weather-Resistant, Isolated Ground Duplex Straight-Blade Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration: Extra-heavy-duty, [NEMA 5-15R] [NEMA 5-20R].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Duplex Straight-Blade Receptacle with Type 3 Surge Protective Device <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration: Heavy-duty, smooth face, [NEMA 5-15R] [NEMA 5-20R].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Tamper-Resistant Duplex Straight-Blade Receptacle with Type 3 Surge Protective Device <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration: Heavy-duty, smooth face, [NEMA 5-15R] [NEMA 5-20R].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Isolated Ground Duplex Straight-Blade Receptacle with Type 3 Surge Protective Device <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration: Heavy-duty, smooth face, [NEMA 5-15R] [NEMA 5-20R].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Tamper-Resistant Duplex Straight-Blade Receptacle with USB Outlet to Power Class 2 Equipment <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration:

Retain one of first five subparagraphs below.

              - General-duty, [NEMA 5-15R] [NEMA 5-20R]; two USB-A ports.

              - General-duty, [NEMA 5-15R] [NEMA 5-20R]; two USB-C ports.

              - General-duty, [NEMA 5-15R] [NEMA 5-20R]; one USB-A port; one USB-C port.

              - General-duty, smooth face, two USB-A ports.

              - General-duty, smooth face, four USB-A ports.

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

      - DUPLEX STRAIGHT-BLADE RECEPTACLES WITH INTEGRAL SWITCHING MEANS

        - Description: Controlled receptacles with integral switching means, intended to be installed on a 20 A maximum branch circuit and for use in dry locations, in accordance with NFPA 70.

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - General Characteristics:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Reference Standards: UL CCN RTXI and UL Subject 498B.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Wired Full-Controlled Duplex Straight-Blade Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration: [NEMA 5-15R] [NEMA 5-20R].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Wired Half-Controlled Duplex Straight-Blade Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration: [NEMA 5-15R] [NEMA 5-20R].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Wireless Full-Controlled Duplex Straight-Blade Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration: [NEMA 5-15R] [NEMA 5-20R].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Wireless Half-Controlled Duplex Straight-Blade Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Coordinate "Device Color" Subparagraph below with architectural requirements. Blue, green, office white, almond, and light almond are not defined in NEMA WD 1, so the same color from different manufacturers may not match. Verify availability of colors with manufacturers.

            - Device Color: [Ivory] [White] [Gray] [Brown] [Black] [Red] [Yellow] [Orange] [ in accordance with NEMA WD 1] [Blue] [Green] [Office White] [Almond] [Light Almond] [As indicated on architectural Drawings].

            - Configuration: [NEMA 5-15R] [NEMA 5-20R].

Retain "Accessories" Subparagraph below only if this cover plate must exactly match color of this wiring device. Use Section 260533.16 "Boxes and Covers for Electrical Systems" to specify common covers or cover plates with matching colors or finishes for use with multiple wiring devices.

          - Accessories:

            - Cover Plate: 0.060 inch (1.5 mm) thick, high-impact thermoplastic (nylon) with smooth finish and color matching wiring device; from same manufacturer as wiring device.

            - Securing Screws for Cover Plate: Metal with head color matching wallplate finish.

- EXECUTION

      - EXAMINATION

        - Verify that receptacles to be procured and installed for Owner-furnished equipment are compatible with mating attachment plugs on equipment.

      - SELECTION OF CONTROLLED AND UNCONTROLLED RECEPTACLES

        - <Double click to insert sustainable design text for selection of controlled receptacles>

      - INSTALLATION

        - Comply with manufacturer's instructions.

NFPA 70 and NECA NEIS 1 are already specified in Section 260010 "Supplemental Requirements for Electrical." Retain "Reference Standards" Paragraph below to specify other standards applicable to Work specified in this Section.

        - Reference Standards:

          - Unless more stringent requirements are specified in Contract Documents or manufacturers' instructions, comply with installation instructions in NECA NEIS 130.

          - Mounting Heights: Unless otherwise indicated in Contract Documents, comply with mounting heights recommended in NECA NEIS 1.

          - Receptacle Orientation: Unless otherwise indicated in Contract Documents, orient receptacle to match configuration diagram in NEMA WD 6.

          - Consult Architect for resolution of conflicting requirements.

        - Identification:

          - Identify cover or cover plate for device with panelboard identification and circuit number in accordance with Section 260553 "Identification for Electrical Systems."

Retain first subparagraph below if self-adhesive labels on cover or cover plate are unacceptable.

            - Mark cover or cover plate using hot, stamped, or engraved machine printing with [black] [white] [red]-filled lettering, and provide durable wire markers or tags inside device box or outlet box.

Retain "Healthcare Facilities" Subparagraph below to provide the distinctive color or marking required by Article 517 of NFPA 70 and NFPA 99.

            - Healthcare Facilities: Distinctively identify covers or cover plates of device boxes and outlet boxes that are supplied from life safety and critical branch power supplies following facility's standard practice.

        - Interfaces with Other Work:

Surge protection works by creating an intentional ground fault to divert the surge current, which will cause nuisance tripping of upstream ground-fault devices. This nuisance tripping is a frequent problem for wet laboratory workbenches when occupants plug their own SPDs for computing equipment into a GFCI-protected outlet.

          - Do not install Type 3 SPD, including surge-protected relocatable taps and power strips, on branch circuit downstream of GFCI device.

          - Coordinate installation of new products for <Insert system or product group> with existing conditions.

            - <Insert requirements for transition between new and existing>.

          - Coordinate with <Insert Section number and title> for <Insert description of interfacing related Work>.

            - <Insert requirements for transition between this Section and related Work>.

      - FIELD QUALITY CONTROL

        - Acceptance Testing Preparation:

          - <Insert requirements>.

Retain first paragraph below to require that field quality-control tests be witnessed. Local ordinance or custom may require that authorities having jurisdiction witness the testing.

        - Field tests and inspections must be witnessed by [Architect] [Tenant] [authorities having jurisdiction] <Insert names or titles of witnesses>.

        - Tests and Inspections:

          - Insert and remove test plug to verify that device is securely mounted.

          - Verify polarity of hot and neutral pins.

          - Measure line voltage.

          - Measure percent voltage drop.

          - Measure grounding circuit continuity; impedance must be not greater than 2 ohms.

Retain "Healthcare Facilities" Subparagraph below to comply with Requirement 6.3.3.2.4 of NFPA 99.

          - Healthcare Facilities: Test straight-blade receptacles in patient care spaces with receptacle pin tension test instrument in accordance with NFPA 99. Retention force of ground pin must be not less than 115 g (4 oz).

          - Perform additional installation and maintenance inspections and diagnostic tests in accordance with NECA NEIS 130 and manufacturers' instructions.

          - <Insert tests and inspections>.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Nonconforming Work:

          - Device will be considered defective if it does not pass tests and inspections.

          - Remove and replace defective units and retest.

        - Assemble and submit test and inspection reports.

Retain "Manufacturer Services" Paragraph below if manufacturer's representative is required to support or supervise the administrant specified in Section 260010 "Supplemental Requirements for Electrical" for field tests and inspections performed by Installer or third-party agencies.

        - Manufacturer Services:

Retain "supervise" option in subparagraph below when third-party tests and inspections must be witnessed and approved by factory-authorized service representative to satisfy special extended warranty requirements. In some cases, Installer may be factory authorized under warranty provisions to fulfill this role.

          - Engage factory-authorized service representative to [support] [supervise] field tests and inspections.

      - ADJUSTING

        - Occupancy Adjustments for Controlled Receptacles: When requested within [12] <Insert number> months from date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions. Provide up to [two] <Insert number> visits to Project during other-than-normal occupancy hours for this purpose.

      - PROTECTION

        - Schedule and sequence installation to minimize risk of contamination of wires and cables, devices, device boxes, outlet boxes, covers, and cover plates by plaster, drywall joint compound, mortar, cement, concrete, dust, paint, and other materials.

        - After installation, protect wires and cables, devices, device boxes, outlet boxes, covers, and cover plates from construction activities. Remove and replace items that are contaminated, defaced, damaged, or otherwise caused to be unfit for use prior to acceptance by Owner.

END OF SECTION 262726.33