Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 262726.39 - LOCKING RECEPTACLES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Locking receptacles.

        - Related Requirements:

Always retain first two subparagraphs below.

          - Section 260010 "Supplemental Requirements for Electrical" for additional abbreviations, definitions, submittals, qualifications, testing agencies, and other Project requirements applicable to Work specified in this Section.

          - Section 260011 "Facility Performance Requirements for Electrical" for seismic-load, wind-load, acoustical, and other field conditions applicable to Work specified in this Section.

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 262726.31 "General-Grade Single Straight-Blade Receptacles" for single receptacles.

          - Section 262726.33 "General-Grade Duplex Straight-Blade Receptacles" for duplex receptacles that are not hospital grade.

          - Section 262726.35 "Hospital-Grade Straight-Blade Receptacles" for hospital-grade receptacles.

          - Section 262726.37 "Receptacles with Arc-Fault and Ground-Fault Protective Devices" for AFCI and GFCI receptacles.

          - Section 262726.41 "Pin-and-Sleeve Receptacles" for pin-and-sleeve receptacles.

      - ALLOWANCES

Retain this article if products and Work included in this Section are covered by lump-sum, unit-cost, quantity, or testing and inspection allowances.

        - See Section 012100 "Allowances" for description of allowances affecting items specified in this Section.

      - UNIT PRICES

Retain this article if products and Work specified in this Section are measured and paid for under the provisions of unit prices.

        - See Section 012200 "Unit Prices" for description of unit prices affecting items specified in this Section.

      - ALTERNATES

Retain this article if products and Work specified in this Section are proposed to be added to or deducted from the base bid amount under the provisions of alternates.

        - See Section 012300 "Alternates" for description of alternates affecting items specified in this Section.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

          - Locking receptacles.

Retain "Samples" Paragraph below if products have critical features needing hands-on appraisal.

        - Samples:

          - One for each kind of locking receptacle[ and cover plate accessory] specified, in each finish and color specified.

Retain "Field Quality-Control Submittals" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field Quality-Control Submittals:

          - Field quality-control reports.

      - INFORMATIONAL SUBMITTALS

Retain "Manufacturers' Instructions" Paragraph below when execution requirements state "in accordance with manufacturer's instructions," especially if those instructions may require preinstallation review and coordination with Construction Documents to verify constructability and commissioning requirements.

        - Manufacturers' Instructions: Record copy of official installation[ and testing] instructions issued to Installer by manufacturer for the following:

          - Locking receptacles.

        - Sample warranties.

      - WARRANTY

When warranties are required and available, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner, after one-year correction period specified in the Contract, under Contractor's general warranty and prevailing local laws.

Verify durations of extended warranty periods needed.

        - Special Manufacturer Extended Warranty: Manufacturer warrants that devices perform in accordance with specified requirements and agrees to provide repair or replacement of devices that fail to perform as specified within extended warranty period.

          - Extended Warranty Period: [Three] [Four] [Five] <Insert number> years from date of Substantial Completion; [full] [prorated] coverage for labor, materials, and equipment.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - EXISTING PRODUCTS[ TO BE MODIFIED] [ TO BE REMOVED AND RE-INSTALLED]

        - Basis for Pricing: <Insert name of manufacturer; model number or series for existing product>.

        - Description: <Insert description of existing product, including special features, options, and finishes that may impact Work>.

        - Accessories: <Insert accessories included with existing product>.

      - LOCKING RECEPTACLES

        - Description: Receptacles that require two motions, insertion and rotation, to fully mate attachment plugs.

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - General Characteristics:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Reference Standards: UL CCN RTRT and UL 498.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - NEMA, 125 V, Locking Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

For "Device Color" Subparagraph below, there is no official standard for color-coding voltage ratings; however, most manufacturers follow this convention for locking receptacles.

            - Device Color: Black with yellow voltage indication on face.

            - Configuration: 2 pole, 3 wire, grounding, [NEMA L5-15R] [NEMA L5-20R] [NEMA L5-30R].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - NEMA, 125 V, Isolated Ground Locking Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

For "Device Color" Subparagraph below, there is no official standard for color-coding voltage ratings; however, most manufacturers follow this convention for locking receptacles.

            - Device Color: Black with yellow voltage indication on face.

            - Configuration: 2 pole, 3 wire, grounding, [NEMA L5-15R] [NEMA L5-20R] [NEMA L5-30R].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - NEMA, 125/250 V, Locking Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

For "Device Color" Subparagraph below, there is no official standard for color-coding voltage ratings; however, most manufacturers follow this convention for locking receptacles.

            - Device Color: Black with orange voltage indication on face.

            - Configuration:

Retain one of two subparagraphs below.

              - 3 pole, 3 wire, non-grounding, [NEMA L10-20R] [NEMA L10-30R].

              - 3 pole, 4 wire, grounding, [NEMA L14-20R] [NEMA L14-30R].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - NEMA, 125/250 V, Isolated Ground Locking Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

For "Device Color" Subparagraph below, there is no official standard for color-coding voltage ratings; however, most manufacturers follow this convention for locking receptacles.

            - Device Color: Black with orange voltage indication on face.

            - Configuration: 3 pole, 4 wire, grounding, [NEMA L14-20R] [NEMA L14-30R].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - NEMA, 250 V, Locking Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

For "Device Color" Subparagraph below, there is no official standard for color-coding voltage ratings; however, most manufacturers follow this convention for locking receptacles.

            - Device Color: Black with blue voltage indication on face.

            - Configuration:

Retain one of four subparagraphs below.

              - 2 pole, 3 wire, grounding, [NEMA L6-15R] [NEMA L6-20R] [NEMA L6-30R].

              - 3 pole, 4 wire, grounding, [NEMA L15-20R] [NEMA L15-30R].

              - 4 pole, 4 wire, non-grounding, [NEMA L18-20R] [NEMA L18-30R].

              - 4 pole, 5 wire, grounding, [NEMA L21-20R] [NEMA L21-30R].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - NEMA, 250 V, Isolated Ground Locking Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

For "Device Color" Subparagraph below, there is no official standard for color-coding voltage ratings; however, most manufacturers follow this convention for locking receptacles.

            - Device Color: Black with blue voltage indication on face.

            - Configuration:

Retain one of three subparagraphs below.

              - 2 pole, 3 wire, grounding, [NEMA L6-15R] [NEMA L6-20R] [NEMA L6-30R].

              - 3 pole, 4 wire, grounding, [NEMA L15-20R] [NEMA L15-30R].

              - 4 pole, 5 wire, grounding, [NEMA L21-20R] [NEMA L21-30R].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - NEMA, 277 V, Locking Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

For "Device Color" Subparagraph below, there is no official standard for color-coding voltage ratings; however, most manufacturers follow this convention for locking receptacles.

            - Device Color: Black with gray voltage indication on face.

            - Configuration: 2 pole, 3 wire, grounding, [NEMA L7-15R] [NEMA L7-20R] [NEMA L7-30R].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - NEMA, 480 V, Locking Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

For "Device Color" Subparagraph below, there is no official standard for color-coding voltage ratings; however, most manufacturers follow this convention for locking receptacles.

            - Device Color: Black with red voltage indication on face.

            - Configuration:

Retain one of four subparagraphs below.

              - 2 pole, 3 wire, grounding, [NEMA L8-20R] [NEMA L8-30R].

              - 3 pole, 4 wire, grounding, [NEMA L16-20R] [NEMA L16-30R].

              - 4 pole, 4 wire, non-grounding, [NEMA L19-20R] [NEMA L19-30R].

              - 4 pole, 5 wire, grounding, [NEMA L22-20R] [NEMA L22-30R].

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - NEMA, 600 V, Locking Receptacle <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

For "Device Color" Subparagraph below, there is no official standard for color-coding voltage ratings; however, most manufacturers follow this convention for locking receptacles.

            - Device Color: Black with black voltage indication on face.

            - Configuration:

Retain one of two subparagraphs below.

              - 2 pole, 3 wire, grounding, 50 A.

              - 3 pole, 4 wire, grounding, 50 A.

- EXECUTION

      - EXAMINATION

        - Verify that receptacles to be procured and installed for Owner-furnished equipment are compatible with mating attachment plugs on equipment.

      - INSTALLATION

        - Comply with manufacturer's instructions.

NFPA 70 and NECA NEIS 1 are already specified in Section 260010 "Supplemental Requirements for Electrical." Retain "Reference Standards" Paragraph below to specify other standards applicable to Work specified in this Section.

        - Reference Standards:

          - Unless more stringent requirements are specified in Contract Documents or manufacturers' instructions, comply with installation instructions in NECA NEIS 130.

          - Mounting Heights: Unless otherwise indicated in Contract Documents, comply with mounting heights recommended in NECA NEIS 1.

          - Receptacle Orientation: Unless otherwise indicated in Contract Documents, orient receptacle to match configuration diagram in NEMA WD 6.

          - Consult Architect for resolution of conflicting requirements.

        - Identification:

          - Identify cover or cover plate for device with panelboard identification and circuit number in accordance with Section 260553 "Identification for Electrical Systems."

Retain first subparagraph below if self-adhesive labels on cover or cover plate are unacceptable.

            - Mark cover or cover plate using hot, stamped, or engraved machine printing with [black] [white] [red]-filled lettering, and provide durable wire markers or tags inside device box or outlet box.

Retain "Healthcare Facilities" Subparagraph below to provide the distinctive color or marking required by Article 517 of NFPA 70 and NFPA 99.

            - Healthcare Facilities: Distinctively identify covers or cover plates of device boxes and outlet boxes that are supplied from life safety and critical branch power supplies following facility's standard practice.

        - Interfaces with Other Work:

          - Coordinate installation of new products for <Insert system or product group> with existing conditions.

            - <Insert requirements for transition between new and existing>.

          - Coordinate with <Insert Section number and title> for <Insert description of interfacing related Work>.

            - <Insert requirements for transition between this Section and related Work>.

      - FIELD QUALITY CONTROL

        - [Acceptance ]Testing Preparation:

          - <Insert requirements>.

Retain first paragraph below to require that field quality-control tests be witnessed. Local ordinance or custom may require that authorities having jurisdiction witness the testing.

        - Field tests and inspections must be witnessed by [Architect] [Tenant] [authorities having jurisdiction] <Insert names or titles of witnesses>.

        - Tests and Inspections:

          - Insert and remove test plug to verify that device is securely mounted.

          - Verify polarity of hot and neutral pins.

          - Measure line voltage.

          - Measure percent voltage drop.

          - Measure grounding circuit continuity; impedance must be not greater than 2 ohms.

          - Perform additional installation and maintenance inspections and diagnostic tests in accordance with NECA NEIS 130 and manufacturers' instructions.

          - <Insert tests and inspections>.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Nonconforming Work:

          - Device will be considered defective if it does not pass tests and inspections.

          - Remove and replace defective units and retest.

        - Assemble and submit test and inspection reports.

Retain "Manufacturer Services" Paragraph below if manufacturer's representative is required to support or supervise the administrant specified in Section 260010 "Supplemental Requirements for Electrical" for field tests and inspections performed by Installer or third-party agencies.

        - Manufacturer Services:

Retain "supervise" option in subparagraph below when third-party tests and inspections must be witnessed and approved by factory-authorized service representative to satisfy special extended warranty requirements. In some cases, Installer may be factory authorized under warranty provisions to fulfill this role.

          - Engage factory-authorized service representative to [support] [supervise] field tests and inspections.

      - PROTECTION

        - Schedule and sequence installation to minimize risk of contamination of wires and cables, devices, device boxes, outlet boxes, covers, and cover plates by plaster, drywall joint compound, mortar, cement, concrete, dust, paint, and other materials.

        - After installation, protect wires and cables, devices, device boxes, outlet boxes, covers, and cover plates from construction activities. Remove and replace items that are contaminated, defaced, damaged, or otherwise caused to be unfit for use prior to acceptance by Owner.

END OF SECTION 262726.39