Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 262726.43 - SPECIAL-PURPOSE POWER OUTLET ASSEMBLIES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Access Manufacturer-Provided, AIA MasterSpec-Based Sections:

<Double click here for this Section based on specific manufacturer’s products set as Basis-of-Design at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED 2009, LEED v4, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using the hypertext links.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Fabricated power outlet cord management assemblies.

          - Fabricated pendant push-button station fittings.

          - Spring-driven commercial/industrial-use cord reels.

          - Motor-driven cord reels.

          - Motor-driven cable management systems.

          - Cord reels for use in hazardous locations.

          - Commercial pendant push-button stations and components.

          - Pendant relocatable power taps.

        - Products Furnished, but Not Installed, under This Section:

          - <Insert products furnished, but not installed>.

        - Products Installed, but Not Furnished, under This Section:

          - <Insert products installed, but not furnished>.

        - Related Requirements:

Always retain first two subparagraphs below.

          - Section 260010 "Supplemental Requirements for Electrical" for additional abbreviations, definitions, submittals, qualifications, testing agencies, and other Project requirements applicable to Work specified in this Section.

          - Section 260011 "Facility Performance Requirements for Electrical" for seismic-load, wind-load, acoustical, and other field conditions applicable to Work specified in this Section.

Retain subparagraph(s) below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Retain first subparagraph below if retaining "Preinstallation Conference" Paragraph. If Project is using Owner-provided Division 01, edit to indicate location where Owner's conference procedures are specified, or delete subparagraph and specify the conference procedures under "Preinstallation Conference" Paragraph.

          - [Section 013100 "Project Management and Coordination"] <Insert section number and title> for preinstallation conference procedures.

      - ALLOWANCES

Retain this article if products and Work included in this Section are covered by lump-sum, unit-cost, quantity, or testing and inspection allowances.

        - See Section 012100 "Allowances" for description of allowances affecting items specified in this Section.

      - UNIT PRICES

Retain this article if products and Work specified in this Section are measured and paid for under the provisions of unit prices.

        - See Section 012200 "Unit Prices" for description of unit prices affecting items specified in this Section.

      - ALTERNATES

Retain this article if products and Work specified in this Section are proposed to be added to or deducted from the base bid amount under the provisions of alternates.

        - See Section 012300 "Alternates" for description of alternates affecting items specified in this Section.

      - DEFINITIONS

Do not duplicate common acronyms, abbreviations, and terms defined in Section 260010 "Supplemental Requirements for Electrical."

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - Commercial/Industrial-Use Cord Reel: A cord reel subject to severe use in factories, commercial garages, construction sites, and similar locations requiring a harder service type cord.

        - General-Use Cord Reel: A cord reel that is acceptable for residential applications, and marked for use either indoors or outdoors. General-use outdoor cord reels are intended to be stored indoors when not in use.

      - PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a conference. Coordinate with "Related Requirements" Paragraph for location of preinstallation conference procedures.

        - Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

Retain "Preinstallation Coordination Meeting(s)" Paragraph below if Work of this Section does not justify a full preinstallation conference as specified in Section 013100 "Project Management and Coordination," but would benefit from a smaller coordination meeting. Consider videoconference option if Project requires social distancing for meetings for infection control.

        - Preinstallation Coordination Meeting(s): For ceiling-mounted cable reels. Conduct meeting [as videoconference] [or] [at Project site] <Insert location> before <Insert construction activity>.

          - Attendees: Installers, fabricators, representatives of manufacturers, and administrants for field tests and inspections. Notify Architect[, Construction Manager] [, and Owner's Commissioning Authority] of scheduled meeting dates.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

Retain one or more of six subparagraphs below as needed to verify Project requirements.

          - Spring-driven commercial/industrial-use cord reels.

          - Motor-driven cord reels.

          - Motor-driven cable management systems.

          - Cord reels for use in hazardous locations.

          - Pendant push-button stations and components.

          - Pendant relocatable power taps.

Retain "Field Quality-Control Submittals" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field Quality-Control Submittals:

          - Field quality-control reports.

      - INFORMATIONAL SUBMITTALS

Retain "Manufacturers' Instructions" Paragraph below when execution requirements state "in accordance with manufacturer's instructions," especially if those instructions may require preinstallation review and coordination with Construction Documents to verify constructability and commissioning requirements.

        - Manufacturers' Instructions: Record copy of official installation[ and testing] instructions issued to Installer by manufacturer for the following:

          - Spring-driven commercial/industrial-use cord reels.

          - Motor-driven cord reels.

          - Motor-driven cable management systems.

          - Cord reels for use in hazardous locations.

          - Pendant push-button stations and components.

          - Pendant relocatable power taps.

        - Sample warranties.

      - CLOSEOUT SUBMITTALS

Submittals for record documents, operation and maintenance data, software, and software documentation are specified in Section 260010 "Supplemental Requirements for Electrical."

        - Warranty documentation.

      - WARRANTY

When warranties are required and available, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner, after one-year correction period specified in the Contract, under the Contractor's general warranty and prevailing local laws.

Verify durations of extended warranty periods needed.

        - Special Installer Extended Warranty: Installer warrants that fabricated and installed cord-reel power outlet assemblies perform in accordance with specified requirements and agrees to repair or replace assemblies that fail to perform as specified within extended warranty period.

          - Extended Warranty Period: [Two] [Three] [Four] <Insert number> years from date of Substantial Completion; full coverage for labor, materials, and equipment.

Retain paragraph below if Project requires that a special manufacturer extended warranty take over when the special installer extended warranty expires. To benefit the Owner, manufacturer extended warranty period must be longer than installer extended warranty period.

        - Special Manufacturer Extended Warranty: Manufacturer warrants that components of cord-reel power outlet assemblies perform in accordance with specified requirements and agrees to provide repair or replacement of components that fail to perform as specified within extended warranty period.

          - [Initial ]Extended Warranty Period: [Three] [Four] [Five] <Insert number> years from date of Substantial Completion; [full] [prorated] coverage for labor, materials, and equipment.

Retain transient voltage surges option in subparagraph below if assembly includes surge protective devices.

Select "origin" option in subparagraph below if recipient assumes ownership of goods when they are shipped. Select "destination" if seller retains ownership of goods until they are delivered. Damaged shipping containers labeled FOB Origin cannot be returned to sender, but carrier is liable to recipient for delay and damage claims.

          - Follow-On Extended Warranty Period: [Eight] <Insert number> years from date of Substantial Completion; [full] [prorated] coverage for materials[ that failed because of transient voltage surges] only, free on board [origin] [destination], freight prepaid.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - OWNER-FURNISHED PRODUCTS

        - Basis for Pricing: <Insert name of manufacturer; model number or series for product that Owner intends to furnish to Contractor>.

        - Description: <Insert description of product, including special features, options, and finishes for Owner-furnished product that may impact Contractor's installation>.

        - Accessories: <Insert accessories that will be provided with product>.

      - EXISTING PRODUCTS[ TO BE MODIFIED] [ TO BE REMOVED AND RE-INSTALLED]

        - Basis for Pricing: <Insert name of manufacturer; model number or series for existing product>.

        - Description: <Insert description of existing product, including special features, options, and finishes that may impact Work>.

        - Accessories: <Insert accessories included with existing product>.

      - FABRICATED POWER OUTLET CORD MANAGEMENT ASSEMBLIES

        - Description: Power outlet cord management assemblies that are custom fabricated by manufacturer or Installer.

Retain "Source Limitations" Paragraph below to require single manufacturer for entire assembly. Some configurations cannot be fabricated using components from one manufacturer. However, special manufacturer extended warranty may only be available if all components are obtained from one manufacturer.

        - Source Limitations: Obtain all components for each power outlet cord management assembly from single manufacturer.

        - Performance Criteria:

          - Regulatory Requirements: Components listed and labeled in accordance with NFPA 70 by qualified electrical testing laboratory recognized by authorities having jurisdiction and marked for intended location and application.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - [Ceiling-Mounted] [Wall-Mounted] [Floor-Mounted] Power Outlet Cord Management Assembly <Insert drawing designation>:

          - General Characteristics: Provide the following specified products with fabricated power outlet cord management assembly:

            - Cord Management System:

Retain and revise one of nine subparagraphs below to indicate title and options for desired product specified elsewhere in this Section.

              - Spring-driven commercial/industrial-use cord reel, <Insert wire size> conductors <Insert drawing designation>.

              - Motor-driven, indoor, general-use cord reel; <Insert wire size> conductors <Insert drawing designation>.

              - DC motor-driven cable management system <Insert drawing designation>.

              - Cord reel for use in Class I Group C hazardous location <Insert drawing designation>.

              - Cord reel for use in Class I Group D hazardous location <Insert drawing designation>.

              - Cord reel for use in Class II Group E hazardous location <Insert drawing designation>.

              - Cord reel for use in Class II Group F hazardous location <Insert drawing designation>.

              - Cord reel for use in Class II Group G hazardous location <Insert drawing designation>.

              - Cord reel for use in Class III hazardous location <Insert drawing designation>.

            - Termination Fitting:

Retain and revise one of first 10 subparagraphs below to indicate title and options for desired product specified elsewhere in this Section.

              - Owner-furnished fitting.

              - Commercial pendant push-button station <Insert drawing designation>.

              - Pendant relocatable power tap <Insert drawing designation>.

              - Fabricated pendant push-button station fitting <Insert drawing designation>.

              - Indoor-use, dry-location cord connector; <Insert NEMA configuration> <Insert drawing designation> specified in Section 262726.51 "Connectors, Cords, and Plugs."

              - Indoor-use, sealed cord connector; <Insert NEMA configuration> <Insert drawing designation> specified in Section 262726.51 "Connectors, Cords, and Plugs."

              - Hospital-grade, indoor-use, sealed cord connector; <Insert NEMA configuration> <Insert drawing designation> specified in Section 262726.51 "Connectors, Cords, and Plugs."

              - Indoor-use, compression-grip, sealed cord connector; <Insert NEMA configuration> <Insert drawing designation> specified in Section 262726.51 "Connectors, Cords, and Plugs."

              - Outdoor-use, watertight, sealed cord connector; <Insert NEMA configuration> <Insert drawing designation> specified in Section 262726.51 "Connectors, Cords, and Plugs."

              - Antimicrobial, watertight, sealed cord connector; <Insert NEMA configuration> <Insert drawing designation> specified in Section 262726.51 "Connectors, Cords, and Plugs."

Retain and revise subparagraph below to indicate product specified in a different section.

              - <Insert title of product> <Insert drawing designation> specified in <Insert Section number and title>.

            - Cord or Cable:

Retain and revise one of five subparagraphs below to indicate title and options for desired product specified elsewhere in this Section.

              - Oil-resistant, extra-hard-usage, jacketed, flexible cord for indoor damp locations; <Indicate wire size>, <Indicate wire quantity>, and <Indicate length> specified in Section 262726.51 "Connectors, Cords, and Plugs."

              - Oil-resistant, extra-hard-usage, jacketed, flexible cord for outdoor or indoor wet locations; <Indicate wire size>, <Indicate wire quantity>, and <Indicate length> specified in Section 262726.51 "Connectors, Cords, and Plugs."

              - Antimicrobial, oil-resistant, extra-hard-usage, jacketed, flexible cord for outdoor or indoor wet locations; <Indicate wire size>, <Indicate wire quantity>, and <Indicate length> specified in Section 262726.51 "Connectors, Cords, and Plugs."

              - Oil-resistant, hard-usage, jacketed, flexible cord for indoor damp locations; <Indicate wire size>, <Indicate wire quantity>, and <Indicate length> specified in Section 262726.51 "Connectors, Cords, and Plugs."

              - Oil-resistant, hard-usage, jacketed, flexible cord for outdoor or indoor wet locations; <Indicate wire size>, <Indicate wire quantity>, and <Indicate length> specified in Section 262726.51 "Connectors, Cords, and Plugs."

            - Strain-relief cord grips specified in Section 262726.51 "Connectors, Cords, and Plugs."

          - Options:

            - <Insert required option>.

        - Accessories:

          - <Insert required accessory>.

      - FABRICATED PENDANT PUSH-BUTTON STATION FITTINGS

        - Description: Pendant push-button station fittings that are custom fabricated by manufacturer or Installer.

Retain "Source Limitations" Paragraph below to require single manufacturer for entire assembly. Some configurations cannot be fabricated using components from one manufacturer. However, special manufacturer extended warranty may only be available if all components are obtained from one manufacturer.

        - Source Limitations: Obtain all components for each pendant push-button station fitting from single manufacturer.

        - Performance Criteria:

          - Regulatory Requirements: Components listed and labeled in accordance with NFPA 70 by qualified electrical testing laboratory recognized by authorities having jurisdiction and marked for intended location and application.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Pendant Push-Button Station Fitting <Insert drawing designation>:

          - General Characteristics: Provide the following specified components with fabricated pendant push-button station fitting:

Retain and revise six subparagraphs below to indicate titles and options for desired products specified elsewhere in this Section.

            - Pendant push-button station enclosure <Insert drawing designation>.

            - <Insert quantity> blank cover plates.

            - Horn for 19 mm accessory hole.

            - Red pilot light for [12 mm accessory hole] [19 mm accessory hole] [22 mm button space].

            - Push-button switch <Insert drawing designation>.

            - Selector switch <Insert drawing designation>.

Retain and revise subparagraph below to indicate product specified in a different section.

            - <Insert title of product> <Insert drawing designation> specified in <Insert Section number and title>.

          - Options:

            - <Insert required option>.

        - Accessories:

          - <Insert required accessory>.

      - SPRING-DRIVEN COMMERCIAL/INDUSTRIAL-USE CORD REELS

        - Description: Reel equipped with, or intended for use with, length of flexible cord, providing means for cord to be unwound by user as desired, providing spring take-up mechanism to rewind cord on reel, and providing latch to restrain action of spring take-up mechanism while cord reel is in use.

        - Performance Criteria:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - General Characteristics:

For assistance with finding guide information for UL Category Control Numbers and identifying UL approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Reference Standards: UL Category Control Number SBCV and UL 355.

            - Spring take-up retraction mechanism.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Spring-Driven Commercial/Industrial-Use Cord Reel, No. 14 AWG Conductors <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Retain one of five options in "Electrical Rating with Cable" Subparagraph below. First option is for two wires and ground; second is for three wires and ground; third is for four to six wires and ground; fourth is for seven to nine wires and ground; fifth is for 10 wires or more and ground.

            - Electrical Rating with Cable: 600 V, [18 A] [15 A] [12 A] [10.5 A] [7.5 A].

            - Color: [Yellow] [Black] [White] <Insert color>.

            - Enclosure Degree of Protection: [Type 4] [Type 4X].

            - Ball stop.

            - Pivot base.

            - Spool Capacity:

Retain one of 12 subparagraphs below.

Configurations listed in first six subparagraphs below are known to be available from at least two sources.

              - No 14 AWG, two wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)] [70 ft (21.3 m)].

              - No 14 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [35 ft (10.7 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)] [70 ft (21.3 m)].

              - No 14 AWG, five wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)].

              - No 14 AWG, seven wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)].

              - No 14 AWG, nine wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)].

              - No 14 AWG, eleven wires and equipment ground, [20 ft (6 m)] [60 ft (18.3 m)].

Configurations listed in six subparagraphs below may be available from only a single source.

              - No 14 AWG, two wires and equipment ground, [25 ft (7.6 m)] [35 ft (10.7 m)] [45 ft (13.7 m)] [90 ft (27.4 m)] [100 ft (30.5 m)] [125 ft (38.1 m)] [150 ft (45.7 m)].

              - No 14 AWG, three wires and equipment ground, [25 ft (7.6 m)] [45 ft (13.7 m)] [65 ft (19.8 m)] [80 ft (24.4 m)] [90 ft (27.4 m)] [100 ft (30.5 m)] [125 ft (38.1 m)] [150 ft (45.7 m)].

              - No 14 AWG, five wires and equipment ground, [25 ft (7.6 m)] [35 ft (10.7 m)] [45 ft (13.7 m)].

              - No 14 AWG, seven wires and equipment ground, [25 ft (7.6 m)] [35 ft (10.7 m)] [45 ft (13.7 m)].

              - No 14 AWG, nine wires and equipment ground, [25 ft (7.6 m)] [50 ft (15.2 m)].

              - No 14 AWG, eleven wires and equipment ground, [25 ft (7.6 m)] [30 ft (9.1 m)].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Spring-Driven Commercial/Industrial-Use Cord Reel, No. 12 AWG Conductors <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Retain one of four options in "Electrical Rating with Cable" Subparagraph below. First option is for two wires and ground; second is for three wires and ground; third is for four to six wires and ground; fourth is for seven to nine wires and ground.

            - Electrical Rating with Cable: 600 V, [25 A] [20 A] [16 A] [14 A].

            - Color: [Yellow] [Black] [White] <Insert color>.

            - Enclosure Degree of Protection: [Type 4] [Type 4X].

            - Ball stop.

            - Pivot base.

            - Spool Capacity:

Retain one of nine subparagraphs below.

Configurations listed in first four subparagraphs below are known to be available from at least two sources.

              - No 12 AWG, two wires and equipment ground, [20 ft (6 m)] [25 ft (7.6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)].

              - No 12 AWG, three wires and equipment ground, [20 ft (6 m)] [25 ft (7.6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [45 ft (13.7 m)] [50 ft (15.2 m)] [60 ft (18.3 m)] [100 ft (30.5 m)].

              - No 12 AWG, five wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)].

              - No 12 AWG, seven wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)].

Configurations listed in five subparagraphs below may be available from only a single source.

              - No 12 AWG, two wires and equipment ground, [35 ft (10.7 m)] [45 ft (13.7 m)] [70 ft (21.3 m)] [80 ft (24.4 m)] [90 ft (27.4 m)] [100 ft (30.5 m)] [125 ft (38.1 m)] [150 ft (45.7 m)].

              - No 12 AWG, three wires and equipment ground, [35 ft (10.7 m)] [70 ft (21.3 m)] [80 ft (24.4 m)] [90 ft (27.4 m)] [125 ft (38.1 m)].

              - No 12 AWG, four wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)].

              - No 12 AWG, five wires and equipment ground, [25 ft (7.6 m)] [35 ft (10.7 m)] [45 ft (13.7 m)].

              - No 12 AWG, seven wires and equipment ground, [25 ft (7.6 m)] [40 ft (12.2 m)].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Spring-Driven Commercial/Industrial-Use Cord Reel, No. 10 AWG Conductors <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Retain one of four options in "Electrical Rating with Cable" Subparagraph below. First option is for two wires and ground; second is for three wires and ground; third is for four to six wires and ground; fourth is for seven to nine wires and ground.

            - Electrical Rating with Cable: 600 V, [30 A] [25 A] [20 A] [17.5 A].

            - Color: [Yellow] [Black] [White] <Insert color>.

            - Enclosure Degree of Protection: [Type 4] [Type 4X].

            - Ball stop.

            - Pivot base.

            - Spool Capacity:

Retain one of eight subparagraphs below.

Configurations listed in first three subparagraphs below are known to be available from at least two sources.

              - No 10 AWG, two wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)].

              - No 10 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)].

              - No 10 AWG, five wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)].

Configurations listed in five subparagraphs below may be available from only a single source.

              - No 10 AWG, two wires and equipment ground, [25 ft (7.6 m)] [35 ft (10.7 m)] [45 ft (13.7 m)] [70 ft (21.3 m)] [80 ft (24.4 m)] [90 ft (27.4 m)] [100 ft (30.5 m)] [125 ft (38.1 m)].

              - No 10 AWG, three wires and equipment ground, [25 ft (7.6 m)] [35 ft (10.7 m)] [45 ft (13.7 m)] [70 ft (21.3 m)] [80 ft (24.4 m)] [90 ft (27.4 m)] [100 ft (30.5 m)] [125 ft (38.1 m)].

              - No 10 AWG, four wires and equipment ground, [30 ft (9.1 m)] [60 ft (18.3 m)] [70 ft (21.3 m)].

              - No 10 AWG, five wires and equipment ground, 25 ft (7.6 m).

              - No 10 AWG, seven wires and equipment ground, 20 ft (6 m).

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Spring-Driven Commercial/Industrial-Use Cord Reel, No. 8 AWG Conductors <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Retain one of two options in "Electrical Rating with Cable" Subparagraph below. First option is for two wires and ground; second is for three wires and ground.

            - Electrical Rating with Cable: 600 V, [40 A] [35 A].

            - Color: [Yellow] [Black] [White] <Insert color>.

            - Enclosure Degree of Protection: [Type 4] [Type 4X].

            - Ball stop.

            - Pivot base.

            - Spool Capacity:

Retain one of four subparagraphs below.

Configurations listed in first two subparagraphs below are known to be available from at least two sources.

              - No 8 AWG, two wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)].

              - No 8 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)].

Configurations listed in two subparagraphs below may be available from only a single source.

              - No 8 AWG, two wires and equipment ground, [25 ft (7.6 m)] [50 ft (15.2 m)].

              - No 8 AWG, three wires and equipment ground, [25 ft (7.6 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)] [70 ft (21.3 m)].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Spring-Driven Commercial/Industrial-Use Cord Reel, No. 6 AWG Conductors <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Retain one of three options in "Electrical Rating with Cable" Subparagraph below. First option is for two wires and ground; second is for three wires and ground; third is for four to six wires and ground.

            - Electrical Rating with Cable: 600 V, [55 A] [45 A] [36 A].

            - Color: [Yellow] [Black] [White] <Insert color>.

            - Enclosure Degree of Protection: [Type 4] [Type 4X].

            - Ball stop.

            - Pivot base.

            - Spool Capacity:

Retain one of three subparagraphs below.

Configurations listed below may be available from only a single source.

              - No 6 AWG, two wires and equipment ground, 70 ft (21.3 m).

              - No 6 AWG, three wires and equipment ground, [30 ft (9.1 m)] [50 ft (15.2 m)].

              - No 6 AWG, four wires and equipment ground, 40 ft (12.2 m).

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Spring-Driven Commercial/Industrial-Use Cord Reel, No. 4 AWG Conductors <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Electrical Rating with Cable: 600 V, 70 A.

            - Color: [Yellow] [Black] [White] <Insert color>.

            - Enclosure Degree of Protection: [Type 4] [Type 4X].

            - Ball stop.

            - Pivot base.

            - Spool Capacity:

Configuration listed in subparagraph below may be available from only a single source.

              - No 4 AWG, two wires and equipment ground, 30 ft (9.1 m).

      - MOTOR-DRIVEN CORD REELS

Products specified in this article may be available from only a single source.

        - Description: Reel equipped with, or intended for use with, length of flexible cord, providing motor to dispense cord from and rewind cord on reel.

        - Performance Criteria:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - General Characteristics:

For assistance with finding guide information for UL Category Control Numbers and identifying UL approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Reference Standards: UL Category Control Number SBCV and UL 355.

            - Electrical Rating with Cable: 125 V, 20 A.

            - DC motor dispensing and rewinding mechanism.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Motor-Driven, Indoor, General-Use Cord Reel <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Color: [Yellow] [Black] [White] <Insert color>.

            - Enclosure Degree of Protection: [Type 4] [Type 4X].

            - Ball stop.

            - Pivot base.

            - Spool Capacity:

              - No 12 AWG, two wires and equipment ground, [25 ft (7.6 m)] [50 ft (15.2 m)].

      - MOTOR-DRIVEN CABLE MANAGEMENT SYSTEMS

Products specified in this article may be available from only a single source.

        - Description: Motor and guiding mechanism for automated dispensing and retrieving of multiconductor cable stored in a basket or container. Unlike reels, motor-driven cable management systems do not require a slip ring to transfer facility power to the cable.

        - Performance Criteria:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - General Characteristics:

For assistance with finding guide information for UL Category Control Numbers and identifying UL approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Reference Standards: UL Category Control Number SBCV and UL 355.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - DC Motor-Driven Cable Management System <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Motor: [12 V(dc)] [24 V(dc)].

            - Environmental Rating: [Indoor, damp] [Outdoor, wet] location.

            - Hawse Pipe: [None] [Stainless steel].

            - Control Operator: [Toggle switch] [Wireless remote control].

            - Cable Size:

Retain one of first three subparagraphs below to indicate cable size.

Size range in first subparagraph below should handle most No. 12 AWG and No. 10 AWG cable configurations.

              - Handles cables between 0.47 inch (12 mm) OD and 0.83 inch (21 mm) OD.

Size range in first subparagraph below should handle most No. 8 AWG and No. 6 AWG cable configurations.

              - Handles cables between 0.83 inch (21 mm) OD and 1.14 inch (29 mm) OD.

Size range in first subparagraph below should handle most No. 4 AWG and No. 2 AWG cable configurations.

              - Handles cables between 1.14 inch (29 mm) OD and 1.63 inch (42 mm) OD.

          - Accessories:

            - Mounting Hardware: <Insert description of hardware needed to mount system to ceiling, wall, or cable storage container>.

            - Cable Storage: <Insert description of basket or container needed to accommodate size and length of cable>.

      - CORD REELS FOR USE IN HAZARDOUS LOCATIONS

        - Description: Reel equipped with, or intended for use with, length of flexible cord, intended for installation in hazardous classified locations.

        - Performance Criteria:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - General Characteristics:

For assistance with finding guide information for UL Category Control Numbers and identifying UL approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Reference Standards: UL Category Control Number SAOX and UL 355.

            - Spring take-up retraction mechanism.

Class I Group A is for acetylene. Class I Group B is for flammable gas or liquid vapor with properties similar to hydrogen. UL has not listed products suitable for these environments.

Retain first paragraph below for installation in locations containing flammable gas or liquid vapor with properties similar to ethylene.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Spring-Driven Cord Reel for Use in Class I Group C Hazardous Locations <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Retain one of five options in "Electrical Rating with Cable" Subparagraph below. First option is for No. 10 AWG two wires and ground; second is for No. 10 AWG three wires and ground or No. 12 AWG two wires and ground; third is for No. 12 AWG three wires and ground; fourth is for No. 14 AWG two wires and ground; fifth is for No. 14 AWG three wires and ground.

            - Electrical Rating with Cable: 600 V, [35 A] [25 A] [20 A] [18 A] [15 A].

            - Color: [Yellow] [Black] [White] <Insert color>.

            - Enclosure Degree of Protection: [Type 4] [Type 4X].

            - Ball stop.

            - Pivot base.

            - Spool Capacity:

Retain one of six subparagraphs below.

Configurations listed below may be available from only a single source.

              - No 14 AWG, two wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)] [70 ft (21.3 m)].

              - No 14 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)].

              - No 12 AWG, two wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)].

              - No 12 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)].

              - No 10 AWG, two wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)].

              - No 10 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)].

Retain first paragraph below for installation in locations containing flammable gas or liquid vapor with properties similar to propane.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Spring-Driven Cord Reel for Use in Class I Group D Hazardous Locations <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Retain one of five options in "Electrical Rating with Cable" Subparagraph below. First option is for No. 10 AWG two wires and ground; second is for No. 10 AWG three wires and ground or No. 12 AWG two wires and ground; third is for No. 12 AWG three wires and ground; fourth option is for No. 14 AWG two wires and ground; fifth is for No. 14 AWG three wires and ground.

            - Electrical Rating with Cable: 600 V, [35 A] [25 A] [20 A] [18 A] [15 A].

            - Color: [Yellow] [Black] [White] <Insert color>.

            - Enclosure Degree of Protection: [Type 4] [Type 4X].

            - Ball stop.

            - Pivot base.

            - Spool Capacity:

Retain one of nine subparagraphs below.

Configurations listed in first three subparagraphs below are known to be available from at least two sources.

              - No 14 AWG, two wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [50 ft (15.2 m)].

              - No 14 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [50 ft (15.2 m)].

              - No 12 AWG, two wires and equipment ground, [30 ft (9.1 m)] [50 ft (15.2 m)].

Configurations listed in six subparagraphs below may be available from only a single source.

              - No 14 AWG, two wires and equipment ground, [40 ft (12.2 m)] [60 ft (18.3 m)] [70 ft (21.3 m)].

              - No 14 AWG, three wires and equipment ground, [40 ft (12.2 m)] [60 ft (18.3 m)].

              - No 12 AWG, two wires and equipment ground, [20 ft (6 m)] [40 ft (12.2 m)] [60 ft (18.3 m)].

              - No 12 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)].

              - No 10 AWG, two wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)].

              - No 10 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)].

Retain first paragraph below for installation in locations containing combustible metal dusts.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Spring-Driven Cord Reel for Use in Class II Group E Hazardous Locations <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Retain one of five options in "Electrical Rating with Cable" Subparagraph below. First option is for No. 10 AWG two wires and ground; second is for No. 10 AWG three wires and ground or No. 12 AWG two wires and ground; third is for No. 12 AWG three wires and ground; fourth option is for No. 14 AWG two wires and ground; fifth is for No. 14 AWG three wires and ground.

            - Electrical Rating with Cable: 600 V, [35 A] [25 A] [20 A] [18 A] [15 A].

            - Color: [Yellow] [Black] [White] <Insert color>.

            - Enclosure Degree of Protection: [Type 4] [Type 4X].

            - Ball stop.

            - Pivot base.

            - Spool Capacity:

Retain one of eight subparagraphs below.

Configurations listed in first two subparagraphs below are known to be available from at least two sources.

              - No 14 AWG, two wires and equipment ground, 30 ft (9.1 m).

              - No 14 AWG, three wires and equipment ground, 30 ft (9.1 m).

Configurations listed in six subparagraphs below may be available from only a single source.

              - No 14 AWG, two wires and equipment ground, [20 ft (6 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)] [70 ft (21.3 m)].

              - No 14 AWG, three wires and equipment ground, [20 ft (6 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)].

              - No 12 AWG, two wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)].

              - No 12 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)].

              - No 10 AWG, two wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)].

              - No 10 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)].

Retain first paragraph below for installation in locations containing combustible carbonaceous dusts (e.g., coal or charcoal).

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Spring-Driven Cord Reel for Use in Class II Group F Hazardous Locations <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Retain one of five options in "Electrical Rating with Cable" Subparagraph below. First option is for No. 10 AWG two wires and ground; second is for No. 10 AWG three wires and ground or No. 12 AWG two wires and ground; third is for No. 12 AWG three wires and ground; fourth option is for No. 14 AWG two wires and ground; fifth is for No. 14 AWG three wires and ground.

            - Electrical Rating with Cable: 600 V, [35 A] [25 A] [20 A] [18 A] [15 A].

            - Color: [Yellow] [Black] [White] <Insert color>.

            - Enclosure Degree of Protection: [Type 4] [Type 4X].

            - Ball stop.

            - Pivot base.

            - Spool Capacity:

Retain one of eight subparagraphs below.

Configurations listed in first two subparagraphs below are known to be available from at least two sources.

              - No 14 AWG, two wires and equipment ground, 30 ft (9.1 m).

              - No 14 AWG, three wires and equipment ground, 30 ft (9.1 m).

Configurations listed in six subparagraphs below may be available from only a single source.

              - No 14 AWG, two wires and equipment ground, [20 ft (6 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)] [70 ft (21.3 m)].

              - No 14 AWG, three wires and equipment ground, [20 ft (6 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)].

              - No 12 AWG, two wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)].

              - No 12 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)].

              - No 10 AWG, two wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)].

              - No 10 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)].

Retain first paragraph below for installation in locations containing combustible dust other than Group E or Group F.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Spring-Driven Cord Reel for Use in Class II Group G Hazardous Locations <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Retain one of five options in "Electrical Rating with Cable" Subparagraph below. First option is for No. 10 AWG two wires and ground; second is for No. 10 AWG three wires and ground or No. 12 AWG two wires and ground; third is for No. 12 AWG three wires and ground; fourth option is for No. 14 AWG two wires and ground; fifth is for No. 14 AWG three wires and ground.

            - Electrical Rating with Cable: 600 V, [35 A] [25 A] [20 A] [18 A] [15 A].

            - Color: [Yellow] [Black] [White] <Insert color>.

            - Enclosure Degree of Protection: [Type 4] [Type 4X].

            - Ball stop.

            - Pivot base.

            - Spool Capacity:

Retain one of nine subparagraphs below.

Configurations listed in first three subparagraphs below are known to be available from at least two sources.

              - No 14 AWG, two wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [50 ft (15.2 m)].

              - No 14 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [50 ft (15.2 m)].

              - No 12 AWG, two wires and equipment ground, [30 ft (9.1 m)] [50 ft (15.2 m)].

Configurations listed in six subparagraphs below may be available from only a single source.

              - No 14 AWG, two wires and equipment ground, [40 ft (12.2 m)] [60 ft (18.3 m)] [70 ft (21.3 m)].

              - No 14 AWG, three wires and equipment ground, [40 ft (12.2 m)] [60 ft (18.3 m)].

              - No 12 AWG, two wires and equipment ground, [20 ft (6 m)] [40 ft (12.2 m)] [60 ft (18.3 m)].

              - No 12 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)].

                - No 10 AWG, two wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)].

                - No 10 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)].

Retain first paragraph below for installation in locations containing easily ignitable fibers or flyings that are not likely to be airborne in ignitable quantities.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Spring-Driven Cord Reel for Use in Class III Hazardous Locations <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Retain one of five options in "Electrical Rating with Cable" Subparagraph below. First option is for No. 10 AWG two wires and ground; second is for No. 10 AWG three wires and ground or No. 12 AWG two wires and ground; third is for No. 12 AWG three wires and ground; fourth option is for No. 14 AWG two wires and ground; fifth is for No. 14 AWG three wires and ground.

            - Electrical Rating with Cable: 600 V, [35 A] [25 A] [20 A] [18 A] [15 A].

            - Color: [Yellow] [Black] [White] <Insert color>.

            - Enclosure Degree of Protection: [Type 4] [Type 4X].

            - Ball stop.

            - Pivot base.

            - Spool Capacity:

Retain one of eight subparagraphs below.

Configurations listed in first two subparagraphs below are known to be available from at least two sources.

              - No 14 AWG, two wires and equipment ground, 30 ft (9.1 m).

              - No 14 AWG, three wires and equipment ground, 30 ft (9.1 m).

Configurations listed in six subparagraphs below may be available from only a single source.

              - No 14 AWG, two wires and equipment ground, [20 ft (6 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)] [70 ft (21.3 m)].

              - No 14 AWG, three wires and equipment ground, [20 ft (6 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)].

              - No 12 AWG, two wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)] [60 ft (18.3 m)].

              - No 12 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)] [50 ft (15.2 m)].

              - No 10 AWG, two wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)].

              - No 10 AWG, three wires and equipment ground, [20 ft (6 m)] [30 ft (9.1 m)] [40 ft (12.2 m)].

      - PENDANT PUSH-BUTTON STATIONS AND COMPONENTS

        - Description: Control assembly for electrical equipment, suspended on a flexible cord, that contains push-buttons alone or in combination with other pilot devices, such as selector switches and indicating lights.

        - Performance Criteria:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - General Characteristics:

For assistance with finding guide information for UL Category Control Numbers and identifying UL approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

In "Reference Standards" Subparagraph below, UL 508 option is for industrial control equipment, UL 1053 option is for ground-fault sensing devices, and remaining options are for low-voltage switchgear. UL 508 is the correct option for most items specified in this Section.

            - Reference Standards: UL Category Control Number NKCR and [UL 508] [UL 1053] [UL 60947-1] [UL 60947-4-1] [UL 60947-5-1].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Commercial Pendant Push-Button Station <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Retain one of 20 subparagraphs below.

            - Two buttons; momentary 1 NO/1 NO.

            - Two buttons; momentary 2 NO/2 NO.

            - Four buttons; two momentary 1 NO/1 NO.

            - Four buttons; two momentary 2 NO/2 NO.

            - Four buttons; momentary 1 NO/1 NO; momentary 1 NC+NO/1 NC+NO.

            - Four buttons; emergency stop; momentary 1 NC+NO/1 NC+NO.

            - Six buttons; maintained 1 NO; two momentary 1 NO/1 NO.

            - Six buttons; maintained 1 NO; two momentary 2 NO/2 NO.

            - Six buttons; maintained 1 NO/1 NC; two momentary 1 NC+NO/1 NC+NO.

            - Six buttons; emergency stop; two momentary 1 NC+NO/1 NC+NO.

            - Eight buttons; maintained 1 NO; three momentary 1 NO/1 NO.

            - Eight buttons; maintained 1 NO; three momentary 2 NO/2 NO.

            - Eight buttons; maintained 1 NO; three momentary 1 NC+NO/1 NC+NO.

            - Eight buttons; emergency stop; three momentary 1 NC+NO/1 NC+NO.

            - Ten buttons; maintained 1 NO; four momentary 1 NO/1 NO.

            - Ten buttons; maintained 1 NO; four momentary 1 NC+NO/1 NC+NO.

            - Ten buttons; emergency stop; four momentary 1 NC+NO/1 NC+NO.

            - Twelve buttons; maintained 1 NO; five momentary 1 NO/1 NO.

            - Twelve buttons; maintained 1 NO; five momentary 1 NC+NO/1 NC+NO.

            - Twelve buttons; emergency stop; five momentary 1 NC+NO/1 NC+NO.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Pendant Push-Button Station Enclosure <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Retain one of first six subparagraphs below.

            - Two-button enclosure.

            - Four-button enclosure.

            - Six-button enclosure.

            - Eight-button enclosure.

            - Ten-button enclosure.

            - Twelve-button enclosure.

          - Accessories:

            - Blank cover plates for unused button holes.

            - Horn for 19 mm accessory hole, one wire, 125 V(ac), 6 A/250 V(ac), 3 A.

            - Red pilot light for 12 mm accessory hole, one wire, 12 V(ac).

            - Red pilot light for 19 mm accessory hole, one wire, [110 V(ac)] [12 V(dc)] [24 V(ac/dc)].

            - Red pilot light for 22 mm button space, one wire, [110 V(ac)] [12 V(dc)] [24 V(ac/dc)].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Push-Button Switch <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Retain one of 23 subparagraphs below.

            - Button Boot: <Insert quantity> clear label cover; <Insert quantity> black; <Insert quantity> red; <Insert quantity> green.

            - Emergency stop button, one wire, 1 NC.

            - Emergency stop button, one wire, 1 NO.

            - Emergency stop button, two wires, 1 NO+NC.

            - Emergency stop button, two wires, 2 NC.

            - Emergency stop button, two wires, 2 NO.

            - One button, one wire, momentary 1 NC.

            - One button, one wire, momentary 1 NO.

            - One button, two wire, momentary 1 NC+NO.

            - One button, two wire, momentary 2 NC.

            - One button, two wire, momentary 2 NO.

            - Two buttons, one wire, maintained interlocked 1 NO.

            - Two buttons, one wire, maintained interlocked 1 NC+NO.

            - Two buttons, two wires, momentary non-interlocked 1 NO/1 NC.

            - Two buttons, two wires, momentary non-interlocked 1 NO/1 NC.

            - Two buttons, two wires, momentary non-interlocked 1 NC+NO/1 NC+NO.

            - Two buttons, four wires, dual pole, momentary, with mechanical interlock 2 NO/2 NO.

            - Two buttons, four wires, dual pole, momentary, with mechanical interlock 2 NC+NO/2 NC+NO.

            - Two buttons, two wires, momentary, with mechanical interlock 1 NO/1 NO.

            - Two buttons, two wires, momentary, with mechanical interlock 1 NC+NO/1 NC+NO.

            - Two buttons, three wires, momentary, with mechanical interlock, 2 Speed 2 NO/2 NO.

            - Two buttons, three wires, momentary, with mechanical interlock, 2 Speed 2 NO+NC/2 NO+NC.

            - Two buttons, four wires, momentary, with mechanical interlock, 3 Speed 1 NC+3 NO/1 NC+3 NO.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Selector Switch <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Retain one of eight subparagraphs below.

            - One button, one wire, maintained 1 NC 2 Position.

            - One button, one wire, maintained 1 NO 2 Position.

            - One button, two wires, maintained 1 NO+NC 2 Position.

            - One button, two wires, maintained 2 NO 2 Position.

            - One button, two wires, maintained 2 NC 3 Position Center Off.

            - One button, two wires, maintained 2 NO 3 Position Center Off.

            - One button, two wires, maintained 2 NC 2 Position.

            - One button, two wires, maintained 1 NO+NC 3 Position Center Off.

      - PENDANT RELOCATABLE POWER TAPS

        - Description: Electrical enclosure providing one or more receptacle outlets that must be attached to a cord reel in accordance with UL 355 to provide the power supply cord and attachment plug required by UL 1363. Portable power strips do not satisfy these requirements.

        - Performance Criteria:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - General Characteristics:

For assistance with finding guide information for UL Category Control Numbers and identifying UL approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Reference Standards: UL Category Control Number XBYS and UL 1363.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

        - Pendant Relocatable Power Tap <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Retain one of 22 subparagraphs below.

            - Nonmetallic outlet box with two duplex cover plates and two NEMA 5-15R duplex receptacles.

            - Weather-resistant, nonmetallic outlet box; two duplex cover plates with flip covers and two NEMA 5-15R duplex receptacles.

            - Nonmetallic outlet box with two duplex cover plates and two NEMA 5-20R duplex receptacles.

            - Weather-resistant, nonmetallic outlet box; two duplex cover plates with flip covers and two NEMA 5-20R duplex receptacles.

            - Weather-resistant, nonmetallic outlet box; two duplex cover plates with flip covers and two NEMA 5-20R duplex GFCI receptacles.

            - Nonmetallic outlet box with two cover plates and two NEMA L5-15R receptacles.

            - Weather-resistant, nonmetallic outlet box; two cover plates with flip covers and two NEMA L5-15R receptacles.

            - Nonmetallic outlet box with two duplex cover plates and two NEMA L5-15R duplex receptacles.

            - Weather-resistant, nonmetallic outlet box; two duplex cover plates with flip covers and two NEMA L5-15R duplex receptacles.

            - Nonmetallic enclosure with three NEMA L5-15R receptacles.

            - Nonmetallic outlet box with two cover plates and two NEMA L5-20R receptacles.

            - Weather-resistant, nonmetallic outlet box; two cover plates with flip covers and two NEMA L5-20R receptacles.

            - Nonmetallic outlet box with two cover plates and two NEMA L6-20R receptacles.

            - Weather-resistant, nonmetallic outlet box; two cover plates with flip covers and two NEMA L6-20R receptacles.

            - Nonmetallic enclosure with three NEMA 5-15R receptacles.

            - Nonmetallic enclosure with three NEMA 5-20R receptacles.

            - Nonmetallic enclosure with three NEMA 6-15R receptacles.

            - Nonmetallic enclosure with three NEMA 6-20R receptacles.

            - Nonmetallic enclosure with three NEMA L5-20R receptacles.

            - Nonmetallic enclosure with three NEMA L6-15R receptacles.

            - Nonmetallic enclosure with three NEMA L6-20R receptacles.

            - Nonmetallic enclosure with three NEMA L7-20R receptacles.

- EXECUTION

      - EXAMINATION

        - Examine roughing-in for cord reel mounting and power connections to verify actual locations of mounts and power connections before cord reel installation.

        - Examine walls, floors, and ceilings for suitable conditions where cord reel will be installed.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION OF CORD REELS AND FITTINGS

        - Comply with manufacturer's instructions.

        - Special Techniques:

          - <Insert more stringent installation requirements that supplement or supersede manufacturers' instructions>.

        - Interfaces with Other Work:

          - Coordinate installation of new products for <Insert system or product group> with existing conditions.

            - <Insert requirements for transition between new and existing>.

          - Coordinate with <Insert Section Number and Title> for <Insert description of interfacing related Work>.

            - <Insert requirements for transition between this Section and related Work>.

      - FIELD QUALITY CONTROL

        - [Acceptance ]Testing Preparation:

          - <Insert requirements>.

Retain first paragraph below to require that field quality-control tests be witnessed. Local ordinance or custom may require that authorities having jurisdiction witness the testing.

        - Field tests and inspections must be witnessed by [Architect] [Tenant] [authorities having jurisdiction] <Insert names or titles of witnesses>.

        - Tests and Inspections:

          - Perform tests and inspections indicated in manufacturer's instructions.

          - <Insert Project-specific test or inspection>.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Nonconforming Work:

          - Components and assemblies will be considered defective if they do not pass tests and inspections.

          - Remove and replace defective units and retest.

        - Assemble and submit test and inspection reports.

Retain "Manufacturer Services" Paragraph below if manufacturer's representative is required to support or supervise the administrant specified in Section 260010 "Supplemental Requirements for Electrical" for field tests and inspections performed by Installer or third party agencies.

        - Manufacturer Services:

Retain supervise option in subparagraph below when third-party tests and inspections must be witnessed and approved by factory-authorized service representative to satisfy special extended warranty requirements. In some cases, Installer may be factory-authorized under warranty provisions to fulfill this role.

          - Engage factory-authorized service representative to [support] [supervise] field tests and inspections.

      - ADJUSTING

        - Adjust spring mechanisms and moving parts of cord reel and fittings to function smoothly, and lubricate as recommended in writing by manufacturer.

      - PROTECTION

        - After installation, protect cord reels and fittings from construction activities. Remove and replace items that are contaminated, defaced, damaged, or otherwise caused to be unfit for use prior to acceptance by Owner.

END OF SECTION 262726.43