Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 262726.51 - CONNECTORS, CORDS, AND PLUGS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Access Manufacturer-Provided, AIA MasterSpec-Based Sections:

<Double click here for this Section based on specific manufacturer’s products set as Basis-of-Design at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Fuseless attachment cord connectors.

          - Extra-hard-usage, jacketed, flexible cord.

          - Antimicrobial, extra-hard-usage, jacketed, flexible cord.

          - Hard-usage, jacketed, flexible cord.

          - Strain-relief cord grips.

        - Related Requirements:

Always retain two subparagraphs below.

          - Section 260010 "Supplemental Requirements for Electrical" for additional abbreviations, definitions, submittals, qualifications, testing agencies, and other Project requirements applicable to Work specified in this Section.

          - Section 260011 "Facility Performance Requirements for Electrical" for seismic-load, wind-load, acoustical, and other field conditions applicable to Work specified in this Section.

      - ALLOWANCES

Retain this article if products and Work included in this Section are covered by lump-sum, unit-cost, quantity, or testing and inspection allowances.

        - See Section 012100 "Allowances" for description of allowances affecting items specified in this Section.

      - UNIT PRICES

Retain this article if products and Work specified in this Section are measured and paid for under the provisions of unit prices.

        - See Section 012200 "Unit Prices" for description of unit prices affecting items specified in this Section.

      - ALTERNATES

Retain this article if products and Work specified in this Section are proposed to be added to or deducted from the base bid amount under the provisions of alternates.

        - See Section 012300 "Alternates" for description of alternates affecting items specified in this Section.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

          - Fuseless attachment cord connectors.

          - Extra-hard-usage, jacketed, flexible cord.

          - Antimicrobial, extra-hard-usage, jacketed, flexible cord.

          - Hard-usage, jacketed, flexible cord.

          - Strain-relief cord grips.

Retain "Samples" Paragraph below if products have critical features needing hands-on appraisal.

        - Samples:

Retain subparagraph below to suit Project.

          - One for each kind of cord connector specified, in each finish and color specified.

Retain "Field Quality-Control Submittals" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field Quality-Control Submittals:

          - Field quality-control reports.

      - MAINTENANCE MATERIAL SUBMITTALS

See Section 017700 "Closeout Procedures" for submission of maintenance material items.

Extra stock items are replacement products.

        - Extra Stock Items: Furnish extra materials to Owner that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Cord Connectors: [One] <Insert number> of each kind.

Special tools are items that would not be available from a typical hardware store.

        - Special Tools: Proprietary equipment and software required to maintain, repair, adjust, or implement future changes to cord connectors.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - EXISTING PRODUCTS[ TO BE MODIFIED] [ TO BE REMOVED AND RE-INSTALLED]

        - Basis for Pricing: <Insert name of manufacturer; model number or series for existing product>.

        - Description: <Insert description of existing product, including special features, options, and finishes that may impact Work>.

        - Accessories: <Insert accessories included with existing product>.

      - FUSELESS ATTACHMENT CORD CONNECTORS

        - Description: Connectors for attachment to cord that do not incorporate switches or overcurrent protection.

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - General Characteristics:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Reference Standards: UL CCN AXUT and UL 498.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Indoor-Use, Dry Location Cord Connector <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Configuration: NEMA 5-15[ with lighted blade].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Indoor-Use, Sealed Cord Connector <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Configuration:

Retain one of 21 subparagraphs below.

              - NEMA 5-15[ with diagnostic LED indicator].

              - NEMA 5-20[ with diagnostic LED indicator].

              - NEMA 6-15.

              - NEMA 6-20.

              - NEMA L5-15.

              - NEMA L5-20[ with diagnostic LED indicator].

              - NEMA L5-30.

              - NEMA L6-15.

              - NEMA L6-20.

              - NEMA L6-30.

              - NEMA L7-15.

              - NEMA L7-20.

              - NEMA L7-30.

              - NEMA L14-20.

              - NEMA L14-30.

              - NEMA L15-20.

              - NEMA L15-30.

              - NEMA L16-20.

              - NEMA L16-30.

              - NEMA L17-30.

              - NEMA L18-30.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Hospital-Grade, Indoor-Use, Sealed Cord Connector <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Configuration: [NEMA 5-15] [NEMA 5-20].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Indoor-Use, Compression-Grip, Sealed Cord Connector <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Configuration:

Retain one of 11 subparagraphs below.

              - NEMA 5-15[ with diagnostic LED indicator].

              - NEMA 5-20[ with diagnostic LED indicator].

              - NEMA 6-15.

              - NEMA 6-20.

              - NEMA L5-15.

              - NEMA L5-20[ with diagnostic LED indicator].

              - NEMA L5-30.

              - NEMA L6-15.

              - NEMA L6-20.

              - NEMA L6-30.

              - NEMA L7-15.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Outdoor-Use, Watertight, Sealed Cord Connector <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Configuration:

Retain one of 21 subparagraphs below.

              - NEMA 5-15[ with diagnostic LED indicator].

              - NEMA 5-20[ with diagnostic LED indicator].

              - NEMA 6-15.

              - NEMA 6-20.

              - NEMA L5-15.

              - NEMA L5-20[ with diagnostic LED indicator].

              - NEMA L5-30.

              - NEMA L6-15.

              - NEMA L6-20.

              - NEMA L6-30.

              - NEMA L7-15.

              - NEMA L7-20.

              - NEMA L7-30.

              - NEMA L14-20.

              - NEMA L14-30.

              - NEMA L15-20.

              - NEMA L15-30.

              - NEMA L16-20.

              - NEMA L16-30.

              - NEMA L17-30.

              - NEMA L18-30.

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Antimicrobial, Watertight, Sealed Cord Connector <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Additional Characteristics: Antimicrobial additive embedded in connector grip polymer.

          - Options:

            - Configuration:

Retain one of 21 subparagraphs below.

              - NEMA 5-15.

              - NEMA 5-20.

              - NEMA 6-15.

              - NEMA 6-20.

              - NEMA L5-15.

              - NEMA L5-20.

              - NEMA L5-30.

              - NEMA L6-15.

              - NEMA L6-20.

              - NEMA L6-30.

              - NEMA L7-15.

              - NEMA L7-20.

              - NEMA L7-30.

              - NEMA L14-20.

              - NEMA L14-30.

              - NEMA L15-20.

              - NEMA L15-30.

              - NEMA L16-20.

              - NEMA L16-30.

              - NEMA L17-30.

              - NEMA L18-30.

      - EXTRA-HARD-USAGE, JACKETED, FLEXIBLE CORD

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - General Characteristics:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Reference Standards: UL CCN ZJCZ and UL 62.

            - 600 V, 90 deg C, hard service cord with oil-resistant jacket[ and oil-resistant insulation] for pendant or portable extra-hard usage in damp locations.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Oil-Resistant, Extra-Hard-Usage, Jacketed, Flexible Cord for Indoor Damp Locations <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Flexible Cord Type: [STO] [STOO] [SEO] [SEOO] [SO] [SOO].

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Oil-Resistant, Extra-Hard-Usage, Jacketed, Flexible Cord for Outdoor or Indoor Wet Locations <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Flexible Cord Type: [STOW] [STOOW] [SEOW] [SEOOW] [SOW] [SOOW].

      - ANTIMICROBIAL, EXTRA-HARD-USAGE, JACKETED, FLEXIBLE CORD

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - General Characteristics:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Reference Standards: UL CCN ZJCZ and UL 62.

            - 600 V, 90 deg C, hard service cord with oil-resistant jacket for pendant or portable extra-hard usage in damp or wet locations.

            - Antimicrobial additive embedded in jacket polymer.

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Antimicrobial, Oil-Resistant, Extra-Hard-Usage, Jacketed, Flexible Cord for Outdoor or Indoor Wet Locations <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Flexible Cord Type: [STOW] [SEOW].

            - Configuration:

Retain one of five subparagraphs below.

              - No. 14 AWG, two wires and equipment ground.

              - No. 12 AWG, two wires and equipment ground.

              - No. 12 AWG, three wires and equipment ground.

              - No. 10 AWG, two wires and equipment ground.

              - No. 10 AWG, three wires and equipment ground.

      - HARD-USAGE, JACKETED, FLEXIBLE CORD

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - General Characteristics:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Reference Standards: UL CCN ZJCZ and UL 62.

            - 300 V, 90 deg C, hard service cord with oil-resistant jacket[ and oil-resistant insulation] for pendant or portable extra-hard usage in damp locations.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Oil-Resistant, Hard-Usage, Jacketed, Flexible Cord for Indoor Damp Locations <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Flexible Cord Type: [SJTO] [SJTOO] [SJEO] [SJEOO] [SJO] [SJOO].

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Oil-Resistant, Hard-Usage, Jacketed, Flexible Cord for Outdoor or Indoor Wet Locations <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Flexible Cord Type: [SJTOW] [SJTOOW] [SJEOW] [SJEOOW] [SJOW] [SJOOW].

      - STRAIN-RELIEF CORD GRIPS

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - General Characteristics:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Reference Standards: UL CCN QCRV and UL 514B.

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Strain-Relief Cord Grip <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

Retain one of three subparagraphs below.

            - Strain-relief grip for bus drop cable.

            - Noninsulated strain-relief grip for flexible cord.

            - Insulated strain-relief grip for flexible cord.

- EXECUTION

      - INSTALLATION

        - Comply with manufacturer's instructions.

NFPA 70 and NECA NEIS 1 are already specified in Section 260010 "Supplemental Requirements for Electrical." Retain "Reference Standards" Paragraph below to specify other standards applicable to Work specified in this Section.

        - Reference Standards:

          - <Insert system or product group>: Unless more stringent requirements are specified in Contract Documents or manufacturers' instructions, comply with <Insert list of standards designations>.

          - Consult Architect for resolution of conflicting requirements.

        - Special Techniques:

          - <Insert more stringent installation requirements that supplement or supersede listed standards and manufacturers' instructions>.

        - Interfaces with Other Work:

          - Coordinate with Section 262726.43 "Special-Purpose Power Outlet Assemblies" for installation of connectors and cords on fabricated power-outlet cord management assemblies.

          - Coordinate installation of new products for <Insert system or product group> with existing conditions.

            - <Insert requirements for transition between new and existing>.

          - Coordinate with <Insert Section number and title> for <Insert description of interfacing related Work>.

            - <Insert requirements for transition between this Section and related Work>.

      - FIELD QUALITY CONTROL

        - [Acceptance ]Testing Preparation:

          - <Insert requirements>.

Retain first paragraph below to require that field quality-control tests be witnessed. Local ordinance or custom may require that authorities having jurisdiction witness the testing.

        - Field tests and inspections must be witnessed by [Architect] [Tenant] [authorities having jurisdiction] <Insert names or titles of witnesses>.

        - Tests and Inspections:

          - Perform tests and inspections indicated in manufacturer's instructions.

          - <Insert Project-specific test or inspection>.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Nonconforming Work:

          - Unit will be considered defective if it does not pass tests and inspections.

          - Remove and replace defective units and retest.

        - Assemble and submit test and inspection reports.

Retain "Manufacturer Services" Paragraph below if manufacturer's representative is required to support or supervise the administrant specified in Section 260010 "Supplemental Requirements for Electrical" for field tests and inspections performed by Installer or third-party agencies.

        - Manufacturer Services:

Retain "supervise" option in subparagraph below when third-party tests and inspections must be witnessed and approved by factory-authorized service representative to satisfy special extended warranty requirements. In some cases, Installer may be factory authorized under warranty provisions to fulfill this role.

          - Engage factory-authorized service representative to [support] [supervise] field tests and inspections.

      - PROTECTION

        - After installation, protect connectors, cords, and plugs from construction activities. Remove and replace items that are contaminated, defaced, damaged, or otherwise caused to be unfit for use prior to acceptance by Owner.

END OF SECTION 262726.51