Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 262933 - CONTROLLERS FOR FIRE PUMP DRIVERS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Full-service controllers.

          - Adjustable-speed fire-pump controller.

          - Limited-service controllers.

          - Standalone ATS.

          - Controllers for diesel-drive fire pumps.

          - Controllers for pressure-maintenance pumps.

          - Remote alarm panels.

          - Low-suction-shutdown panels.

          - Enclosures.

        - Related Requirements:

Always retain first two subparagraphs below.

          - Section 260010 "Supplemental Requirements for Electrical" for additional abbreviations, definitions, submittals, qualifications, testing agencies, and other Project requirements applicable to Work specified in this Section.

          - Section 260011 "Facility Performance Requirements for Electrical" for seismic-load, wind-load, acoustical, and other field conditions applicable to Work specified in this Section.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

        - ECM: Electronic control module.

        - MCCB: Molded-case circuit breaker.

        - PID: Proportional integral derivative.

      - ACTION SUBMITTALS

        - Product Data: For each type of product. Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

        - Shop Drawings: For each type of product indicated.

          - Include plans, elevations, sections, and attachment details.

          - Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

          - Show tabulations of the following:

            - Each installed unit's type and details.

            - Enclosure types and details for types other than NEMA 250, Type 2.

            - Factory-installed devices.

            - Nameplate legends.

            - Short-circuit current (withstand) rating of integrated unit.

            - Features, characteristics, ratings, and factory settings of individual overcurrent protective devices.

Retain first subparagraph below if specifying modifications in Part 2.

            - Specified modifications.

          - Include diagrams for power, signal, alarm, control wiring, and pressure-sensing tubing.

      - INFORMATIONAL SUBMITTALS

Retain "Product Certificates" Paragraph below to require submittal of product certificates from manufacturers.

        - Product Certificates: For each type of product indicated, from manufacturer.

        - Source quality-control reports.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

      - MAINTENANCE MATERIAL SUBMITTALS

Revise this article to include extra materials that Owner may require or that are critical to the functionality of equipment. This list does not include spare equipment mandated by NFPA 20, such as current limiters. Consult manufacturers for recommended extra materials to retain or insert.

        - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Indicating Lights: [Two] <Insert number> of each type and color of lens installed; [two] <Insert number> of each type and size of lamp installed.

          - Auxiliary Contacts: [One] <Insert number> for each size and type of magnetic contactor installed.

          - Power Contacts: [Three] <Insert number> for each size and type of magnetic contactor installed.

          - Contactor Coils: [One] <Insert number> for each size and type of magnetic controller installed.

          - Relay Boards: [One] <Insert number> for each size and type of relay board installed.

          - Operator Interface: [One] <Insert number> microprocessor board(s), complete with display and membrane keypad.

          - <Insert extra materials>.

      - QUALITY ASSURANCE

        - Source Limitations: Obtain fire-pump controllers and associated equipment from single source or producer.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - PERFORMANCE REQUIREMENTS

        - Comply with NFPA 20.

Retain "IEEE Compliance" Paragraph below for projects in seismic areas. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems."

        - IEEE Compliance: Fabricate and test enclosed controllers in accordance with IEEE 344 to withstand seismic forces defined in Section 260548.16 "Seismic Controls for Electrical Systems."

        - Electrical Components, Devices, and Accessories: Listed and labeled in accordance with NFPA 70, by a qualified electrical testing laboratory, and marked for intended location and application.

      - FULL-SERVICE CONTROLLERS

Show voltage, size, type, accessories, and enclosure type for each controller on Drawings if not included in the Section Text. See "Specifying Fire-Pump Controllers" Article in the Evaluations for selection considerations.

Standard features vary considerably among manufacturers of full-service, electric-motor-driver, fire-pump controllers; not all features in this article are available for every type and from every listed manufacturer. Features vary in accordance with motor characteristics and the driven-equipment operating criteria. Verify availability and unique characteristics with manufacturers; indicate in the Section Text or show on Drawings those features that apply to each controller. See "Peculiar Characteristics of Controllers for Electric-Drive Fire Pumps" Article in the Evaluations for additional guidance.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

See "General Requirements for Fire-Pump Controllers" Article in the Evaluations for restrictions on using nonautomatic controllers.

Some authorities having jurisdiction or the Owner's insurance underwriter may require specific local approvals (e.g., the New York Department of Buildings) or an FM Approvals certification and mark. Insert additional or replacement standards or approvals in "General Requirements for Full-Service Controllers" Paragraph below.

        - General Requirements for Full-Service Controllers:

          - Comply with NFPA 20 and [UL 218] <Insert standard>.

          - [Combined automatic and nonautomatic] [Nonautomatic] operation.

          - Factory assembled, wired, and tested; continuous-duty rated.

        - Method of Starting:

Retain first subparagraph below for controllers with automatic operation. Retain first option for controllers actuated by water flow in fire-suppression piping; retain second option for other starting means (e.g., fire-protection equipment, sequential starting), and provide details of starting method here or on Drawings.

          - [Pressure] [Nonpressure]-switch actuated.

Retain first two subparagraphs below for automatic operation and pressure-switch actuation.

            - Water-pressure-actuated switch and pressure transducer with independent high- and low-calibrated adjustments responsive to water pressure in fire-suppression piping.

            - System pressure recorder, electric ac driven, with spring backup.

Retain first two subparagraphs below for automatic operation.

            - Programmable minimum-run-time relay to prevent short cycling.

            - Programmable timer for weekly tests.

Retain "Magnetic Controller" or "Solid-State Controller" Subparagraph below. First option in first subparagraph is full-voltage starting; remaining options are reduced-voltage starting. See "Full-Voltage Controllers" and "Reduced-Voltage Controllers" articles in the Evaluations for additional guidance.

          - Magnetic Controller: [Across-the-line] [Autotransformer] [Part-winding] [Primary-resistor] [Primary-reactor] [Wye-delta (open transition)] [Wye-delta (closed transition)] <Insert type> type.

          - Solid-State Controller: [Reduced-voltage] <Insert type> type.

          - Emergency Start: Mechanically operated start handle that closes and retains the motor RUN contactor independent of electric or pressure actuators.

NFPA 20 restricts use of automatic shutdown. Retain first option in "Method of Stopping" Paragraph below if allowed and required to suit Project. See "General Requirements for Fire-Pump Controllers" Article in the Evaluations if retaining first option.

        - Method of Stopping: [Automatic and nonautomatic shutdown after automatic starting] [Nonautomatic].

Show controller short-circuit current (withstand) rating (or available short-circuit currents) on Drawings. Consider conductor size and distance from substation or supply transformers when calculating short-circuit currents at controllers.

        - Capacity: Rated for fire-pump-driver horsepower and short-circuit-current (withstand) rating equal to or greater than short-circuit current available at controller location.

Functions in "Method of Isolation and Overcurrent Protection" and "Door-Mounted Operator Interface and Controls" paragraphs below are the minimum required by NFPA 20; however, standard features and optional modifications vary considerably among manufacturers of fire-pump controllers; they must be closely coordinated with "General Requirements for Full-Service Controllers," "Method of Starting," and "Method of Stopping" paragraphs in this article. Verify availability and unique characteristics with manufacturers; include in first two paragraphs below or show on Drawings those features that apply to the controllers.

        - Method of Isolation and Overcurrent Protection: Interlocked isolating switch and nonthermal MCCB; with a common, externally mounted operating handle, and providing locked-rotor protection.

        - Door-Mounted Operator Interface and Controls:

          - Monitor, display, and control the devices, alarms, functions, and operations listed in NFPA 20 as required for drivers and controller types used.

          - Method of Control and Indication:

            - [Microprocessor-based logic] <Insert logic type> controller, with multiline digital readout.

            - [Membrane] <Insert keypad type> keypad.

            - [LED] <Insert lamp type> alarm and status indicating lights.

          - Local[ and Remote] Alarm and Status Indications:

Manufacturers offer numerous alarm and status indications and interfaces. Consult manufacturers for availability and types.

            - Controller power on.

            - Motor running condition.

            - Loss-of-line power.

            - Line-power phase reversal.

            - Line-power single-phase condition.

            - <Insert indication>.

          - Audible alarm, with silence push button.

          - Nonautomatic START and STOP push buttons or switches.

          - <Insert function>.

        - Optional Features:

Manufacturers offer numerous optional features for fire-pump controllers. Consult manufacturers for availability and limitations. Retain applicable features in "Extra Output Contacts" Subparagraph below; insert others to suit Project. Indicate requirements for and quantities of optional features on Drawings if not included here. These features are normally added-cost items.

          - Extra Output Contacts:

            - [One] <Insert number> NO contact(s) for motor running condition.

            - [One] <Insert number> set(s) of contacts for loss-of-line power.

            - [One] <Insert number> each, Form C contacts for high and low reservoir level.

            - <Insert contact type>.

          - Local alarm bell.

          - Door-mounted thermal or impact printer for alarm and status logs.

          - Operator Interface Communications Ports: USB, Ethernet, and TIA-485.

          - <Insert optional feature>.

Retain "ATS" Paragraph below if an ATS ahead of the fire-pump controller is required and the ATS is integral with the controller. See "Automatic Transfer Switches" Article in the Evaluations for additional guidance.

        - ATS:

          - Complies with NFPA 20, [UL 218] <Insert standard>, and [UL 1008] <Insert standard>.

          - Integral with controller as a listed combination fire-pump controller and power transfer switch.

          - Automatically transfers fire-pump controller from normal power supply to alternate power supply in event of power failure.

          - Allows manual transfer from one source to the other.

          - Alternate-Source Isolating and Disconnecting Means:

Retain one of first two subparagraphs below. Retain first subparagraph if the alternate source is a standby generator with a capacity of less than 225 percent of the motor's full-load current rating. Coordinate with upstream external overcurrent protection.

            - Integral molded-case switch, with an externally mounted operating handle.

NFPA 20 has separate, more stringent requirements for an integral ATS if the alternate source is a second utility service, an upstream ATS, or an emergency generator with a capacity exceeding 225 percent of the fire-pump motor's full-load current rating. Retain first subparagraph below if any of these situations apply.

            - Mechanically interlocked isolation switch and circuit breaker rated at a minimum of 115 percent of rated motor full-load current, with an externally mounted operating handle; circuit breaker must be provided with nonthermal sensing, instantaneous-only short-circuit overcurrent protection to comply with available fault currents.

          - Local[ and Remote] Alarm and Status Indications:

Manufacturers offer additional local and remote alarm and status indications and interfaces. Consult manufacturers for availability and types.

            - Normal source available.

            - Alternate source available.

            - In normal position.

            - In alternate position.

            - Isolating means open.

            - <Insert indication>.

          - Audible alarm, with silence push button.

          - Nonautomatic (manual, nonelectric) means of transfer.

Retain first three subparagraphs below if alternate power is from a standby generator.

          - Engine test push button.

          - Start generator output contacts.

          - Timer for weekly generator tests.

          - <Insert function>.

      - ADJUSTABLE-SPEED FIRE-PUMP CONTROLLER

Show voltage, size, type, accessories, and enclosure type for each controller on Drawings if not included in the Section Text. See "Specifying Fire-Pump Controllers" Article in the Evaluations for selection considerations.

Standard features vary considerably among manufacturers of full-service, electric-motor-driver, fire-pump controllers; not all features in this article are available for every type and from every listed manufacturer. Features vary in accordance with motor characteristics and the driven-equipment operating criteria. Verify availability and unique characteristics with manufacturers; indicate in the Section Text or show on Drawings those features that apply to each controller. See "Peculiar Characteristics of Controllers for Electric-Drive Fire Pumps" Article in the Evaluations for additional guidance.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

See "General Requirements for Fire-Pump Controllers" Article in the Evaluations for restrictions on using nonautomatic controllers.

Some authorities having jurisdiction or the Owner's insurance underwriter may require specific local approvals (e.g., the New York Department of Buildings) or an FM Approvals certification and mark. Insert additional or replacement standards or approvals in "General Requirements for Adjustable-Speed Controllers" Paragraph below.

        - General Requirements for Adjustable-Speed Controllers:

          - Comply with NFPA 20 and [UL 218] <Insert standard>.

          - [Combined automatic and nonautomatic] [Nonautomatic] operation.

          - Factory assembled, wired, and tested; continuous-duty rated.

        - Method of Starting:

Retain first subparagraph below for controllers with automatic operation. Retain first option for controllers actuated by water flow in fire-suppression piping; retain second option for other starting means (e.g., fire-protection equipment, sequential starting), and provide details of starting method here or on Drawings.

          - Pressure-switch actuated.

Retain first two subparagraphs below for automatic operation and pressure-switch actuation.

            - Water-pressure-actuated switch and pressure transducer with independent high- and low-calibrated adjustments responsive to water pressure in fire-suppression piping.

            - System pressure recorder, electric ac driven, with spring backup.

Retain first two subparagraphs below for automatic operation.

            - Programmable minimum-run-time relay to prevent short cycling.

            - Programmable timer for weekly tests.

Retain "ASD" or "Emergency Start" Subparagraph below. First option in first subparagraph is full-voltage starting; remaining options are reduced-voltage starting. See "Full-Voltage Controllers" and "Reduced-Voltage Controllers" articles in the Evaluations for additional guidance.

          - ASD: [Across-the-line bypass] [Autotransformer bypass] [Digital soft-start bypass] <Insert type> type.

          - Emergency Start: Mechanically operated start handle that closes and retains the motor RUN contactor independent of electric or pressure actuators.

NFPA 20 restricts use of automatic shutdown. Retain first option in "Method of Stopping" Paragraph below if allowed and required to suit Project. See "General Requirements for Fire-Pump Controllers" Article in the Evaluations if retaining first option.

        - Method of Stopping: [Automatic and nonautomatic shutdown after automatic starting] [Nonautomatic].

Show controller short-circuit current (withstand) rating (or available short-circuit currents) on Drawings. Consider conductor size and distance from substation or supply transformers when calculating short-circuit currents at controllers.

        - Capacity: Rated for fire-pump-driver horsepower and short-circuit-current (withstand) rating equal to or greater than short-circuit current available at controller location.

Functions in "Method of Isolation and Overcurrent Protection" and "Door-Mounted Operator Interface and Controls" paragraphs below are the minimum required by NFPA 20; however, standard features and optional modifications vary considerably among manufacturers of fire-pump controllers; they must be closely coordinated with "General Requirements for Full-Service Controllers," "Method of Starting," and "Method of Stopping" paragraphs in previous article. Verify availability and unique characteristics with manufacturers; include in first two paragraphs below or show on Drawings those features that apply to the controllers.

        - Method of Isolation and Overcurrent Protection: Interlocked isolating switch and nonthermal MCCB; with a common, externally mounted operating handle, and providing locked-rotor protection.

        - Door-Mounted Operator Interface and Controls:

          - Monitor, display, and control the devices, alarms, functions, and operations listed in NFPA 20 as required for drivers and controller types used.

          - Method of Control and Indication:

            - [Microprocessor-based logic] <Insert logic type> controller, with multiline digital readout.

            - [Membrane] <Insert keypad type> keypad.

            - [LED] <Insert lamp type> alarm and status indicating lights.

          - Local[ and Remote] Alarm and Status Indications:

Manufacturers offer numerous alarm and status indications and interfaces. Consult manufacturers for availability and types.

            - Controller power on.

            - Motor running condition.

            - Loss-of-line power.

            - Line-power phase reversal.

            - Line-power single-phase condition.

            - <Insert indication>.

          - Audible alarm, with silence push button.

          - Nonautomatic START and STOP push buttons or switches.

          - Set pressure and system pressure.

          - <Insert function>.

        - Optional Features:

Manufacturers offer numerous optional features for fire-pump controllers. Consult manufacturers for availability and limitations. Retain applicable features in "Extra Output Contacts" Subparagraph below; insert others to suit Project. Indicate requirements for and quantities of optional features on Drawings if not included here. These features are normally added-cost items.

          - Extra Output Contacts:

            - [One] <Insert number> NO contact(s) for motor running condition.

            - [One] <Insert number> set(s) of contacts for loss-of-line power.

            - [One] <Insert number> each, Form C contacts for high and low reservoir level.

            - <Insert contact type>.

          - Local alarm bell.

          - Door-mounted thermal or impact printer for alarm and status logs.

          - Operator Interface Communications Ports: USB, Ethernet, and TIA-485.

          - <Insert optional feature>.

Retain "ATS" Paragraph below if an ATS ahead of the fire-pump controller is required and the ATS is integral with the controller. See "Automatic Transfer Switches" Article in the Evaluations for additional guidance.

        - ATS:

          - Complies with NFPA 20, [UL 218] <Insert standard>, and [UL 1008] <Insert standard>.

          - Integral with controller as a listed combination fire-pump controller and power transfer switch.

          - Automatically transfers fire-pump controller from normal power supply to alternate power supply in event of power failure.

          - Allows manual transfer from one source to the other.

          - Alternate-Source Isolating and Disconnecting Means:

Retain one of first two subparagraphs below. Retain first subparagraph if the alternate source is a standby generator with a capacity of less than 225 percent of the motor's full-load current rating. Coordinate with upstream external overcurrent protection.

            - Integral molded-case switch, with an externally mounted operating handle.

NFPA 20 has separate, more stringent requirements for an integral ATS if the alternate source is a second utility service, an upstream ATS, or an emergency generator with a capacity exceeding 225 percent of the fire-pump motor's full-load current rating. Retain first subparagraph below if any of these situations apply.

            - Mechanically interlocked isolation switch and circuit breaker rated at a minimum of 115 percent of rated motor full-load current, with an externally mounted operating handle; circuit breaker must be provided with nonthermal sensing, instantaneous-only short-circuit overcurrent protection to comply with available fault currents.

          - Local[ and Remote] Alarm and Status Indications:

Manufacturers offer additional local and remote alarm and status indications and interfaces. Consult manufacturers for availability and types.

            - Normal source available.

            - Alternate source available.

            - In normal position.

            - In alternate position.

            - Isolating means open.

            - <Insert indication>.

          - Audible alarm, with silence push button.

          - Nonautomatic (manual, nonelectric) means of transfer.

Retain first three subparagraphs below if alternate power is from a standby generator.

          - Engine test push button.

          - Start generator output contacts.

          - Timer for weekly generator tests.

          - <Insert function>.

        - ASD Operational Modes:

          - Operated in a PID process control loop to control the centrifugal fire-pump speed to limit the system pressure.

          - PID controller receives signal from the pressure transducer that measures the system pressure.

          - PID output controls the current frequency of the pump motor regulating the pump speed to maintain the system pressure at the set point.

          - Upon detection of a drive failure, the drive is bypassed and the motor runs at full speed.

          - Once set point pressure is maintained for a set period, the drive soft stops the pump motor.

          - Provides both soft start and soft stop of the pump motor.

      - LIMITED-SERVICE CONTROLLERS

Show voltage, size, type, accessories, and enclosure type for each controller on Drawings if not included in the Section Text. See "Specifying Fire-Pump Controllers" Article in the Evaluations for selection considerations.

Standard features vary considerably among manufacturers of limited-service, electric-motor-driver, fire-pump controllers; not all features in this article are available for every type and from every listed manufacturer. Features depend on motor characteristics and driven-equipment operating criteria. Verify availability and unique characteristics with manufacturers; include in the Section Text or show on Drawings those features that apply to each controller. See "Peculiar Characteristics of Controllers for Electric-Drive Fire Pumps" and "Limited-Service Controllers" articles in the Evaluations for additional guidance.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

See "General Requirements for Fire-Pump Controllers" Article in the Evaluations for restrictions on using nonautomatic controllers.

Some authorities having jurisdiction or the Owner's insurance underwriter may require specific local approvals (e.g., the New York Department of Buildings) or an FM Approvals certification and mark. Insert additional or replacement standards or approvals in "General Requirements for Limited-Service Controllers" Paragraph below.

        - General Requirements for Limited-Service Controllers:

          - Comply with NFPA 20 and [UL 218] <Insert standard>.

          - [Combined automatic and nonautomatic] [Nonautomatic] operation.

          - Factory assembled, wired, and tested; continuous-duty rated.

        - Method of Starting:

Retain first subparagraph below for controllers with automatic operation. Retain first option for controllers actuated by water flow in fire-suppression piping; retain second option for other starting means (e.g., fire-protection equipment, sequential starting), and provide details of starting method here or on Drawings.

          - [Pressure] [Nonpressure]-switch actuated.

Retain first two subparagraphs below for automatic operation and pressure-switch actuation.

            - Water-pressure-actuated switch and pressure transducer with independent high- and low-calibrated adjustments responsive to water pressure in fire-suppression piping.

            - System pressure recorder, electric ac driven, with spring backup.

Retain first two subparagraphs below for automatic operation.

            - Programmable minimum-run-time relay to prevent short cycling.

            - Programmable timer for weekly tests.

Full-voltage, across-the-line starting is the only starting method allowed by NFPA 20 for limited-service controllers.

          - Across-the-line magnetic controller.

          - Emergency Start: Mechanically operated start handle that closes and retains the motor RUN contactor independent of electric or pressure actuators.

NFPA 20 restricts use of automatic shutdown. Retain first option in "Method of Stopping" Paragraph below if allowed and required to suit Project. See "General Requirements for Fire-Pump Controllers" Article in the Evaluations if retaining first option.

        - Method of Stopping: [Automatic and nonautomatic shutdown after automatic starting] [Nonautomatic].

Show controller short-circuit current (withstand) rating (or available short-circuit currents) on Drawings. Consider conductor size and distance from substation or supply transformers when calculating short-circuit currents at controllers.

        - Capacity: Rated for fire-pump-driver horsepower and short-circuit-current (withstand) rating equal to or greater than short-circuit current available at controller location.

Functions in "Method of Isolation and Overcurrent Protection" and "Door-Mounted Operator Interface and Controls" paragraphs below are the minimum required by NFPA 20; however, standard features and optional modifications vary considerably among manufacturers of fire-pump controllers; they must be closely coordinated with "General Requirements for Limited-Service Controllers," "Method of Starting," and "Method of Stopping" paragraphs in this article. Verify availability and unique characteristics with manufacturers; include in first two paragraphs below or show on Drawings those features that apply to the controllers.

        - Method of Isolation and Overcurrent Protection: Inverse-time, nonadjustable MCCB, with an externally mounted operating handle.

        - Door-Mounted Operator Interface and Controls:

          - Monitor, display, and control the devices, alarms, functions, and operations listed in NFPA 20 as required for drivers and controller types used.

          - Method of Control and Indication:

            - [Microprocessor-based logic] <Insert logic type> controller, with multiline [LCD] <Insert display type> digital readout.

            - [Membrane] <Insert keypad type> keypad.

            - [LED] <Insert lamp type> alarm and status indicating lights.

          - Local[ and Remote] Alarm and Status Indications:

Manufacturers offer numerous alarm and status indications and interfaces. Consult manufacturers for availability and types.

            - Controller power on.

            - Motor running condition.

            - Loss-of-line power.

            - Line-power phase reversal.

            - Line-power single-phase condition.

            - <Insert indication>.

          - Audible alarm, with silence push button.

          - Nonautomatic START and STOP push buttons.

          - <Insert function>.

        - Optional Features:

Manufacturers offer numerous optional features for fire-pump controllers. Consult manufacturers for availability and limitations. Retain applicable features in "Extra Output Contacts" Subparagraph below; insert others to suit Project. Indicate requirements for and quantities of optional features on Drawings if not included here. These features are normally added-cost items.

          - Extra Output Contacts:

            - [One] <Insert number> NO contact(s) for motor running condition.

            - [One] <Insert number> set(s) of contacts for loss-of-line power.

            - [One] <Insert number> each, Form C contacts for high and low reservoir level.

            - <Insert contact type>.

          - Local alarm bell.

          - Door-mounted thermal or impact printer for alarm and status logs.

          - Operator Interface Communications Ports: USB, Ethernet, and TIA-485.

          - <Insert optional feature>.

Retain "ATS" Paragraph below if an ATS ahead of the fire-pump controller is required and the ATS is integral with the controller. See "Automatic Transfer Switches" Article in the Evaluations for additional guidance.

        - ATS:

          - Complies with NFPA 20, [UL 218] <Insert standard>, and [UL 1008] <Insert standard>.

          - Integral with controller as a listed combination fire-pump controller and power transfer switch.

          - Automatically transfers fire-pump controller from normal power supply to alternate power supply in event of power failure.

          - Allows manual transfer from one source to the other.

          - Alternate-Source Isolating and Disconnecting Means:

Retain one of first two subparagraphs below. Retain first subparagraph if the alternate source is a standby generator with a capacity of less than 225 percent of the motor's full-load current rating. Coordinate with upstream external overcurrent protection.

            - Integral molded-case switch, with an externally mounted operating handle.

NFPA 20 has separate, more stringent requirements for an integral ATS if the alternate source is a second utility service, an upstream ATS, or an emergency generator with a capacity exceeding 225 percent of the fire-pump motor's full-load current rating. Retain first subparagraph below if any of these situations apply.

            - Mechanically interlocked isolation switch and circuit breaker rated at a minimum of 115 percent of rated motor full-load current, with an externally mounted operating handle; circuit breaker must be provided with nonthermal sensing, instantaneous-only, short-circuit overcurrent protection to comply with available fault currents.

          - Local[ and Remote] Alarm and Status Indications:

Manufacturers offer additional local and remote alarm and status indications and interfaces. Consult manufacturers for availability and types.

            - Normal source available.

            - Alternate source available.

            - In normal position.

            - In alternate position.

            - Isolating means open.

            - <Insert indication>.

          - Audible alarm, with silence push button.

          - Nonautomatic (manual, nonelectric) means of transfer.

Retain one of first three subparagraphs below if alternate power is from a standby generator.

          - Engine test push button.

          - Start generator output contacts.

          - Timer for weekly generator tests.

          - <Insert function>.

      - STANDALONE ATS

Retain this article if an ATS ahead of the fire-pump controller is required, and the ATS is external to the controller. Show voltage, size, type, accessories, and enclosure type for each ATS on Drawings if not included in the Section Text. See "Automatic Transfer Switches" Article in the Evaluations for additional guidance.

Standard features vary considerably among manufacturers of ATS for electric-motor-driver, fire-pump controllers; not all features in this article are available for every type and from every listed manufacturer. Features depend on controller characteristics and driven-equipment operating criteria; they may not be compatible with controllers other than those of the same manufacturer. Verify availability, suitability with the specified or existing controller, and unique characteristics with manufacturer; include in the Section Text or show on Drawings those features that apply to each ATS.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Some authorities having jurisdiction or the Owner's insurance underwriter may require specific local approvals (e.g., the New York Department of Buildings) or an FM Approvals certification and mark. Insert additional or replacement standards or approvals in "General Requirements for Standalone ATS" Paragraph below.

NFPA 20 does not allow nonautomatic-only operation for fire-pump controller transfer switches.

        - General Requirements for Standalone ATS:

          - Complies with NFPA 20, [UL 218] <Insert standard>, and [UL 1008] <Insert standard>.

          - Automatic and nonautomatic operation.

          - Separate from controller and individually listed as a fire-pump-controller power transfer switch.

          - Automatically transfers fire-pump controller from normal power supply to alternate power supply in event of power failure.

          - Allows manual transfer from one source to the other; factory assembled, wired, and tested.

Indicate ATS short-circuit current (withstand) rating (or available short-circuit currents) on Drawings. Consider conductor size and distance from substation or supply transformers when calculating short-circuit currents at the ATS.

        - Capacity: Rated for fire-pump-driver horsepower and short-circuit-current (withstand) rating equal to or greater than short-circuit current available at ATS location.

Functions in this article are the minimum required by NFPA 20; however, standard features and optional features vary considerably among manufacturers of ATS for fire-pump controllers; they must be closely coordinated with "General Requirements for Full-Service Controllers," "General Requirements for Limited-Service Controllers," "Method of Starting," and "Method of Stopping" paragraphs in electric controller articles. Verify availability and unique characteristics with manufacturers; include in first two paragraphs below or show on Drawings those features that apply to the ATS.

        - Alternate-Source Isolating and Disconnecting Means:

Retain one of first two subparagraphs below. Retain first subparagraph if the alternate power source is supplied from a standby generator, and coordinate with upstream external overcurrent protection; retain second subparagraph for an alternate power source from a second utility. NFPA 20 allows the isolating and overcurrent protection means to be external and upstream of standalone ATS; however, listed manufacturers incorporate the isolating means for alternate power from a standby generator or second utility service.

          - Integral molded-case switch, with an externally mounted operating handle.

          - Mechanically interlocked isolation switch and circuit breaker rated at a minimum of 115 percent of rated motor full-load current.

            - Externally mounted operating handle.

            - Circuit breaker provided with nonthermal sensing, instantaneous-only, short-circuit overcurrent protection.

            - Equipped with a voltage surge arrester.

        - Door-Mounted Operator Interface and Controls:

          - Monitor, display, and control devices, alarms, functions, and operations listed in NFPA 20 as required for drivers and controller types used.

          - Method of Control and Indication:

            - [Microprocessor-based logic] <Insert logic type> controller, with multiline [LCD] <Insert display type> readout.

            - [Membrane] <Insert keypad type> keypad.

            - [LED] <Insert lamp type> alarm and status indicating lights.

          - Local[ and Remote] Alarm and Status Indications:

Manufacturers offer additional local and remote alarm and status indications and interfaces. Consult manufacturers for availability and types.

            - Normal source available.

            - Alternate source available.

            - In normal position.

            - In alternate position.

            - Isolating means open.

            - <Insert indication>.

          - Audible alarm, with silence push button.

          - Nonautomatic (manual, nonelectric) means of transfer.

Retain first three subparagraphs below if alternate power is from a standby generator.

          - Engine test push button.

          - Start generator output contacts.

          - Timer for weekly generator tests.

          - <Insert function>.

        - Optional Features:

Manufacturers offer optional features and enhancements for ATS. Consult manufacturers for availability and limitations. Retain applicable features in "Extra Output Contacts" Subparagraph below; insert others to suit Project. Indicate requirements for and quantities of optional features on Drawings if not included here. These features are normally added-cost items.

          - Extra Output Contacts:

            - [One] <Insert number> each, Form A; isolating means open.

            - [One] <Insert number> each, Form C; in normal or alternate position.

            - <Insert contact type>.

          - Door-mounted thermal or impact printer for alarm and status logs.

          - Operator Interface Communications Ports: USB, Ethernet, and TIA-485.

          - <Insert optional feature>.

      - CONTROLLERS FOR DIESEL-DRIVE FIRE PUMPS

Show voltage, size, type, accessories, and enclosure type for each controller on Drawings if not included in the Section Text. See "Specifying Fire-Pump Controllers" Article in the Evaluations for selection considerations.

Standard features vary considerably among manufacturers of diesel-engine-driver, fire-pump controllers; not all features in this article are available for every type and from every listed manufacturer. Features depend on motor characteristics and driven-equipment operating criteria. Verify availability and unique characteristics with manufacturer; include in the Section Text or show on Drawings those features that apply to each controller. See "Peculiar Characteristics of Controllers for Diesel-Drive Fire Pumps" Article in the Evaluations for additional guidance.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Some authorities having jurisdiction or the Owner's insurance underwriter may require specific local approvals (e.g., the New York Department of Buildings) or an FM Approvals certification and mark. Insert additional or replacement standards or approvals in "General Requirements for Controllers" Paragraph below.

        - General Requirements for Controllers:

          - Comply with NFPA 20 and [UL 218] <Insert standard>.

          - [Combined automatic and nonautomatic] [Nonautomatic] operation.

          - Factory assembled, wired, and tested.

        - Method of Starting:

Retain first subparagraph below for controllers with automatic operation. Retain first option for controllers actuated by water flow in fire-suppression piping; retain second option for other starting means (e.g., fire-protection equipment, sequential starting), and provide details of starting method here or on Drawings.

          - [Pressure] [Nonpressure]-switch actuated.

Retain first two subparagraphs below for automatic operation and pressure-switch actuation.

            - Water-pressure-actuated switch and pressure transducer with independent high- and low-calibrated adjustments responsive to water pressure in fire-suppression piping.

            - System pressure recorder, electric ac driven, with spring backup.

Retain first two subparagraphs below for automatic operation.

            - Programmable minimum-run-time relay to prevent short cycling.

            - Programmable timer for weekly tests.

Only a battery-powered starting method is allowed by NFPA 20 for diesel-engine controllers.

          - Dual, redundant dc-voltage battery units, with automatic changeover.

          - Emergency Control: Bypasses automatic control circuits during manual starting and running.

          - Automatic engine start on loss of ac power to the controller.

NFPA 20 restricts use of automatic shutdown. Retain first option in "Method of Stopping" Paragraph below if allowed and required to suit Project. See "General Requirements for Fire-Pump Controllers" Article in the Evaluations if retaining first option.

        - Method of Stopping: [Automatic and nonautomatic shutdown after automatic starting] [Nonautomatic].

Functions in "Door-Mounted Operator Interface and Controls" Paragraph below are the minimum required by NFPA 20; however, standard features and optional modifications vary considerably among manufacturers of fire-pump controllers; they must be closely coordinated with "General Requirements for Controllers," "Method of Starting," and "Method of Stopping" paragraphs in this article. Verify availability and unique characteristics with manufacturers; include in first paragraph or show on Drawings those features that apply to the controllers.

        - Door-Mounted Operator Interface and Controls:

          - Monitor, display, and control devices, alarms, functions, and operations listed in NFPA 20 as required for drivers and controller types used.

          - Method of Control and Indication:

            - [Microprocessor-based logic] <Insert logic type> controller, with multiline [LCD] <Insert display type> readout.

            - [Membrane] <Insert keypad type> keypad.

            - [LED] <Insert lamp type> alarm and status indicating lights.

          - Local[ and Remote] Alarm and Status Indications:

Manufacturers offer numerous local and remote alarm and status indications and interfaces. Consult manufacturers for availability and types.

            - Controller power on.

            - Engine-lubrication-system critically low oil pressure.

            - Engine-jacket coolant high temperature.

            - Engine fail-to-start.

            - Engine overspeed shutdown.

            - Low fuel level.

            - Missing or failed battery.

            - Battery charger failure.

Retain first subparagraph below for engines equipped with pressure-limiting controls.

            - System overpressure.

Retain first two subparagraphs below for engines equipped with ECM controls.

            - ECM selector switch in alternate ECM position.

            - Fuel injector malfunction.

            - <Insert indication>.

NFPA 20 does not allow a silence switch or push button for alarms listed in this article.

          - Audible alarm.

          - Nonautomatic START and STOP push buttons or switches.

          - <Insert function>.

        - Optional Features:

Manufacturers offer numerous optional features for fire-pump controllers. Consult manufacturers for availability and limitations. Retain applicable optional features in "Extra Output Contacts" Subparagraph below; insert others to suit Project. Indicate requirements for and quantities of optional features on Drawings if not included here.

          - Extra Output Contacts:

            - [One] <Insert number> Form C contacts for low pump-room temperature.

            - [One] <Insert number> each, Form C contacts for high and low fuel levels.

            - [One] <Insert number> each, Form C contacts for high and low reservoir levels.

            - <Insert contact type>.

          - Door-mounted thermal or impact printer for alarm and status logs.

          - Operator Interface Communications Ports: USB, Ethernet, and TIA-485.

NFPA 20 allows use of diesel-engine controllers "to supply essential and necessary ac or dc power to operate pump room dampers and engine oil heaters and other associated and required engine equipment only when provided with factory-equipped, dedicated, field terminals and overcurrent protection." Consult manufacturers for availability of optional feature in first subparagraph below; retain if required.

          - Powered louver contacts.

          - Powered engine-oil heater contacts.

          - <Insert optional feature>.

        - Battery Charger System:

          - Built-in, independent, dual battery chargers with automatic changeover; [12 V(dc)] [24 V(dc)] for [lead-acid] [nickel-cadmium] batteries.

          - Standard: [UL 1236] <Insert standard>.

      - CONTROLLERS FOR PRESSURE-MAINTENANCE PUMPS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - General Requirements for Pressure-Maintenance-Pump Controllers:

          - Type: UL 508, factory-assembled, -wired, and -tested, across-the-line controller; for combined automatic and manual operation.

          - Enclosure: UL 508 and NEMA 250, Type 2 for wall-mounting.

          - Factory assembled, wired, and tested.

          - Finish: Manufacturer's standard color paint.

        - Rate controller for scheduled horsepower and include the following:

          - Fusible disconnect switch.

          - Pressure switch.

          - Hand-off-auto selector switch.

          - Pilot light.

          - Running period timer.

      - REMOTE ALARM PANELS

NFPA 20 requires use of a remote alarm panel located in an area that is constantly attended if the fire-pump controller is in a location that is not constantly attended or supervised. See "Remote Alarm Panels" Article in the Evaluations for additional guidance.

        - General Requirements for Remote Alarm Panels: Factory assembled, wired, and tested; and complying with NFPA 20 and [UL 218] <Insert standard>.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Not all features, accessories, and options in this article are available from every listed manufacturer. Verify availability and unique characteristics with manufacturers.

Retain first and last options in first paragraph below if a separate and redundant normal power source is provided to the panel. Not all listed manufacturers offer dual-voltage sources.

        - Supervisory[ and Normal] Control Voltage: [120 V(ac)] [240 V(ac)] <Insert voltage>; [single] [dual] source.

Alarms and status indications in "Audible and Visual Alarm and Status Indications for Electric-Driven Pump Controllers" and "Audible and Visual Alarm and Status Indications for Diesel-Driven Pump Controllers" paragraphs below are the minimum required by NFPA 20; however, standard and optional features vary considerably among manufacturers of remote alarm panels. Verify availability and unique characteristics with manufacturer; include in first paragraph below or show on Drawings those features that apply to each alarm panel. Retain first paragraph for electric controllers; retain second paragraph for diesel-engine controllers.

        - Audible and Visual Alarm and Status Indications for Electric-Driven Pump Controllers:

          - Driver running.

          - Loss of phase.

          - Phase reversal.

          - Supervised power on.

If retaining second option in first subparagraph below, insert list of required alarms.

          - [Common] [Separate] trouble on the controller.

            - <Insert alarm>.

Retain first subparagraph below if power is supplied from multiple sources.

          - Controller connected to alternate power source.

          - <Insert indication>.

        - Audible and Visual Alarm and Status Indications for Diesel-Driven Pump Controllers: Manufacturer's standard indicating lights; [push-to-test] [non-push-to-test, with separate test push button].

          - Engine running.

          - Controller main switch turned to the off or manual position.

          - Supervised power on.

If retaining second option in first subparagraph below, insert list of required alarms.

          - [Common] [Separate] trouble on the controller or engine.

            - <Insert alarm>.

          - Common pump room trouble.

Retain first subparagraph below if power is supplied from multiple sources.

          - Controller connected to alternate power source.

          - <Insert indication>.

        - Audible alarm, with silence push button.

Retain paragraph below if applicable; this is an optional feature at added cost.

        - Pump REMOTE START push button.

      - LOW-SUCTION-SHUTDOWN PANELS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Although prohibited by NFPA 20, some local laws or authorities having jurisdiction mandate use of low-suction-shutdown panels to inhibit starting and to activate shutdown of automatically controlled fire pumps on low-suction pressure in the municipal water supplies. Consult authorities having jurisdiction for specifics and retain this article only if required by local mandates. Some manufacturers listed in fire-pump-controller articles incorporate this feature into their microprocessor-based controllers as an alternative.

Not all features, accessories, and options in this article are available from every listed manufacturer. Verify availability and unique characteristics with manufacturers. See "Low-Suction-Shutdown Panels" Article in the Evaluations for additional guidance.

        - General Requirements for Low-Suction-Shutdown Panels:

          - Factory assembled, wired, and tested.

          - Prevents automatic start of fire pump, and shuts down automatically started fire pump, on low-suction pressure.

          - [Automatic] [Manual] reset.

        - Operation: [External contact input] [Integral pressure switch] <Insert operation>.

Retain first and last options in first paragraph below if a separate and redundant normal power source is provided to the controller. Not all listed manufacturers offer dual voltage sources.

        - Supervisory[ and Normal] Control Voltage: [120 V(ac)] [240 V(ac)] <Insert voltage>; [single] [dual] source.

Standard and optional features vary considerably among manufacturers of low-suction-shutdown panels. Verify availability and unique characteristics with manufacturer; include in paragraph below or show on Drawings those features that apply to each controller.

        - Include audible and visual alarms and status indications, with silence push button, for the following conditions:

          - Control power available.

          - Low-suction pressure.

          - Normal-suction pressure.

          - <Insert optional features>.

      - ENCLOSURES

        - Fire-Pump Controllers, ATS, Remote Alarm Panels, and Low-Suction-Shutdown Panels: NEMA 250, to comply with environmental conditions at installed locations and NFPA 20.

See "Enclosures" Article in the Evaluations for discussion of enclosure types. Coordinate subparagraphs below with Drawings by identifying the designated areas on plans or by including the required enclosure types. Enclosure materials and finishes may be added to the Section Text. NFPA 20 requires NEMA 250, Type 2 as the minimum allowable enclosure type for indoor controllers and ATS; NEMA 250, Type 1 is allowed for alarm panels. Consult manufacturers for availability of, and limitations on, other than NEMA 250, Type 2 enclosures.

Retain "Indoor, Dry and Clean Locations" Subparagraph below only if retaining remote alarm panels.

          - Indoor, Dry and Clean Locations: [Type 1 (IEC IP10)] <Insert type>.

          - Indoor Locations Subject to Dripping Noncorrosive Liquids: [Type 2 (IEC IP11)] <Insert type>.

          - Outdoor Locations: [Type 3R (IEC IP14)] [Type 4 (IEC IP56)] [Type 4X (IEC IP56)] <Insert type>.

          - Other Wet or Damp, Indoor Locations: [Type 4 (IEC IP56)] [Type 4X (IEC IP56)] <Insert type>.

          - Indoor Locations Subject to Dust, Falling Dirt, and Dripping Noncorrosive Liquids: Type 12 (IEC IP12).

        - Enclosure Color: [Manufacturer's standard "fire-pump-controller red"] <Insert color>.

        - Nameplates: Comply with NFPA 20; complete with capacity, characteristics, approvals, listings, and other pertinent data.

        - Optional Features:

Optional features in subparagraphs below pertain mainly to enclosures for fire-pump controllers; they are also limited in application by controller, enclosure type, and manufacturer. Retain applicable optional features and indicate requirements for and quantities of accessories on Drawings. Consult manufacturers for availability and limitations.

          - Floor stands, 12 inch (305 mm) high, for floor-mounted controllers.

          - Space heater, [120 V(ac)] [240 V(ac)] [, with humidistat] [, with thermostat].

          - Tropicalization.

          - <Insert optional feature>.

      - SOURCE QUALITY CONTROL

NFPA 20 requires that "all controllers must be completely assembled, wired, and tested by the manufacturer before shipment from the factory." Retain "Testing" Paragraph below for requesting copies of the test reports.

        - Testing: Test and inspect fire-pump controllers in accordance with requirements in NFPA 20 and [UL 218] <Insert standard>.

          - Verification of Performance: Rate controllers in accordance with operation of functions and features specified.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Fire-pump controllers will be considered defective if they do not pass tests and inspections.

        - Prepare test and inspection reports.

- EXECUTION

      - EXAMINATION

        - Examine areas and surfaces to receive equipment, with Installer present, for compliance with requirements and other conditions affecting performance.

        - Examine equipment before installation. Reject equipment that is wet or damaged by moisture or mold.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION OF CONTROLLERS

        - Coordinate installation of controllers with other construction including conduit, piping, fire-pump equipment, and adjacent surfaces. Maintain required clearances for workspace and equipment access doors and panels. Ensure that controllers are within sight of fire-pump drivers.

Retain first paragraph below if required for base-supported controllers.

        - Coordinate sizes and locations of concrete bases with actual equipment provided.

NFPA 20 and NFPA 70 define specific installation requirements for fire-pump controllers. See "General Installation Requirements for Fire-Pump Controllers" Article in the Evaluations for additional information.

        - Install controllers within sight of their respective drivers.

Retain first paragraph below for controllers actuated by water flow in fire-suppression piping.

        - Connect controllers to their dedicated pressure-sensing lines.

Limited-service controllers and small-to-medium-sized, full-service controllers are readily suited for wall mounting. Retain "Wall-Mounting Controllers" Paragraph below for equipment supported by walls or freestanding racks.

        - Wall-Mounting Controllers: Install controllers on walls with disconnect operating handles not higher than 79 inch (2 m) above finished floor, and bottom of enclosure not less than 12 inch (305 mm) above finished floor unless otherwise indicated. Bolt units to wall or mount on lightweight structural-steel channels bolted to wall. For controllers not on walls, provide freestanding racks complying with Section 260529 "Hangers and Supports for Electrical Systems."

Full- and limited-service controllers are available with standard or optional floor stands. Retain "Floor-Mounting Controllers" Paragraph below for controllers supported on slabs-on-grade.

        - Floor-Mounting Controllers: Install controllers on concrete base(s), using floor stands high enough so that the bottom of enclosure cabinet is not less than 12 inches (305 mm) above finished floor. Comply with requirements for concrete bases specified in Section 260529 "Hangers and Supports for Electrical Systems."

          - For supported equipment, install epoxy-coated anchor bolts that extend through concrete base, and anchor into structural concrete floor.

          - Place and secure anchorage devices. Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

          - Install anchor bolts to elevations required for proper attachment to supported equipment.

Retain "Seismic Bracing" Paragraph below if seismic controls are Project requirement. Coordinate with Drawings.

        - Seismic Bracing: Comply with requirements specified in Section 260548.16 "Seismic Controls for Electrical Systems."

        - Temporary Lifting Provisions: Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from enclosures and components.

Retain paragraph below if retaining full- or limited-service, electric-drive controllers in Part 2.

        - Comply with NEMA ICS 15.

      - INSTALLATION OF STANDALONE ATS

Small-to-medium-sized ATS are readily suited for wall mounting. Retain "Wall-Mounting ATS" Paragraph below for equipment supported by walls or freestanding racks.

        - Wall-Mounting ATS: Install ATS on walls with disconnect operating handles not higher than 79 inch (2 m) above finished floor, and bottom of enclosure not less than 12 inch (305 mm) above finished floor unless otherwise indicated. Bolt units to wall or mount on lightweight structural-steel channels bolted to wall. For ATS not on walls, provide freestanding racks complying with Section 260529 "Hangers and Supports for Electrical Systems."

ATS are available with standard or optional floor stands. Retain "Floor-Mounting ATS" Paragraph below for ATS supported on slabs-on-grade.

        - Floor-Mounting ATS: Install ATS on concrete bases, using floor stands high enough so that the bottom of enclosure cabinet is not less than 12 inch (305 mm) above finished floor. Comply with requirements for concrete bases specified in Section 260529 "Hangers and Supports for Electrical Systems."

          - For supported equipment, install epoxy-coated anchor bolts that extend through concrete base, and anchor into structural concrete floor.

          - Place and secure anchorage devices. Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

          - Install anchor bolts to elevations required for proper attachment to supported equipment.

Retain "Seismic Bracing" Paragraph below if seismic controls are Project requirement. Coordinate with Drawings.

        - Seismic Bracing: Comply with requirements specified in Section 260548.16 "Seismic Controls for Electrical Systems."

        - Temporary Lifting Provisions: Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from enclosures and components.

      - INSTALLATION OF REMOTE ALARM AND LOW-SUCTION-SHUTDOWN PANELS

Retain this article if retaining "Remote Alarm Panels" or "Low-Suction-Shutdown Panels" Article.

        - Install panels on walls with tops not higher than [72 inch (1829 mm)] <Insert height> above finished floor unless otherwise indicated. Bolt units to wall or mount on lightweight structural-steel channels bolted to wall. For ATS not on walls, provide freestanding racks complying with Section 260529 "Hangers and Supports for Electrical Systems."

      - INSTALLATION OF POWER WIRING

Retain this article if retaining electric-drive controllers. NFPA 20 and NFPA 70 have specific requirements and restrictions on wiring for electric-drive controllers; review these standards before revising this article. See "General Installation Requirements for Fire-Pump Controllers" Article in the Evaluations for restrictions on other wiring systems routed through controllers.

        - Install power wiring between controllers and their services or sources, and between controllers and their drivers. Comply with requirements in NFPA 20, NFPA 70, and Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

      - INSTALLATION OF CONTROL AND ALARM WIRING

Retain this article if remote control or remote status indication is required. NFPA 20 and NFPA 70 have specific requirements and restrictions on control and alarm wiring for all fire-pump controllers and associated remote panels; review these standards before revising this article. See "General Installation Requirements for Fire-Pump Controllers" Article in the Evaluations for restrictions on other wiring systems routed through controllers.

        - Install wiring between controllers and remote devices[ and facility's central monitoring system]. Comply with requirements in NFPA 20, NFPA 70, and Section 260523 "Control-Voltage Electrical Power Cables."

Retain first paragraph below if remote alarm panels or low-suction-shutdown panels are required.

        - Install wiring between remote alarm[ and low-suction-shutdown] panels and controllers. Comply with requirements in NFPA 20, NFPA 70, and Section 260523 "Control-Voltage Electrical Power Cables."

        - Install wiring between controllers and the building's fire-alarm system. Comply with requirements specified in Section 284621.11 "Addressable Fire-Alarm Systems."

        - Bundle, train, and support wiring in enclosures.

        - Connect remote manual and automatic activation devices where applicable.

      - IDENTIFICATION

        - Comply with requirements in NFPA 20 for marking fire-pump controllers.

        - Identify system components, wiring, cabling, and terminals. Comply with requirements for identification in NFPA 20 and as specified in Section 260553 "Identification for Electrical Systems."

      - FIELD QUALITY CONTROL

Field acceptance tests are part of the formal process to verify compliance with NFPA 20; therefore, all pre-acceptance testing preparation should be complete before scheduling the tests for witnessing by authorities having jurisdiction.

        - Acceptance Testing Preparation:

          - Inspect and Test Each Component:

            - Inspect wiring, components, connections, and equipment installations. Test and adjust components and equipment.

            - Test insulation resistance for each element, component, connecting supply, feeder, and control circuits.

            - Test continuity of each circuit.

Retain first subparagraph below if retaining full- or limited-service, electric-drive controllers in Part 2.

          - Verify and Test Each Electric-Drive Controller:

            - Verify that voltages at controller locations are within plus 10 or minus 1 percent of motor nameplate rated voltages, with motors off. If outside this range for motor, notify [Architect] [Construction Manager] [Owner] before starting the motor(s).

            - Test each motor for proper phase rotation.

          - Operational Test: After electrical circuitry has been energized, start units to confirm proper unit operation.

          - Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

NFPA 20 requires manufacturers of fire-pump controllers and ATS to be present during field acceptance testing regardless of who does the testing.

        - Representatives from manufacturers of fire-pump controllers and ATS must be present during acceptance tests and inspections in accordance with NFPA 20.

Retain first paragraph below to require that field quality-control tests be witnessed. Local ordinance or custom may require that authorities having jurisdiction witness the testing.

        - Acceptance tests and inspections must be witnessed by [Architect] [Tenant] [authorities having jurisdiction] <Insert names or titles of witnesses>.

Coordinate "Acceptance Tests and Inspections" Paragraph below with "Qualifications" and "Field Quality Control" articles in Section 260010 "Supplemental Requirements for Electrical."

        - Acceptance Tests and Inspections:

          - Do not begin field acceptance testing until suction piping has been flushed and hydrostatically tested and the certificate for flushing and testing has been submitted to [Architect] [Construction Manager] [Owner] and authorities having jurisdiction.

          - Prior to starting, notify authorities having jurisdiction of the time and place of the acceptance testing.

          - Engage manufacturer's factory-authorized service representative to be present during the testing.

          - Perform field acceptance tests as outlined in NFPA 20.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Nonconforming Work:

          - Controllers will be considered defective if they do not pass tests and inspections.

          - Remove and replace defective units and retest.

        - Prepare test and inspection reports.

      - STARTUP SERVICE

        - [Engage a factory-authorized service representative to perform] [Perform] startup service.

          - Complete installation and startup checks in accordance with manufacturer's written instructions.

          - <Insert startup steps if any>.

      - ADJUSTING

Retain applicable paragraphs in this article. Coordinate with selections made in Part 2.

        - Adjust controllers[ and battery charger systems] to function smoothly and as recommended by manufacturer.

        - Set field-adjustable switches, auxiliary relays, time-delay relays, and timers.

        - Program microprocessors for required operational sequences, status indications, alarms, event recording, and display features. Clear events memory after final acceptance testing and prior to Substantial Completion.

        - Set field-adjustable pressure switches.

      - PROTECTION

Retain this article if retaining "Delivery, Storage, and Handling" Article and if retaining space heaters in "Enclosures" Article.

        - Temporary Heating: Apply temporary heat to maintain temperature in accordance with manufacturer's written instructions until enclosed controllers are ready to be energized and placed into service.

        - Replace controllers whose interiors have been exposed to water or other liquids prior to Substantial Completion.

END OF SECTION 262933