Copyright 2022 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 264313 - SURGE PROTECTIVE DEVICES FOR LOW-VOLTAGE ELECTRICAL POWER CIRCUITS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Access Manufacturer-Provided, AIA MasterSpec-Based Sections:

<Double click here for this Section based on specific manufacturer’s products set as Basis-of-Design at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Type 1 surge protective devices (SPDs).

          - Type 2 surge protective devices (SPDs).

          - Type 3, Type 4, and Type 5 surge protective devices (SPDs).

          - Enclosures.

          - Conductors and cables.

        - Related Requirements:

Always retain first two subparagraphs below.

          - Section 260010 "Supplemental Requirements for Electrical" for additional abbreviations, definitions, submittals, qualifications, testing agencies, and other Project requirements applicable to Work specified in this Section.

          - Section 260011 "Facility Performance Requirements for Electrical" for seismic-load, wind-load, acoustical, and other field conditions applicable to Work specified in this Section.

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 262413 "Switchboards" for integral SPDs installed by switchboard manufacturer.

          - Section 262416 "Panelboards" for integral SPDs installed by panelboard manufacturer.

          - Section 262726 "Wiring Devices" for integral SPDs installed by receptacle manufacturer.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project. See the Evaluations, particularly the "UL 1449 Requirements" Article, for expanded details of definitions below.

        - In: Nominal discharge current.

        - Maximum Continuous Operating Voltage (MCOV): The maximum designated RMS value of the power frequency voltage that may be continuously applied to the mode of protection of an SPD.

        - Metal-Oxide Varistor (MOV): An electronic component with a significant bidirectional, nonlinear current-voltage characteristic.

        - Mode(s), Modes of Protection, or Protection Modes: Electrical paths where the SPD offers defense against transient overvoltages. Examples include: line to neutral (L-N), line to ground (L-G), line to line (L-L), and neutral to ground (N-G).

        - SCCR: Short-circuit current rating.

        - Type 1 SPDs: Permanently connected SPDs intended for installation between the secondary of the service transformer and the line side of the service disconnect overcurrent device.

        - Type 2 SPDs: Permanently connected SPDs intended for installation on the load side of the service disconnect overcurrent device, including SPDs located at the branch panel.

        - Type 3 SPDs: Point of utilization SPDs.

        - Type 4 SPDs: Component SPDs, including discrete components, as well as assemblies.

        - Type 5 SPDs: Discrete component surge suppressors, such as MOVs that may be mounted on a printed wiring board, connected by its leads or provided within an enclosure with mounting means and wiring terminations.

        - Voltage Protection Rating (VPR): A rating selected from UL 1449 list of preferred values assigned to each mode of protection.

      - ACTION SUBMITTALS

        - Product Data:

          - For each type of product.

            - Include electrical characteristics, specialties, and accessories for SPDs.

See "UL 1449 Requirements" Article in the Evaluations for explanation of terms used in subparagraph below.

            - Certification of compliance with UL 1449 by qualified electrical testing laboratory recognized by authorities having jurisdiction including the following information:

              - Tested values for VPRs.

              - In ratings.

              - MCOV, type designations.

              - OCPD requirements.

              - Manufacturer's model number.

              - System voltage.

              - Modes of protection.

        - Field quality-control reports.

      - INFORMATIONAL SUBMITTALS

        - Sample Warranty: For manufacturer's special warranty.

      - WARRANTY

When warranties are required and available, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner, after one-year correction period specified in the Contract, under the Contractor's general warranty and prevailing local laws.

Verify duration of extended warranty periods needed.

        - Special Manufacturer Extended Warranty: Manufacturer warrants that SPDs perform in accordance with specified requirements and agrees to provide repair or replacement of SPDs that fail to perform as specified within extended warranty period.

          - Initial Extended Warranty Period: [Five] <Insert number> year(s) from date of Substantial Completion, for labor, materials, and equipment.

          - Follow-On Extended Warranty Period: [10] <Insert number> year(s) from date of Substantial Completion, for materials only, f.o.b. the nearest shipping point to Project site.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - TYPE 1 SURGE PROTECTIVE DEVICES (SPDs)

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain devices from single source from single manufacturer.

See "SPD Types" Article in the Evaluations for discussion of applying Type 1 and Type 2 devices at service entrance locations.

        - General Characteristics:

          - Reference Standards: UL 1449, Type 1.

See "Surge Protection Fundamentals" Article in the Evaluations for discussion of nominal system voltage.

          - MCOV: Not less than 125 percent of nominal system voltage for 208Y/120 V and 120/240 V power systems, and not less than 115 percent of nominal system voltage for 480Y/277 V power systems.

See "UL 1449 Requirements" Article in the Evaluations for guidance before retaining one of four options in "Peak Surge Current Rating" Subparagraph below.

          - Peak Surge Current Rating: Minimum single-pulse surge current withstand rating per phase must not be less than [160] [200] [240] [320] <Insert value> kA. Peak surge current rating must be arithmetic sum of the ratings of individual MOVs in a given mode.

Retain one of first two subparagraphs below. Verify compatibility of peak surge current rating and VPR.

          - Protection modes and UL 1449 VPR for grounded wye circuits with [480Y/277 V] [208Y/120 V], three-phase, four-wire circuits must not exceed the following:

            - Line to Neutral: [1200 V for 480Y/277 V] [700 V for 208Y/120 V].

            - Line to Line: [2000 V for 480Y/277 V] [1200 V for 208Y/120 V].

          - Protection modes and UL 1449 VPR for 240/120 V, single-phase, three-wire circuits must not exceed the following:

            - Line to Neutral: 700 V.

            - Line to Line: 1200 V.

See "UL 1449 Requirements" Article in the Evaluations for discussion on SCCR selection in "SCCR" Subparagraph below.

          - SCCR: Not less than [100] [200] <Insert value> kA.

See "UL 1449 Requirements" Article in the Evaluations for discussion on In selection in "In Rating" Subparagraph below.

          - In Rating: 20 kA.

        - Options:

Retain first subparagraph below when specifying Type 1 SPD to be installed ahead of the service disconnect, when this disconnect is installed to facilitate maintenance.

          - Include integral disconnect switch.

Retain first subparagraph below to disconnect the SPD when low-current, high-impedance faults occur.

          - Include internal thermal protection that disconnects the SPD before damaging internal suppressor components.

          - Include indicator light display for protection status.

          - Include audible alarm.

Insert other contact forms and ratings when required by building power monitoring and control system. See "SPD Options" Article in the Evaluations for additional guidance.

          - Include NEMA ICS 5, dry Form C contacts rated at [2 A and 24 V(ac)] <Insert values> for remote monitoring of protection status.

          - Include surge counter.

      - TYPE 2 SURGE PROTECTIVE DEVICES (SPDs)

Retain this article for SPDs other than those installed before the service entrance OCPD. SPDs described in this article are required by NFPA 70 to be installed with OCPD and means of disconnect. The type and size of OCPD depends on the UL listing requirements. See "SPD Types" Article in the Evaluations.

See "SPD Types" Article in the Evaluations for discussion of applying Type 2 devices at load side of service entrance OCPD.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Source Limitations: Obtain devices from single source from single manufacturer.

See "SPD Types" Article in the Evaluations for discussion of applying Type 2 devices at service entrance requiring an OCPD.

        - General Characteristics:

Retain Type 2 SPDs option to be co-listed as electromagnetic interference and radio-frequency interference filters. See the Evaluations for explanation of combining SPD and power-line noise filters.

          - Reference Standards: UL 1449, Type 2[; UL 1283].

See "Surge Protection Fundamentals" Article in the Evaluations for discussion of nominal system voltage.

          - MCOV: Not less than 125 percent of nominal system voltage for 208Y/120 V and 120/240 V power systems, and not less than 115 percent of nominal system voltage for 480Y/277 V power systems.

See "UL 1449 Requirements" Article in the Evaluations for guidance before retaining one of two options in "Peak Surge Current Rating" Subparagraph below. Generally, available surge current ratings are 480, 300, 250, 200, 150, and 100 kA; exact values vary among manufacturers.

          - Peak Surge Current Rating: Minimum single-pulse surge current withstand rating per phase must not be less than [100] [150] <Insert value> kA. Peak surge current rating must be arithmetic sum of the ratings of individual MOVs in a given mode.

Retain one of first two subparagraphs below. Verify compatibility of peak surge current rating and clamping voltage.

          - Protection modes and UL 1449 VPR for grounded wye circuits with [480Y/277 V] [208Y/120 V], three-phase, four-wire circuits must not exceed the following:

            - Line to Neutral: [1200 V for 480Y/277 V] [700 V for 208Y/120 V].

            - Line to Ground: [1200 V for 480Y/277 V] [700 V for 208Y/120 V].

            - Neutral to Ground: [1200 V for 480Y/277 V] [700 V for 208Y/120 V].

            - Line to Line: [2000 V for 480Y/277 V] [1200 V for 208Y/120 V].

          - Protection modes and UL 1449 VPR for 240/120 V, single-phase, three-wire circuits must not exceed the following:

            - Line to Neutral: 700 V.

            - Line to Ground: 700 V.

            - Neutral to Ground: 700 V.

            - Line to Line: 1200 V.

See "UL 1449 Requirements" Article in the Evaluations for discussion on SCCR selection in "SCCR" Subparagraph below.

          - SCCR: Equal or exceed [100] [200] <Insert value> kA.

See "UL 1449 Requirements" Article in the Evaluations for discussion on In selection in "In Rating" Subparagraph below.

          - In Rating: [20] [10] kA.

        - Options:

          - Include LED indicator lights for power and protection status.

Retain first subparagraph below to disconnect the SPD when low-current, high-impedance faults occur.

          - Include internal thermal protection that disconnects the SPD before damaging internal suppressor components.

          - Include NEMA ICS 5, dry Form C contacts rated at [2 A and 24 V(ac)] <Insert values> for remote monitoring of protection status.

          - Include surge counter.

      - TYPE 3, TYPE 4, AND TYPE 5 SURGE PROTECTIVE DEVICES (SPDs)

        - Type 3, Type 4, and Type 5 SPDs are not approved for field installation.[ See "Related Requirements" Paragraph in "Summary" Article for products with manufacturer-installed Type 3, Type 4, and Type 5 SPDs.]

      - ENCLOSURES

        - Indoor Enclosures: Type 1.

        - Outdoor Enclosures: [Type 3R] [Type 4X].

      - CONDUCTORS AND CABLES

Retain this article when SPD listing and specific manufacturer's instruction permit lead adjustment in the field. Control cable specifications are not included in this Section because accessories include only dry contacts for remote status indication.

        - Power Wiring: Same size as SPD leads, complying with Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

- EXECUTION

      - INSTALLATION

        - Provide OCPD and disconnect for installation of SPD in accordance with UL 1449 and manufacturer's instructions.

        - Install leads between disconnects and SPDs short, straight, twisted, and in accordance with manufacturer's instructions. Comply with wiring methods in Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

          - Do not splice and extend SPD leads unless specifically permitted by manufacturer.

          - Do not exceed manufacturer's recommended lead length.

          - Do not bond neutral and ground.

        - Use crimped connectors and splices only. Wire nuts are unacceptable.

      - FIELD QUALITY CONTROL

Retain first paragraph below to require that field quality-control tests be witnessed. Local ordinance or custom may require that authorities having jurisdiction witness the testing.

        - Field tests and inspections must be witnessed by [Architect] [Tenant] [authorities having jurisdiction] <Insert names or titles of witnesses>.

Coordinate "Tests and Inspections" Paragraph below with "Qualifications" and "Field Quality Control" articles in Section 260010 "Supplemental Requirements for Electrical."

        - Tests and Inspections:

          - Compare equipment nameplate data for compliance with Drawings and the Specifications.

          - Inspect anchorage, alignment, grounding, and clearances.

          - Verify that electrical wiring installation complies with manufacturer's installation requirements.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Nonconforming Work:

          - SPDs that do not pass tests and inspections will be considered defective.

          - Remove and replace defective units and retest.

        - Prepare test and inspection reports.

Retain "Manufacturer Services" Paragraph below if manufacturer's representative is required to support or supervise the administrant specified in Section 260010 "Supplemental Requirements for Electrical" for field tests and inspections performed by Installer or third party agencies.

        - Manufacturer Services:

Retain supervise option in subparagraph below when third-party tests and inspections must be witnessed and approved by factory-authorized service representative to satisfy special extended warranty requirements. In some cases, Installer may be factory-authorized under warranty provisions to fulfill this role.

          - Engage factory-authorized service representative to [support] [supervise] field tests and inspections.

      - STARTUP SERVICE

        - Complete startup checks in accordance with manufacturer's instructions.

        - Do not perform insulation-resistance tests of the distribution wiring equipment with SPDs installed. Disconnect SPDs before conducting insulation-resistance tests; reconnect them immediately after the testing is over.

        - Energize SPDs after power system has been energized, stabilized, and tested.

END OF SECTION 264313