Copyright 2022 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 265617 - FLUORESCENT EXTERIOR LIGHTING

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED 2009, LEED v4, LEED v4.1, IgCC, and Green Globes. Sustainable design requirements may be inserted in the Section Text using the hypertext links.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Fluorescent lamps.

          - Ballasts for fluorescent lamps.

          - Luminaire types.

          - Materials.

          - Finishes.

          - Luminaire support components.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 260923 "Lighting Control Devices" for automatic control of lighting, including time switches, photoelectric relays, occupancy sensors, and multipole lighting relays and contactors.

          - Section 260926 "Lighting Control Panelboards" for panelboard-based lighting control.

          - Section 260936 "Modular Dimming Controls" for architectural dimming systems and fluorescent dimming controls with dimming ballasts specified in Section 265100 "Interior Lighting."

          - Section 260943.16 "Addressable-Luminaire Lighting Controls" and Section 260943.23 "Relay-Based Lighting Controls" for manual or programmable control systems with low-voltage control wiring or data communication circuits.

          - Section 265613 "Lighting Poles and Standards" for poles and standards used to support lighting equipment.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

        - CCT: Correlated color temperature.

        - CRI: Color rendering index.

        - Fixture: See "Luminaire."

        - Luminaire: Complete lighting unit, including lamp, reflector, and housing.

      - ACTION SUBMITTALS

        - Product Data: For each type of luminaire.

Optional requirements in subparagraphs below expand "product data" submittal requirements for when more specific information is needed. Do not require submittal of manufacturer's specifications, material safety data sheets, installation instructions, and similar items that may conflict with specification requirements or needlessly involve Architect in Contractor's means and methods of construction.

          - Arrange in order of luminaire designation.

          - Include data on features, accessories, and finishes.

          - Include physical description and dimensions of the luminaires.

          - Ballast, including BF.

          - Lamps, including life, output (lumens, CCT, and CRI), and energy-efficiency data.

          - Photometric data and adjustment factors based on laboratory tests, complying with IES "Lighting Measurements Testing and Calculation Guides," of each luminaire type. The adjustment factors shall be for lamps, ballasts, and accessories identical to those indicated for the luminaire as applied in this Project.

Retain "Manufacturers' Certified Data" or "Testing Agency Certified Data" Subparagraph below, or both, to specify qualifications for laboratories providing photometric data. Retain first subparagraph for testing laboratories that are associated with a luminaire manufacturer's production facility. Retain second subparagraph for testing laboratories that are independent of a luminaire manufacturer's production facility.

            - Manufacturers' Certified Data: Photometric data certified by manufacturer's laboratory with a current accreditation under the NVLAP for Energy Efficient Lighting Products.

            - Testing Agency Certified Data: For indicated luminaires, photometric data certified by a qualified independent testing agency. Photometric data for remaining luminaires shall be certified by manufacturer.

          - Photoelectric relays.

          - Means of attaching luminaires to supports and indication that the attachment is suitable for components involved.

        - Sustainable Design Submittals:

          - <Double click to insert sustainable design text for BUG Rating.>

          - <Double click to insert sustainable design text for luminaire calculation requirements.>

          - <Double click to insert sustainable design text for lighting submittals.>

          - <Double click to insert sustainable design text for mercury content.>

        - Shop Drawings: For nonstandard or custom luminaires.

          - Include plans, elevations, sections, and mounting and attachment details.

          - Include details of luminaire assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

          - Include diagrams for power, signal, and control wiring.

Retain "Samples" Paragraph below for single-stage Samples, with a subordinate list if applicable. Retain "Samples for Initial Selection" and "Samples for Verification" paragraphs for two-stage Samples.

        - Samples: For each luminaire and for each color and texture specified with factory-applied finish.

        - Samples for Initial Selection: For each type of luminaire with custom, factory-applied finish.

          - Include Samples of luminaires and accessories involving color and finish selection.

        - Samples for Verification: For each type of luminaire.

          - Include Samples of luminaires and accessories to verify finish selection.

          - Lamps and ballasts, installed.

          - Cords and plugs.

          - Support system.

        - Product Schedule: For luminaires and lamps.[ Use same designations indicated on Drawings.]

Retain "Delegated Design Submittals" Paragraph below if design services, such as luminaire support, have been delegated to Contractor or manufacturer.

        - Delegated Design Submittals: For luminaire supports.

          - Include design calculations for luminaire supports[ and seismic restraints] [ and for designing vibration isolation bases].

      - INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Coordinate paragraph with other Sections specifying products listed below. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

        - Coordination Drawings: Plans, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

          - Luminaires.

          - Structural members to which [equipment] [and] luminaires will be attached.

          - Underground utilities and structures.

          - Existing underground utilities and structures.

          - Above-grade utilities and structures.

          - Existing above-grade utilities and structures.

          - Building features.

          - Vertical and horizontal information.

          - <Insert feature>.

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Data: For testing laboratory providing photometric data for luminaires.

Retain "Seismic Qualification Data" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems." See ASCE/SEI 7 for certification requirements for equipment and components.

        - Seismic Qualification Data: For luminaires, accessories, and components, from manufacturer.

          - Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

          - Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

          - Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain "Product Certificates" Paragraph below to require submittal of product certificates from manufacturers.

        - Product Certificates: For each type of the following:

          - Ballast for bi-level and dimmable luminaires.

          - Lamp.

          - Photoelectric relay.

        - Product Test Reports: For each luminaire, for tests performed by [manufacturer and witnessed by a qualified testing agency] [a qualified testing agency].

        - Sample warranty.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For luminaires [and photoelectric relay ]to include in operation and maintenance manuals.

      - MAINTENANCE MATERIAL SUBMITTALS

        - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Lamps: [Ten for every 100] <Insert quantity> of each type and rating installed. Furnish at least one of each type.

          - Glass, Acrylic, and Plastic Lenses, Covers, and Other Optical Parts: [One for every 100] <Insert quantity> of each type and rating installed. Furnish at least one of each type.

          - Diffusers and Lenses: [One for every 100] <Insert quantity>of each type and rating installed. Furnish at least one of each type.

          - Globes and Guards: [One for every 20] <Insert quantity>of each type and rating installed. Furnish at least one of each type.

          - Ballasts: [One for every 100] <Insert quantity> of each type and rating installed. Furnish at least one of each type.

      - QUALITY ASSURANCE

        - Luminaire Photometric Data Testing Laboratory Qualifications:

Retain one of two subparagraphs below to specify qualifications for laboratories providing photometric data to be submitted for luminaires. Retain first subparagraph for testing laboratories that are associated with a luminaire manufacturer's production facility. Retain second subparagraph for testing laboratories that are independent of a luminaire manufacturer's production facility.

          - Luminaire manufacturers' laboratory accredited under the NVLAP for Energy Efficient Lighting Products.

          - Provided by an independent agency, with the experience and capability to conduct the testing indicated, that is an NRTL as defined by OSHA in 29 CFR 1910.7, accredited under the NVLAP for Energy Efficient Lighting Products and complying with applicable IES testing standards.

        - Installer Qualifications: An authorized representative who is trained and approved by manufacturer.

        - Mockups: For exterior luminaires, complete with power and control connections.

          - Obtain Architect's approval of luminaires in mockups before starting installations.

          - Maintain mockups during construction in an undisturbed condition as a standard for judging the completed Work.

          - Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing.

Retain subparagraph below if the intention is to make an exception to the default requirement in Section 014000 "Quality Requirements" for demolishing and removing mockups.

          - Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

      - DELIVERY, STORAGE, AND HANDLING

        - Protect finishes of exposed surfaces by applying a strippable, temporary protective covering prior to shipping.

      - FIELD CONDITIONS

        - Verify existing and proposed utility structures prior to the start of work associated with luminaire installation.

        - Mark locations of exterior luminaires for approval by Architect prior to the start of luminaire installation.

      - WARRANTY

When warranties longer than one year are required and would exceed the "one-year period for correction of Work," verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

        - Warranty: Manufacturer and Installer agree to repair or replace components of luminaires that fail in materials or workmanship within specified warranty period.

          - Failures include, but are not limited to, the following:

            - Structural failures, including luminaire support components.

            - Faulty operation of luminaires, ballasts, and accessories.

            - Deterioration of metals, metal finishes, and other materials beyond normal weathering.

            - <Insert failure modes>.

Verify available warranties and warranty periods.

          - Warranty Period: [Two] <Insert number> year(s) from date of Substantial Completion.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Terminology used to describe products complies with NEMA LE 6 product classifications. These classifications were current at the time this Specification was updated, but may not be inclusive of products required for the Project. For additional products, add new articles, describe characteristics not already included in the Specification, and choose the appropriate manufacturer listing.

      - PERFORMANCE REQUIREMENTS

        - Seismic Performance:

Retain one of first two subparagraphs below with "Seismic Qualification Data" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Delete both subparagraphs if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

          - Luminaires shall withstand the effects of earthquake motions determined in accordance with [ASCE/SEI 7] <Insert requirement>.

          - Luminaires and lamps shall be labeled vibration and shock resistant.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

          - The term "withstand" means "the luminaire will remain in place without separation of any parts when subjected to the seismic forces specified[ and the luminaire will be fully operational during and after the seismic event]."

      - LUMINAIRE REQUIREMENTS

Product characteristics in this article apply to all luminaires in the Project.

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

        - NRTL Compliance: Luminaires shall comply with UL 1598 and be listed and labeled for indicated class and division of hazard by an NRTL.

Coordinate "FM Global Compliance" Paragraph below with Drawings.

        - FM Global Compliance: Luminaires for hazardous locations shall be listed and labeled for indicated class and division of hazard by FM Global.

        - UL Compliance: Comply with UL 1598. [Luminaire assembly consists of UL-recognized components] [Luminaire assembly listed for wet location].

        - Lamp base complying with [ANSI C81.61] [or] [IEC 60061-1].

        - Nominal Operating Voltage: [120 V ac] [240 V ac] [277 V ac] [480 V ac].

Retain "EMI Filters" Paragraph below for special applications where freedom from conducted EMI is critical. Coordinate with the Exterior Luminaire Schedule on Drawings.

        - EMI Filters: Factory installed to suppress conducted EMI as required by MIL-STD-461E. Fabricate luminaires with one filter on each ballast that is indicated to require a filter.

Retain "In-line Fusing" Paragraph below when an integral fuse is not included with the specified ballast. Coordinate with the Exterior Luminaire Schedule on Drawings.

        - In-line Fusing: [On the ballast primary for each luminaire] [Separate in-line fuse for each luminaire].

        - Lamp Rating: Lamp marked for [outdoor use] [and] [in enclosed locations].

        - Source Limitations:

Retain one of two subparagraphs below.

          - Obtain luminaires from single source from a single manufacturer.

          - For luminaires, obtain each color, grade, finish, type, and variety of luminaire from single source with resources to provide products of consistent quality in appearance and physical properties.

      - FLUORESCENT LAMPS

Coordinate this article with Drawings. Where color rendition or color uniformity is important and several types of fluorescent lamps are used, provide consistent manufacturer designations or ANSI lamp designations to define requirements.

Paragraphs below are sample specifications for typical lamps, which are a few of the thousands of types and ratings available for building illumination. Indicate here or in the Exterior Luminaire Schedule the standard designations of the lamps that comply with lumen output, energy rating, CRI, color temperature, lamp life, and other requirements for specific Project applications.

        - T8 rapid-start lamps, rated 32-W maximum, nominal length of 48 inches (1220 mm), 2800 initial lumens (minimum), CRI of 75 (minimum), color temperature of [3500] <Insert value> K, and average rated life of 20,000 hours unless otherwise indicated.

        - T8 rapid-start lamps, rated 17-W maximum, nominal length of 24 inches (610 mm), 1300 initial lumens (minimum), CRI of 75 (minimum), color temperature of [3500] <Insert value> K, and average rated life of 20,000 hours unless otherwise indicated.

        - T5 rapid-start lamps, rated 28-W maximum, nominal length of 45.2 inches (1150 mm), 2900 initial lumens (minimum), CRI of 85 (minimum), color temperature of [3000] <Insert value> K, and average rated life of 20,000 hours unless otherwise indicated.

        - T5HO rapid-start, high-output lamps, rated 54-W maximum, nominal length of 45.2 inches (1150 mm), 5000 initial lumens (minimum), CRI of 85 (minimum), color temperature of [4100] <Insert value> K, and average rated life of 20,000 hours unless otherwise indicated.

        - Compact Fluorescent Lamps: Four-pin, CRI of 80 (minimum), color temperature of [3500] <Insert value> K, average rated life of 10,000 hours at three hours of operation per start[, and suitable for use with dimming ballasts] unless otherwise indicated.

Add compact fluorescent lamp type(s) to list below if needed.

          - 13 W: T4, double or triple tube, rated 900 initial lumens (minimum).

          - 18 W: T4, double or triple tube, rated 1200 initial lumens (minimum).

          - 26 W: T4, double or triple tube, rated 1800 initial lumens (minimum).

          - 32 W: T4, triple tube, rated 2400 initial lumens (minimum).

          - 42 W: T4, triple tube, rated 3200 initial lumens (minimum).

          - 57 W: T4, triple tube, rated 4300 initial lumens (minimum).

          - 70 W: T4, triple tube, rated 5200 initial lumens (minimum).

          - <Insert type>.

      - BALLASTS FOR FLUORESCENT LAMPS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

For luminaires requiring other than instant-start ballasts, indicate ballast type in the Exterior Luminaire Schedule on Drawings.

        - General Requirements for Electronic Ballasts:

          - Comply with UL 935 and with ANSI C82.11.

          - Designed for type and quantity of lamps served.

          - Ballasts shall be designed for full light output unless another BF, dimmer, or bi-level control is indicated.

ANSI C82.11 states that lamp and ballast combinations are for operation at temperatures of 50 to 105.8 deg F (10 to 41 deg C). Applications outside this range should be noted in the Exterior Luminaire Schedule on Drawings.

          - Sound Rating: [Class A] [Class A, except Class B for T12/HO and T12/Slimline lamp ballasts].

See the Evaluations for discussion on harmonic considerations.

          - THD Rating: Less than [10] [20] <Insert number> percent.

          - Surge Protection: IEEE C62.41.1 and IEEE C62.41.2, Category A or better.

Lower operating frequencies are available but may interfere with default ballasts when used in proximity of infrared sensors.

          - Operating Frequency: [42] <Insert number> kHz or higher.

          - Lamp Current Crest Factor: [1.7] <Insert number> or less.

          - BF: [0.88] <Insert number> or higher.

          - Power Factor: [0.95] [0.98] <Insert number> or higher.

        - Electronic Programmed-Start Ballasts for [T5] [T8] [T5HO] [T5 and T5HO] Lamps: Comply with ANSI C82.11 and the following:

          - Lamp end-of-life detection and shutdown circuit for T5 diameter lamps.

          - Automatic lamp starting after lamp replacement.

        - Electromagnetic Ballasts: Comply with ANSI C82.11; energy saving, high-power factor, Class P, and having automatic-reset thermal protection.

ANSI C82.11 states that lamp and ballast combinations are for operation at temperatures of 50 to 105 deg F (10 to 40 deg C). Applications outside this range should be noted in the Exterior Luminaire Schedule on Drawings.

          - Ballast Manufacturer Certification: Indicated by label.

Retain "Single Ballasts for Multiple Luminaires" Paragraph below to require ballasts in some luminaires to serve lamps in other luminaires. Indicate luminaire types to which this requirement applies in the Exterior Luminaire Schedule on Drawings, and indicate connections on lighting plans.

        - Single Ballasts for Multiple Luminaires: Factory wired with ballast arrangements and bundled extension wiring to suit final installation conditions without modification or rewiring in the field.

        - Ballasts for Low-Temperature Environments:

Retain first option in "Temperatures 0 Deg F (Minus 17 Deg C) and Higher" Subparagraph below if lamp-starting and -operating temperature near 0 deg F (minus 17 deg C) is a critical requirement. Verify, with manufacturers, the compatibility of ballasts with indicated lamps for low-temperature operation.

          - Temperatures 0 Deg F (Minus 17 Deg C) and Higher: [Electronic] [or] [electromagnetic] type rated for 0 deg F (minus 17 deg C) starting and operating temperature with indicated lamp types.

          - Temperatures Minus 20 Deg F (Minus 29 Deg C) and Higher: Electromagnetic type designed for use with indicated lamp types.

Coordinate "Control" Subparagraph below if lighting control Sections, such as Section 260943.16 "Addressable-Fixture Lighting Controls," Section 260943.23 "Relay-Based Lighting Controls," and Section 260923 "Lighting Control Devices," are used for Project.

          - Control: Coordinate wiring from ballast to control device to ensure that ballast, controller, and connecting wiring are compatible.

Use of bi-level and tri-level ballasts may comply with state and local energy-conservation code requirements, including Title 24, Part 6, of the California Code of Regulations.

        - Ballasts for Bi-Level Controlled Luminaires: Electronic type.

          - Operating Modes: Ballast circuit and leads provide for remote control of the light output of the associated lamp between high- and low-level operation and off.

            - High-Level Operation: 100 percent of rated lamp lumens.

            - Low-Level Operation: 30 percent of rated lamp lumens.

          - Ballast shall provide equal current to each lamp in each operating mode.

          - Compatibility: Certified by manufacturer for use with specific bi-level control system and lamp type indicated.

        - Ballasts for Tri-Level Controlled Luminaires: Electronic type.

          - Operating Modes: Ballast circuit and leads provide for remote control of the light output of the associated lamp between high- and low-level operation and off.

            - High-Level Operation: 100 percent of rated lamp lumens.

In "Low-Level Operation" Subparagraph below, retain either option for tri-level ballasts, depending on manufacturer.

            - Low-Level Operation: [30 and 50] [30 and 60] percent of rated lamp lumens.

          - Ballast shall provide equal current to each lamp in each operating mode.

          - Compatibility: Certified by manufacturer for use with specific tri-level control system and lamp type indicated.

      - LUMINAIRE TYPES

Retain "Area and Site" Paragraph below for an outdoor luminaire used for general lighting of a large area, typically mounted on a pole with an arm or on top of a post. Typical uses include parking lots, walkways, and plazas.

        - Area and Site:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Luminaire Shape: [Round] [Square] [Hexagonal] <Insert shape or feature>.

          - Mounting: [Pole] [Building] <Insert mounting type> with [extruded-aluminum] [stainless steel] <Insert material> [rectangular] [round] arm, [11 inches (280 mm)] [13 inches (330 mm)] in length.

          - Luminaire-Mounting Height: <Insert height of luminaire from finished grade>.

          - Distribution: [Type I] [Type II] [Type III] [Type IV] [Type V].

Materials for "Diffusers and Globes" and "Housings" subparagraphs below may be specific to each type of luminaire. General requirements for "Diffusers and Globes" and "Housings" are specified in separate articles toward the end of Part 2.

          - Diffusers and Globes: [Tempered Fresnel glass] [Prismatic glass] [Diffuse glass] [Clear glass] [Prismatic acrylic] [Clear, UV-stabilized acrylic] [Clear polycarbonate] <Insert material>.

          - Housings:

            - [Extruded-aluminum] <Insert material> housing and heat sink.

            - [Clear] <Insert color> [anodized] [powder-coat] [painted] finish.

Retain "Bollard" Paragraph below for an outdoor luminaire with a height lower than pedestrian level used to light an area in close proximity.

        - Bollard:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Shape: [Round] [Square] [Hexagonal] [Fluted] <Insert shape or feature>.

          - Height from Finished Grade: [24 inches (600 mm)] [30 inches (762 mm)] [36 inches (900 mm)] <Insert value>.

          - Overall Height: [30 inches (762 mm)] [36 inches (900 mm)] <Insert value>.

          - Diameter: [6 inches (150 mm)] <Insert value>.

          - Mounting: [Three-point cast-aluminum base] <Insert mounting provisions>.

          - Distribution: [Type III] [Type V].

Materials for "Diffusers and Globes" and "Housings" subparagraphs below may specific to each type of luminaire. General requirements for subparagraphs are specified in separate articles toward the end of Part 2.

          - Diffusers and Globes: [Tempered Fresnel glass] [Prismatic glass] [Diffuse glass] [Clear glass] [Prismatic acrylic] [Clear, UV-stabilized acrylic] [Clear polycarbonate] <Insert material>.

          - Housings:

            - [Extruded-aluminum] <Insert material> housing and heat sink.

            - [Clear] <Insert color> [anodized] [powder-coat] [painted] finish.

Retain "Border" Paragraph below for an outdoor luminaire used to light an area in close proximity and ranges in height from less than 20 inches (500 mm) down, with lower rim flush with the ground/concrete and the light-emitting opening above grade. Typical uses include sidewalks, promenades, drive-over applications, and landscaped areas.

        - Border:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Shape: [Round] [Square] <Insert shape>.

          - Dimensions: [12 inches (300 mm)] [square] [in diameter].

          - [Flush] <Insert dimension> with grade.

Materials for "Diffusers and Globes" and "Housings" subparagraphs below may specific to each type of luminaire. General requirements for subparagraphs are specified in separate articles toward the end of Part 2.

          - Diffusers and Globes: [Tempered Fresnel glass] [Prismatic glass] [Diffuse glass] [Clear glass] [Prismatic acrylic] [Clear, UV-stabilized acrylic] [Clear polycarbonate] <Insert material>.

          - Housings:

            - [Extruded-aluminum] <Insert material> housing and heat sink.

            - [Clear] <Insert color> [anodized] [powder-coat] [painted] finish.

Retain "Canopy" Paragraph below for a surface or recessed luminaire installed under a canopy or overhang. Typical uses include drive-through windows, building entrances, and gas stations.

        - Canopy:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Shape: [Round] [Square] <Insert shape>.

          - Dimensions: [12 inches (300 mm)] [square] [in diameter].

Materials for "Diffusers and Globes" and "Housings" subparagraphs below may specific to each type of luminaire. General requirements for subparagraphs are specified in separate articles toward the end of Part 2.

          - Diffusers and Globes: [Tempered Fresnel glass] [Prismatic glass] [Diffuse glass] [Clear glass] [Prismatic acrylic] [Clear, UV-stabilized acrylic] [Clear polycarbonate] <Insert material>.

          - Housings:

            - [Extruded-aluminum] <Insert material> housing and heat sink.

            - [Clear] <Insert color> [anodized] [powder-coat] [painted] finish.

Retain "Decorative Post Top" Paragraph below for an outdoor luminaire designed for daytime and nighttime aesthetics. Typical uses include walkways, plazas, streetscapes, and building entrances.

        - Decorative Post Top:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Luminaire-Mounting Height: <Insert height of luminaire from finished grade>.

          - Mounting Type: [Arm] [Tenon] [Ring].

          - Distribution: [Type I] [Type II] [Type III] [Type IV] [Type V].

Materials for "Diffusers and Globes" and "Housings" subparagraphs below may specific to each type of luminaire. General requirements for subparagraphs are specified in separate articles toward the end of Part 2.

          - Diffusers and Globes: [Tempered Fresnel glass] [Prismatic glass] [Diffuse glass] [Clear glass] [Prismatic acrylic] [Clear, UV-stabilized acrylic] [Clear polycarbonate] <Insert material>.

          - Housings:

            - [Extruded-aluminum] <Insert material> housing and heat sink.

            - [Clear] <Insert color> [anodized] [powder-coat] [painted] finish.

      - MATERIALS

        - Metal Parts: Free of burrs and sharp corners and edges.

        - Sheet Metal Components: [Corrosion-resistant aluminum] [Stainless steel] [Epoxy-coated steel] <Insert material>. Form and support to prevent warping and sagging.

        - Doors, Frames, and Other Internal Access: Smooth operating, free of light leakage under operating conditions, and designed to permit relamping without use of tools. Designed to prevent doors, frames, lenses, diffusers, and other components from falling accidentally during relamping and when secured in operating position. Doors shall be removable for cleaning or replacing lenses. Ballast shall automatically disconnect when door opens.

        - Diffusers and Globes:

Retain "Acrylic Diffusers" Subparagraph below if an acrylic option in the product description was retained.

          - Acrylic Diffusers: 100 percent virgin acrylic plastic, with high resistance to yellowing and other changes due to aging, exposure to heat, and UV radiation.

Retain "Glass" Subparagraph below if a glass option in the product description was retained.

          - Glass: Annealed crystal glass unless otherwise indicated.

Retain "Lens Thickness" Subparagraph below for all diffuser and globe types.

          - Lens Thickness: At least 0.125-inch (3.175-mm) minimum unless otherwise indicated.

        - Lens and Refractors Gaskets: Use heat- and aging-resistant resilient gaskets to seal and cushion lenses and refractors in luminaire doors.

        - Reflecting surfaces shall have minimum reflectance as follows unless otherwise indicated:

          - White Surfaces: 85 percent.

          - Specular Surfaces: 83 percent.

          - Diffusing Specular Surfaces: 75 percent.

        - Housings:

          - Rigidly formed, weather- and light-tight enclosure that will not warp, sag, or deform in use.

          - Provide filter/breather for enclosed luminaires.

        - Factory-Applied Labels: Comply with UL 1598. Include recommended lamps. Labels shall be located where they will be readily visible to service personnel, but not seen from normal viewing angles when lamps are in place.

          - Label shall include the following lamp characteristics:

            - "USE ONLY," including specific lamp type.

            - Lamp diameter, shape, size, wattage, and coating.

            - CCT and CRI for all luminaires.

      - FINISHES

Retain "Variations in Finishes" Paragraph below if finish is prone to variation; an example is color-anodized aluminum.

        - Variations in Finishes: Noticeable variations in same piece are unacceptable. Variations in appearance of adjoining components are acceptable if they are within the range of approved Samples and are assembled or installed to minimize contrast.

Revise "Luminaire Finish" Paragraph below to include custom colors. Coordinate custom-color requirements for luminaires with those for poles and other luminaire support requirements.

        - Luminaire Finish: Manufacturer's standard paint applied to factory-assembled and -tested luminaire before shipping. Where indicated, match finish process and color of pole or support materials.

Retain "Factory-Applied Finish for Aluminum Luminaires" Paragraph below when luminaire material is aluminum that is not to be field painted and is not required to match finish of pole or support materials.

        - Factory-Applied Finish for Aluminum Luminaires: Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

          - Finish designations prefixed by AA comply with the system established by the Aluminum Association for designating aluminum finishes.

Retain "Natural Satin Finish," "Class I, Clear-Anodic Finish," or "Class I, Color-Anodic Finish" Subparagraph below or revise to suit Project.

          - Natural Satin Finish: Provide fine, directional, medium satin polish (AA-M32); buff complying with AA-M20 requirements; and seal aluminum surfaces with clear, hard-coat wax.

          - Class I, Clear-Anodic Finish: AA-M32C22A41 (Mechanical Finish: Medium satin; Chemical Finish: Etched, medium matte; Anodic Coating: Architectural Class I, clear coating 0.018 mm or thicker), complying with AAMA 611.

          - Class I, Color-Anodic Finish: AA-M32C22A42/A44 (Mechanical Finish: Medium satin; Chemical Finish: Etched, medium matte; Anodic Coating: Architectural Class I, integrally colored or electrolytically deposited color coating 0.018 mm or thicker), complying with AAMA 611.

            - Color: [Light bronze] [Medium bronze] [Dark bronze] [Black] <Insert color>.

Retain "Factory-Applied Finish for Steel Luminaires" Paragraph below when luminaire material is steel that is not to be field painted and is not required to match finish of pole or support materials.

        - Factory-Applied Finish for Steel Luminaires: Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

          - Surface Preparation: Clean surfaces to comply with SSPC-SP 1 to remove dirt, oil, grease, and other contaminants that could impair paint bond. Grind welds and polish surfaces to a smooth, even finish. Remove mill scale and rust, if present, from uncoated steel, complying with SSPC-SP 5/NACE No. 1 or SSPC-SP 8.

          - Exterior Surfaces: Manufacturer's standard finish consisting of one or more coats of primer and two finish coats of high-gloss, high-build polyurethane enamel.

            - Color:

Retain one of three subparagraphs below.

              - As selected from manufacturer's standard catalog of colors.

              - Match Architect's sample of [manufacturer's standard] [custom] color.

              - As selected by Architect from manufacturer's full range.

      - LUMINAIRE SUPPORT COMPONENTS

        - Comply with requirements in Section 260529 "Hangers and Supports for Electrical Systems" for channel and angle iron supports and nonmetallic channel and angle supports.

        - Single-Stem Hangers: 1/2-inch (13-mm) steel tubing with swivel ball fittings and ceiling canopy. Finish shall match luminaire.

        - Wires: ASTM A641/A641M, Class 3, soft temper, zinc-coated steel, [12 gage (2.68 mm)] <Insert size>.

        - Rod Hangers: 3/16-inch (5-mm) minimum diameter, cadmium-plated, threaded steel rod.

- EXECUTION

      - EXAMINATION

        - Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

        - Examine roughing-in for luminaire electrical conduit to verify actual locations of conduit connections before luminaire installation.

        - Examine walls, roofs, [and] [canopy ceilings] [and] [overhang ceilings] for suitable conditions where luminaires will be installed.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - TEMPORARY LIGHTING

        - If approved by Architect, use selected permanent luminaires for temporary lighting. When construction is sufficiently complete, clean luminaires used for temporary lighting and install new lamps.

      - GENERAL INSTALLATION REQUIREMENTS

        - Comply with NECA 1.

Retain first paragraph below if seismic restraint is required by local code or authorities having jurisdiction. See the Evaluations.

        - Use fastening methods and materials selected to resist seismic forces defined for the application and approved by manufacturer.

        - Install lamps in each luminaire.

        - Fasten luminaire to structural support.

NFPA 70 requires minimum support for luminaires. Retain "Supports" Paragraph below for more specific support requirements and for requirements exceeding code minimums. For projects requiring seismic design, additional supports and restraining devices beyond those specified here may be required. See the Evaluations.

        - Supports:

          - Sized and rated for luminaire weight.

          - Able to maintain luminaire position after cleaning and relamping.

          - Support luminaires without causing deflection of finished surface.

          - Luminaire-mounting devices shall be capable of supporting a horizontal force of 100 percent of luminaire weight and a vertical force of 400 percent of luminaire weight.

        - Wall-Mounted Luminaire Support:

          - [Attached to structural members in walls] [Attached to a minimum 1/8-inch (3-mm) backing plate attached to wall structural members] [Attached using through bolts and backing plates on either side of wall] <Insert means of attachment>.

        - Wiring Method: Install cables in raceways. Conceal raceways and cables.

        - [Install luminaires level, plumb, and square with finished grade unless otherwise indicated.] [Install luminaires at height and aiming angle as indicated on Drawings.]

        - Coordinate layout and installation of luminaires with other construction.

        - Adjust luminaires that require field adjustment or aiming. [Include adjustment of photoelectric device to prevent false operation of relay by artificial light sources, favoring a north orientation.]

        - Comply with requirements in Section 260519 "Low-Voltage Electrical Power Conductors and Cables" and Section 260533.13 "Conduits for Electrical Systems" for wiring connections and wiring methods.

      - INSTALLATION OF BOLLARD LUMINAIRES

Coordinate this article with Drawings. Delete if installation is detailed on Drawings.

        - Align units for optimum directional alignment of light distribution.

Retain subparagraph below if luminaires require protection from damage at base due to landscaping maintenance or snow removal operations. Coordinate with Drawings.

          - Install on concrete base with top [4 inches (100 mm)] <Insert dimension> above finished grade or surface at luminaire location. Cast conduit into base, and shape base to match shape of bollard base. Finish by troweling and rubbing smooth. Concrete materials, installation, and finishing are specified in Section 033000 "Cast-in-Place Concrete."

      - INSTALLATION OF INDIVIDUAL GROUND-MOUNTED LUMINAIRES

Coordinate this article with Drawings. Delete if installation is detailed on Drawings.

        - Install on concrete base with top [4 inches (100 mm)] <Insert dimension> above finished grade or surface at luminaire location. Cast conduit into base, and finish by troweling and rubbing smooth. Concrete materials, installation, and finishing are specified in Section 033000 "Cast-in-Place Concrete."

      - CORROSION PREVENTION

        - Aluminum: Do not use in contact with earth or concrete. When in direct contact with a dissimilar metal, protect aluminum by insulating fittings or treatment.

        - Steel Conduits: Comply with Section 260533.13 "Conduits for Electrical Systems." In concrete foundations, wrap conduit with 0.010-inch- (0.254-mm-) thick, pipe-wrapping plastic tape applied with a 50 percent overlap.

      - IDENTIFICATION

        - Identify system components, wiring, cabling, and terminals. Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

      - FIELD QUALITY CONTROL

        - Inspect each installed luminaire for damage. Replace damaged luminaires and components.

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

        - Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

Coordinate "Operational Test" Subparagraph below with requirements in Section 260923 "Lighting Control Devices."

          - Operational Test: After installing luminaires, switches, and accessories, and after electrical circuitry has been energized, test units to confirm proper operation.

Retain "Verify operation of photoelectric controls" Subparagraph below for luminaires controlled by photoelectric controls.

          - Verify operation of photoelectric controls.

Retain "Illumination Tests" Paragraph below if specific illumination performance is indicated.

        - Illumination Tests:

          - Measure light intensities at night. Use photometers with calibration referenced to NIST standards. Comply with the following IES testing guide(s):

Retain one or more of first four subparagraphs below.

            - IES LM-5.

            - IES LM-50.

            - IES LM-52.

            - IES LM-72.

Coordinate "Operational Test" Subparagraph below with requirements in Section 260923 "Lighting Control Devices."

          - Operational Test: After installing luminaires, switches, and accessories, and after electrical circuitry has been energized, test units to confirm proper operation.

        - Luminaire will be considered defective if it does not pass tests and inspections.

        - Prepare a written report of tests, inspections, observations, and verifications indicating and interpreting results. If adjustments are made to lighting system, retest to demonstrate compliance with standards.

      - DEMONSTRATION

        - [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain luminaires[ and photocell relays].

      - STARTUP SERVICE

        - Burn-in all lamps that require specific aging period to operate properly, prior to occupancy by Owner. Burn-in fluorescent and compact fluorescent lamps intended to be dimmed, for at least 100 hours at full voltage.

      - ADJUSTING

Verify with Owner that adjusting service is required for Project.

        - Occupancy Adjustments: When requested within [12] <Insert number> months of date of Substantial Completion, provide on-site assistance in adjusting the direction of aim of luminaires to suit occupied conditions. Make up to [two] <Insert number> visits to Project during other-than-normal hours for this purpose. Some of this work may be required during hours of darkness.

          - During adjustment visits, inspect all luminaires. Replace lamps or luminaires that are defective.

          - Parts and supplies shall be manufacturer's authorized replacement parts and supplies.

          - Adjust the aim of luminaires in the presence of Architect.

END OF SECTION 265617