Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 271100 - COMMUNICATIONS EQUIPMENT ROOM FITTINGS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Backboards.

          - Boxes, enclosures, and cabinets.

          - Power strips.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 270536 "Cable Trays for Communications Systems" for cable trays and accessories.

          - Section 271313 "Communications Copper Backbone Cabling" for copper data cabling associated with system panels and devices.

          - Section 271323 "Communications Optical Fiber Backbone Cabling" for optical-fiber data cabling associated with system panels and devices.

          - Section 271333 "Communications Coaxial Backbone Cabling" for coaxial data cabling associated with system panels and devices.

          - Section 271513 "Communications Copper Horizontal Cabling" for copper data cabling associated with system panels and devices.

          - Section 271523 "Communications Optical Fiber Horizontal Cabling" for coaxial data cabling associated with system panels and devices.

          - Section 271533 "Communications Coaxial Horizontal Cabling" for coaxial data cabling associated with system panels and devices.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project. Definitions of "access provider" and "service provider" are derived from BICSI's "Telecommunications Distribution Methods Manual."

        - Access Provider: An operator that provides a circuit path or facility between the service provider and user. An access provider can also be a service provider.

        - BICSI: Building Industry Consulting Service International.

        - RCDD: Registered communications distribution designer.

        - Service Provider: The operator of a telecommunications transmission service delivered through access provider facilities.

        - TGB: Telecommunications grounding bus bar.

        - TMGB: Telecommunications main grounding bus bar.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

          - Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for equipment racks and cabinets.

          - Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

        - Shop Drawings: For communications equipment room fittings. Include plans, elevations, sections, details, and attachments to other work.

          - Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

          - Equipment Racks and Cabinets: Include workspace requirements and access for cable connections.

          - Grounding: Indicate location of grounding bus bar and its mounting detail showing standoff insulators and wall mounting brackets.

      - INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Data: For [Installer, ]qualified layout technician, installation supervisor, and field inspector.

Retain "Seismic Qualification Data" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Sections specifying telecommunications equipment supports and seismic controls. See ASCE/SEI 7 for certification requirements for equipment and components.

        - Seismic Qualification Data: Certificates, from manufacturer.

          - Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

          - Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions. Base certification on the maximum number of components capable of being mounted in each rack type. Identify components on which certification is based.

          - Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

      - QUALITY ASSURANCE

        - Installer Qualifications: Cabling installer must have personnel certified by BICSI on staff.

          - Layout Responsibility: Preparation of Shop Drawings shall be under direct supervision of [RCDD] [Technician].

          - Installation Supervision: Installation shall be under direct supervision of [Technician] [Installer 2, Copper or Fiber], who shall be present at all times when Work of this Section is performed at Project site.

          - Field Inspector: Currently registered by BICSI as [RCDD] [Technician] to perform the on-site inspection.

- PRODUCTS

Manufacturers and products listed in SpecAgent and Masterworks Paragraph Builder are neither recommended nor endorsed by the AIA or Deltek. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - PERFORMANCE REQUIREMENTS

Retain "Seismic Performance" Paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design or to require seismic-rated equipment. Delete paragraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

        - Seismic Performance: Equipment shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] [Telcordia GR-63-CORE requirements for Zone 4 Seismic Earthquake Environments] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

          - The term "withstand" means "the unit will remain in place without separation of any parts when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

      - BACKBOARDS

        - Backboards: Plywood, [fire-retardant treated, ]3/4 by 48 by 96 inches (19 by 1220 by 2440 mm).

        - Backboard Paint: [Pre-painted] [Light-colored fire-retardant paint] [Light-colored interior latex paint].

For 19-inch- and 23-inch-wide racks, frames, and enclosures, see Section 271116 "Communications Racks, Frames, and Enclosures."

      - BOXES, ENCLOSURES, AND CABINETS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - General Requirements for Boxes, Enclosures, and Cabinets: Boxes, enclosures, and cabinets shall be listed and labeled for intended location and use.

        - Sheet Metal Outlet and Device Boxes: Comply with NEMA OS 1 and UL 514A.

In "Cast-Metal Outlet and Device Boxes" Paragraph below, aluminum boxes are suitable for use with steel raceways in most environments. Type FD is a device box with extra depth. Many other configurations are available.

        - Cast-Metal Outlet and Device Boxes: Comply with NEMA FB 1, Type FD, [ferrous alloy] [aluminum], with gasketed cover.

        - Nonmetallic Outlet and Device Boxes: Comply with NEMA OS 2 and UL 514C.

        - Small Sheet Metal Pull and Junction Boxes: NEMA OS 1.

        - Cast-Metal Access, Pull, and Junction Boxes: Comply with NEMA FB 1 and UL 1773, [cast aluminum] [galvanized cast iron] with gasketed cover.

        - Box extensions used to accommodate new building finishes shall be of same material as recessed box.

        - Device Box Dimensions: [4 inches square by 2-1/8 inches deep (100 mm square by 60 mm deep)] [4 inches by 2-1/8 inches by 2-1/8 inches deep (100 mm by 60 mm by 60 mm deep)] <Insert dimension>.

Coordinate "Hinged-Cover Enclosures" Paragraph below with Drawings, if hinged-cover enclosures other than NEMA 250, Type 1 are required, such as for very dusty areas, or if consideration should be given to use of NEMA 250, Type 3R or Type 12 enclosures.

        - Hinged-Cover Enclosures: Comply with UL 50 and NEMA 250, [Type 1] [Type 3R] [Type 4] [Type 12] <Insert type> with continuous-hinge cover with flush latch unless otherwise indicated.

          - Metal Enclosures: Steel, finished inside and out with manufacturer's standard enamel.

          - Nonmetallic Enclosures: [Plastic] [Fiberglass].

          - Interior Panels: Steel; all sides finished with manufacturer's standard enamel.

        - Cabinets:

          - NEMA 250, [Type 1] [Type 3R] [Type 12] <Insert type> galvanized-steel box with removable interior panel and removable front, finished inside and out with manufacturer's standard enamel.

          - Hinged door in front cover with flush latch and concealed hinge.

          - Key latch to match panelboards.

          - Metal barriers to separate wiring of different systems and voltage.

          - Accessory feet where required for freestanding equipment.

          - Nonmetallic cabinets shall be listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

      - POWER STRIPS

Retain one of two paragraphs below.

        - Comply with requirements in Section 271116 "Communications Racks, Frames, and Enclosures."

        - Power Strips: Comply with UL 1363.

          - Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

          - Rack mounting, with [detachable] [integral] flanges.

          - Height: [1 RU]. <Insert value>.

          - Housing: [Metal] <Insert material>.

          - [Six] <Insert number>, [15-A, 120-V ac, NEMA WD 6, Configuration 5-15R] [20-A, 120-V ac, NEMA WD 6, Configuration 5-20R] receptacles.

          - [Front] [Rear]-facing receptacles.

          - LED indicator lights for power and protection status.

          - LED indicator lights for reverse polarity and open outlet ground.

          - Circuit Breaker and Thermal Fusing:

Retain one of first two subparagraphs below.

            - When protection is lost, circuit opens and cannot be reset.

            - Unit continues to supply power if protection is lost.

          - [Close-coupled, direct plug-in] [Cord connected with 15-foot (4.5-m)] line cord.

          - Rocker-type on-off switch, illuminated when in on position.

Retain subparagraphs below if power strips contain surge protection.

          - Surge Protection: UL 1449, Type 3.

            - Maximum Surge Current, Line to Neutral: [27 kA] [72 kA] <Insert value>.

            - Protection modes shall be line to neutral, line to ground, and neutral to ground.

            - UL 1449 Voltage Protection Rating for line to neutral and line to ground shall be [600 V] <Insert value> and [500 V].<Insert value> for neutral to ground.

- EXECUTION

      - ENTRANCE FACILITIES

Retain first paragraph below if demarcation point and service entrance cabling are from telecommunications service provider.

        - Contact telecommunications service provider and arrange for installation of demarcation point, protected entrance terminals, and a housing when so directed by service provider.

        - Comply with requirements in Section 270528 "Pathways for Communications Systems" for materials and installation requirements for [underground] [buried] [aerial] pathways.

      - INSTALLATION

        - Comply with NECA 1.

        - Comply with BICSI's "Telecommunications Distribution Methods Manual" for layout of communications equipment spaces.

        - Comply with BICSI's "Information Technology Systems Installation Methods Manual" for installation of equipment in communications equipment spaces.

        - Bundle, lace, and train conductors and cables to terminal points without exceeding manufacturer's limitations on bending radii. Install lacing bars and distribution spools.

Revise paragraphs below to specify coordination with other parties involved in finalizing communications equipment room Work. See the Evaluations.

        - Coordinate layout and installation of communications equipment in tracks and in room. Coordinate service entrance configuration with service provider.

          - Meet jointly with systems providers, equipment suppliers, and Owner to exchange information and agree on details of equipment configurations and installation interfaces.

          - Record agreements reached in meetings and distribute them to other participants.

          - Adjust configurations and locations of distribution frames, cross-connects, and patch panels in equipment rooms to accommodate and optimize configurations and space requirements of communications equipment.

          - Adjust configurations and locations of equipment with distribution frames, cross-connects, and patch panels of cabling systems of other communications, electronic safety and security, and related systems that share space in equipment room.

        - Coordinate location of power raceways and receptacles with locations of communications equipment requiring electrical power to operate.

        - Backboards:

          - Install from 6 inches (150 mm) to 8 feet, 6 inches (2588 mm) above finished floor. If plywood is fire rated, ensure that fire-rating stamp is visible after installation.

          - Paint all sides of backboard with two coats of paint[, leaving fire rating stamp visible].

          - Comply with requirements for backboard installation in BICSI's "Information Technology Systems Installation Methods Manual" and TIA-569-D.

      - SLEEVE AND SLEEVE SEAL INSTALLATION FOR ELECTRICAL PENETRATIONS

        - Install sleeves and sleeve seals at penetrations of exterior floor and wall assemblies. Comply with requirements in Section 270544 "Sleeves and Sleeve Seals for Communications Pathways and Cabling."

      - FIRESTOPPING

        - Comply with requirements in Section 078413 "Penetration Firestopping."

        - Comply with TIA-569-D, Annex A, "Firestopping."

        - Comply with BICSI's "Information Technology Systems Installation Methods Manual," "Firestopping Practices" Ch.

END OF SECTION 271100