Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 281500 - INTEGRATED ACCESS CONTROL HARDWARE DEVICES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Integrated credential readers and entry management.

          - Access control credentials.

          - Electrified locking devices and accessories.

          - Egress management devices.

          - Access control remote devices.

          - Electronic key management systems.

        - Related Requirements:

Always retain first two subparagraphs below.

          - Section 260011 "Facility Performance Requirements for Electrical" for seismic-load, wind-load, acoustical, and other field conditions applicable to Work specified in this Section.

          - Section 280010 "Supplemental Requirements for Electronic Safety and Security" for additional abbreviations, definitions, submittals, qualifications, testing agencies, and other Project requirements applicable to Work specified in this Section.

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 281511 "Integrated Credential Readers and Entry Management" for additional integrated access control hardware device products.

          - Section 281513 "Access Control Credentials" for additional access control hardware credential products.

          - Section 281515 "Electrified Locking Devices and Accessories" for additional electronically controlled lock and latch products.

          - Section 281517 "Egress Management Devices" for additional access control hardware device products intended for use along the means of egress.

          - Section 281519 "Access Control Remote Devices" for additional wireless access control hardware device products.

          - Section 281521 "Telephone Entry Systems" for access control telephone entry products.

          - Section 281523 "Intercom Entry Systems" for access control intercom entry products.

          - Section 281525 "Electronic Key Management Systems" for additional key management system products with access control interfaces.

          - Section 281527 "Access Control Electronic Turnstiles and Mobility Systems" for security turnstile operator products with access control interfaces.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - NFC: Near Field Communications.

      - PREINSTALLATION MEETINGS

Retain "Preinstallation Coordination Meeting(s)" Paragraph below if Work of this Section does not justify a full preinstallation conference as specified in Section 013100 "Project Management and Coordination," but would benefit from a smaller coordination meeting. Consider videoconference option if Project requires social distancing for meetings for infection control.

        - Preinstallation Coordination Meeting(s): For integrated access control hardware devices. Conduct meeting(s) [as videoconference] [or] [at Project site] <Insert location> before <Insert construction activity>.

          - Attendees: Installers, fabricators, representatives of manufacturers, representatives from telecommunications, [Owner's security representatives,] [IT representatives,] and administrants for field tests and inspections. Notify Architect[, Construction Manager] [, and Owner's Commissioning Authority] of scheduled meeting dates.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

Retain one or more subparagraphs below as needed to verify compliance of Work with Project requirements.

          - Integrated Credential Readers and Entry Management:

            - Credential readers.

            - Keypads.

            - Combination reader devices.

          - Access Control Credentials:

            - Access control cards.

          - Electrified Locking Devices and Accessories:

            - Electrically controlled single-point locks and latches.

            - Electrically controlled two- and three-point locks and latches.

            - High-security electronic locks.

            - Status monitoring and egress devices.

          - Egress Management Devices:

            - Panic hardware with special locking arrangement.

            - Fire-exit hardware with special locking arrangement.

          - Access Control Remote Devices:

            - NFC access control devices.

          - Electronic Key Management Systems:

            - Electronic key management system units.

Coordinate "Shop Drawings" Paragraph below with "Regulatory Agency Approvals for Egress Management Devices" Article.

        - Shop Drawings:

Retain one or more of six subparagraphs below as needed to verify compliance of Work with Project requirements.

          - Project general notes.

          - Device layout.

          - Block diagram and cable/conduit routing.

          - System communications details.

          - System mounting details.

          - Secondary power calculations.

Retain "Certificates" Paragraph below if certificate from manufacturer or fabricator is required by Architect to verify that product or assembly has been investigated and approved/recognized by third party prior to installation.

        - Certificates:

          - <Insert certificate requirement>.

        - Field Quality-Control Submittals:

          - Field quality-control reports.

      - INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Retain "Manufacturers' Published Instructions" Paragraph below when execution requirements state "in accordance with manufacturer's published instructions," especially if those instructions may require preinstallation review and coordination with Construction Documents to verify constructability and commissioning requirements.

        - Manufacturers' Published Instructions: Record copy of official installation[ and testing] instructions issued to Installer by manufacturer for the following:

          - Installation instructions for integrated credential readers and entry management devices.

          - Manufacturer's recommended tests and inspections for integrated credential readers and entry management devices.

          - Printing, programming, and handling instructions for access control credentials.

          - Installation instructions for electrified locking devices and accessories.

          - Manufacturer's recommended tests and inspections for electrified locking devices and accessories.

          - Installation instructions for egress management devices.

          - Manufacturer's recommended tests and inspections for egress management devices.

          - Installation instructions for access control remote devices.

          - Manufacturer's recommended tests and inspections for access control remote devices.

          - Installation instructions for electronic key management systems.

          - Manufacturer's recommended tests and inspections for electronic key management systems.

        - Sample warranties.

      - CLOSEOUT SUBMITTALS

Submittals for record documents, operation and maintenance data, software, and software documentation are specified in Section 280010 "Supplemental Requirements for Electronic Safety and Security."

        - Maintenance Contracts:

          - Software and firmware service agreements.

        - Warranty documentation.

      - MAINTENANCE MATERIAL SUBMITTALS

See Section 017700 "Closeout Procedures" for submission of maintenance material items.

Extra stock items are replacement products; for example: luminaires, receptacles, and switches.

        - Extra Stock Material: Furnish to Owner extra materials[, from same production run,] that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.[ Include the following:]

          - Integrated Credential Readers and Entry Management Devices: [One] <Insert number> of each type.

          - Electrified Locking Devices and Accessories: [One] <Insert number> of each type.

Retain "Special Tools" Paragraph below if special tools are required for installation or maintenance. Special tools are items that would not be available from a typical hardware store; for example: keys, circuit-breaker test sets, circuit-breaker racking handles, circuit-breaker hoists, and battery hoists.

        - Special Tools: Furnish to Owner proprietary equipment, keys, and software required to operate, maintain, repair, adjust, or implement future changes to integrated access control hardware devices, that are packaged with protective covering for storage on-site and identified with labels describing contents.[ Include the following:]

          - <Insert item>.

      - REGULATORY AGENCY APPROVALS FOR EGRESS MANAGEMENT DEVICES

Retain this article when review and approval of Contractor's submittals by authorities having jurisdiction is required.

Retain one of two paragraphs below. Retain first paragraph if Contractor's submittals are prepared by Contractor's professional engineer who is recognized by authorities having jurisdiction as designer of record for egress management devices. Retain second paragraph if Contractor's submittals require review and approval with signature and seal by Architect's professional engineer who is recognized as designer of record.

In first paragraph, first option may lead to unnecessary delays for resubmission of Contractor's submittals to authorities having jurisdiction after action by Architect. Second option may lead to unnecessary delays for rework if Contractor's submittals are rejected by authorities having jurisdiction after action by Architect. Architects typically prefer receiving approval by authorities having jurisdiction before taking action, but likelihood and consequences of risks under Project's delivery method (e.g., design-bid-build or design-build) should be considered before retaining an option.

        - Submittals for egress management devices requiring approval by authorities having jurisdiction must be signed and sealed by qualified life safety professional engineer responsible for their preparation. [Obtain approval by authorities having jurisdiction prior to submitting for action by Architect.] [Submit for action by Architect prior to submitting for approval by authorities having jurisdiction.]

        - Submittals for egress management devices require action by Architect prior to submitting for approval by authorities having jurisdiction.

      - WARRANTY

When warranties are required and available, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner, after one-year correction period specified in the Contract, under Contractor's general warranty and prevailing local laws.

Verify durations of extended-warranty periods needed.

        - Integrated Credential Readers and Entry Management Devices Warranty:

          - Special Installer Extended Warranty: Installer warrants that fabricated and installed integrated credential readers and entry management devices perform in accordance with specified requirements and agrees to repair or replace components that fail to perform as specified within extended-warranty period.

            - Extended-Warranty Period: [Two] [Three] [Four] <Insert number> years from date of Substantial Completion; full coverage for labor, materials, and equipment.

Retain "Special Manufacturer Extended Warranty" Subparagraph below if Project requires that a special manufacturer extended warranty take over when the special Installer extended warranty expires. To benefit Owner, manufacturer extended-warranty period must be longer than Installer extended-warranty period.

          - Special Manufacturer Extended Warranty: Manufacturer warrants that integrated credential readers and entry management devices perform in accordance with specified requirements and agrees to provide repair or replacement of components or products that fail to perform as specified within extended-warranty period.

            - [Initial ]Extended-Warranty Period: [Three] [Four] [Five] <Insert number> years from date of Substantial Completion; [full] [prorated] coverage for labor, materials, and equipment.

Retain "origin" option in "Follow-On Extended-Warranty Period" Subparagraph below if recipient assumes ownership of goods when they are shipped. Retain "destination" option if seller retains ownership of goods until they are delivered. Damaged shipping containers labeled "FOB Origin" cannot be returned to sender, but carrier is liable to recipient for delay and damage claims.

            - Follow-On Extended-Warranty Period: [Eight] <Insert number> years from date of Substantial Completion; [full] [prorated] coverage for materials only, free on board [origin] [destination], freight prepaid.

Verify durations of extended warranty periods needed.

        - Electrified Locking Devices and Accessories Warranty:

          - Special Installer Extended Warranty: Installer warrants that fabricated and installed electrified locking devices and accessories perform in accordance with specified requirements and agrees to repair or replace components that fail to perform as specified within extended-warranty period.

            - Extended-Warranty Period: [Two] [Three] [Four] <Insert number> years from date of Substantial Completion; full coverage for labor, materials, and equipment.

Retain "Special Manufacturer Extended Warranty" Subparagraph below if Project requires that a special manufacturer extended warranty take over when the special Installer extended warranty expires. To benefit Owner, manufacturer extended-warranty period must be longer than Installer extended warranty period.

          - Special Manufacturer Extended Warranty: Manufacturer warrants that electrified locking devices and accessories perform in accordance with specified requirements and agrees to provide repair or replacement of components or products that fail to perform as specified within extended-warranty period.

            - [Initial ]Extended-Warranty Period: [Three] [Four] [Five] <Insert number> years from date of Substantial Completion; [full] [prorated] coverage for labor, materials, and equipment.

Retain "origin" option in "Follow-On Extended-Warranty Period" Subparagraph below if recipient assumes ownership of goods when they are shipped. Retain "destination" option if seller retains ownership of goods until they are delivered. Damaged shipping containers labeled "FOB Origin" cannot be returned to sender, but carrier is liable to recipient for delay and damage claims.

            - Follow-On Extended-Warranty Period: [Eight] <Insert number> years from date of Substantial Completion; [full] [prorated] coverage for materials only, free on board [origin] [destination], freight prepaid.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - INTEGRATED CREDENTIAL READERS AND ENTRY MANAGEMENT

Products listed in this article are subset of products specified in Section 281511 "Integrated Credential Readers and Entry Management."

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Swipe Card Reader <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

          - Performance Criteria:

            - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

            - Listing Criteria:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

              - UL CCN ALVY; including UL 294.

              - Plastic Enclosure: UL CCN QMFZ2; including UL 94.

            - General Characteristics: Visual LED indication of card read.

          - Options:

            - Enclosure Rating: IEC 60529, [IP55] [IP65] [IP66] <Insert IP rating>.

            - Input Voltage: [5 to 12 V(dc)] <Insert power input>.

            - Operating Temperature: [Minus 40 to plus 160 deg F (Minus 40 to plus 71 deg C)] <Insert temperature>.

            - Materials: [Long-wearing polymeric plastic] [Polycarbonate] [Metal].

            - Colors: [Black] [Gray] <Insert color>.

            - Climate: [Indoor] [and] [outdoor].

            - Size: [Single gang] [or] [double gang].

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Proximity Reader for Card, Fob, or Smartphone <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

          - Performance Criteria:

            - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

            - Listing Criteria:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

              - UL CCN ALVY; including UL 294.

              - Plastic Enclosure: UL CCN QMFZ2; including UL 94.

            - General Characteristics: Visual LED indication of card read.

          - Options:

            - Enclosure Rating: IEC 60529, [IP55] [IP65] [IP66] <Insert IP rating>.

            - Input Voltage: [5 to 16 V(dc)] [PoE] <Insert power input>.

            - Operating Temperature: [Minus 40 to plus 160 deg F (Minus 40 to plus 71 deg C)] <Insert temperature>.

            - Read Range: Up to [1 inch (25 mm)] [2 inch (51 mm)] [3 inch (76 mm)].

            - Transmit Frequency: [125 kHz] [13.56 MHz] [2.4 GHz].

            - Materials: [Long-wearing polymeric plastic] [Polycarbonate] [Metal].

            - Colors: [Black] [Gray] <Insert color>.

            - Climate: [Indoor] [and] [outdoor].

            - Size: [Single gang] [or] [double gang].

          - Accessories:

            - Long-range receiver module.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Door Lock Keypad <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

          - Performance Criteria:

            - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

            - Listing Criteria:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

              - UL CCN ALVY; including UL 294.

              - Plastic Enclosure: UL CCN QMFZ2; including UL 94.

          - Options:

            - Enclosure Rating: IEC 60529, [IP55] [IP65] [IP66] <Insert IP rating>.

            - Visual LED indication of [three-] [or] [six-]digit code read.

            - Input Power: [5 to 16 V(dc)] [12 to 28 V(dc)] [Alkaline batteries] <Insert power input>.

            - Operating Temperature: [Minus 20 to plus 150 deg F (Minus 29 to plus 66 deg C)] <Insert temperature>.

            - Materials: [Long-wearing polymeric plastic] [Polycarbonate] [Metal].

            - Colors: [Black] [Gray] <Insert color>.

            - Climate: [Indoor] [and] [outdoor].

            - Size: [Single gang] [or] [double gang].

            - Mounting:

Retain one or more of four subparagraphs below to suit Project.

              - Door/window mullions.

              - Outlet boxes.

              - Flat surfaces.

              - Integrated door lock keypad.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Scramble Keypad <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

          - Performance Criteria:

            - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

            - Listing Criteria:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

              - UL CCN ALVY; including UL 294.

              - Plastic Enclosure: UL CCN QMFZ2; including UL 94.

          - Options:

            - Enclosure Rating: IEC 60529, [IP55] [IP65] [IP66] <Insert IP rating>.

            - Visual LED indication of [three-] [or] [six-] [or] [nine-]digit code read.

            - Input Power: [8 to 12 V(dc)] <Insert power input>.

            - Operating Temperature: [5 to 122 deg F (Minus 15 to plus 50 deg C)] <Insert operating temperature>.

            - Materials: [Long-wearing polymeric plastic] [Polycarbonate] [Metal].

            - Colors: [Black] [Gray] <Insert color>.

            - Climate: [Indoor] [and] [outdoor].

            - Mounting: [Single-gang] [or] [double-gang] outlet box.

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Combination Card Reader and Keypad <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

          - Performance Criteria:

            - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

            - Listing Criteria:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

              - UL CCN ALVY; including UL 294.

              - Plastic Enclosure: UL CCN QMFZ2; including UL 94.

            - General Characteristics: Visual LED indication of code and/or card read.

          - Options:

            - Enclosure Rating: IEC 60529, [IP55] [IP65] [IP66] <Insert IP rating>.

            - Input Power: [5 to 16 V(dc)] [12 to 28 V(dc)] <Insert power input>.

            - Operating Temperature: [32 to 122 deg F (0 to 50 deg C)] <Insert temperature>.

            - Materials: [Long-wearing polymeric plastic] [Polycarbonate] [Metal].

            - Colors: [Black] [Gray] [White] <Insert color>.

            - Climate: [Indoor] [and] [outdoor].

            - Mounting:

Retain one of two subparagraphs below, or both, to suit Project.

              - Surface mount.

              - Triple-gang wall box.

      - ACCESS CONTROL CREDENTIALS

Products listed in this article are subset of products specified in Section 281513 "Access Control Credentials."

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Access Control Cards <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Performance Criteria:

            - Reference Standards:

Retain "Personal Identity Verification (PIV)" Subparagraph below for Federal Government projects. Other owners may also use similar technology. PIV cards provide identity information that can be verified both by humans (e.g., photo) and by automated systems (e.g., fingerprints, iris images, PIN).

              - Personal Identity Verification (PIV): FIPS PUB 201-2.

              - Physical: IEC 7810; IEC 10373; IEC 7816 for contact cards; and IEC 14443 for contactless cards.

              - Functional: UL 294; IEC 60839-11-1; and IEC 60839-11-2.

              - Material Durability: INCITS 322.

            - Format: Customizable, including artwork.[ Provide credential template with provisions for the following:]

Retain "On Front," "On Back," and "Stored Data Elements" subparagraphs below where access control cards may be issued by third party. Revise subparagraphs to suit Project.

              - On Front: Photograph, full name (surname first), affiliation, organization, card expiration date, color-coding, Owner's name, Owner's logo, two-dimensional bar code.

              - On Back: Physical characteristics of cardholder, employee ID number, card number, magnetic stripe, linear bar code, return address. Include the following message:

                - <Insert message>.

              - Stored Data Elements: PIN, employee ID number, two fingerprint templates, electronic facial image, one iris image, digital signature private key and certificate, key management private key and certificate, card authenticate data, and PIV authentication data.

          - Options:

            - Data Format: Wiegand [26 bit] [34 bit] [37 bit].

            - Transmit Frequency: [125 kHz] [and] [13.56 MHz].

            - Data Retention: [10] [20] years.

            - Memory Capacity: [2.5 kB] [8 kB] [16 kB] [32 kB].

            - Operating Temperature: [Minus 40 to plus 185 deg F (Minus 40 to plus 85 deg C)].

            - Materials: [Plastic] [ABS] [PVC laminate].

            - Color: [White] [Off-white] [Glossy white] <Insert color>.

            - Reading Medium: [Multi-criteria use] [Proximity] [and] [chip] [and] [magnetic strip].

      - ELECTRIFIED LOCKING DEVICES AND ACCESSORIES

Products listed in this article are subset of products specified in Section 281515 "Electrified Locking Devices and Accessories."

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Electrically Controlled Single-Point Latch <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

          - Performance Criteria:

            - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

            - Listing Criteria:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

              - Special Locking Arrangements: UL CCN FWAX; including UL 294, NFPA 101, and ICC IBC.

              - Electrically Controlled Single-Point Locks and Latches: UL CCN GYQS, UL 10B, and UL 10C; designed to be used with Class 2 control-voltage circuits in accordance with Article 725 of NFPA 70.

          - Options:

            - [Audible] [and] [visual] indication of door unlock.

            - Input Power: [12 V(ac/dc)] [or] [24 V(ac/dc)] [PoE] [AA batteries] <Insert power input>.

            - Operating Temperature: [Minus 31 to plus 151 deg F (Minus 35 to plus 66 deg C)] <Insert temperature>.

            - Connectivity: [Hardwired] [Wireless].

            - Materials: [Zinc] <Insert material>.

            - Finishes: [US26D Satin Chrome] <Insert finish>.

            - Integrated Credential Reader:

              - Proximity (125 kHz).

              - Smart (13.56 MHz).

              - Bluetooth, low energy (2.4 GHz).

              - NFC.

            - Integrated [combination lock] [keypad].

            - Failure Mode: [Fail-safe] [Fail-secure].

            - Mechanical key override.

            - Latch bolt monitor.

            - [With] [or] [without] deadbolt.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Electrically Controlled Three-Point Latches <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

          - Performance Criteria:

            - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

            - Listing Criteria:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

              - Special Locking Arrangements: UL CCN FWAX; including UL 294, NFPA 101, and ICC IBC.

              - Two- and Three-Point Locks and Latches: UL CCN GYXR; including UL 10B.

          - Options:

            - [Audible] [and] [visual] indication of door unlock.

            - Input Power: [12 V(ac/dc)] [or] [24 V(ac/dc)] [PoE] <Insert power input>.

            - Operating Temperature: [Minus 31 to plus 151 deg F (Minus 35 to plus 66 deg C)] <Insert temperature>.

            - Connectivity: [Hardwired] [Wireless].

            - Materials: [Zinc] <Insert material>.

            - Finishes: [US26D Satin Chrome] <Insert finish>.

            - Integrated Credential Reader:

              - Proximity (125 kHz).

              - Smart (13.56 MHz).

              - Bluetooth, low energy (2.4 GHz).

              - NFC.

            - Integrated [combination lock] [keypad].

            - Failure Mode: [Fail-safe] [Fail-secure].

            - Mechanical key override.

            - Latch bolt monitor.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Type 1 High-Security Electronic Lock <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

          - Performance Criteria:

            - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

            - Listing Criteria:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

              - Special Locking Arrangements: UL CCN FWAX; including UL 294, NFPA 101, and ICC IBC.

              - High-Security Electronic Locks: UL CCN OZDC; including UL Subject 2058.

              - Type 1 Locks: UL CCN OZDU.

          - Options:

            - [Audible] [and] [visual] indication of door unlock.

            - Input Power: [12 V(ac/dc)] [or] [24 V(ac/dc)] [PoE] [Li-ion battery] <Insert power input>.

            - Operating Temperature: [Minus 4 to plus 140 deg F (Minus 20 to plus 60 deg C)] <Insert temperature>.

            - Connectivity: [Hardwired] [Wireless].

            - Memory:

              - Access time/date stamp stored in [key] [and] [cylinder].

              - Audit Trail: [100] [1000] <Insert number> events.

              - Directory of authorized keys stored in cylinder.

            - Cylinder Type: [Single] [Double] [Mortise] <Insert type>.

            - Materials: [Zinc] [Steel] <Insert material>.

            - Finishes: [US26D Satin Chrome] <Insert finish>.

            - Integrated credential reader.

            - Failure Mode: [Fail-safe] [Fail-secure].

            - Mechanical key override.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Type 1F High-Security Electronic Lock <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

          - Performance Criteria:

            - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

            - Listing Criteria:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

              - Special Locking Arrangements: UL CCN FWAX; including UL 294, NFPA 101, and ICC IBC.

              - High-Security Electronic Locks: UL CCN OZDC; including UL Subject 2058.

Retaining option in "Type 1F Locks" Subparagraph below may eliminate all available manufacturers.

              - Type 1F Locks: [UL CCN OZEM; including ]Fed. Spec. FF-L-2740.

          - Options:

            - [Audible] [and] [visual] indication of door unlock.

            - Input Power: [12 V(ac/dc)] [or] [24 V(ac/dc)] [PoE] [Li-ion battery] <Insert power input>.

            - Operating Temperature: [Minus 4 to plus 140 deg F (Minus 20 to plus 60 deg C)] <Insert temperature>.

            - Connectivity: [Hardwired] [Wireless].

            - Materials: [Zinc] [Steel] <Insert material>.

            - Finishes: [US26D Satin Chrome] <Insert finish>.

            - Failure Mode: [Fail-safe] [Fail-secure].

            - Mechanical key override.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Request-to-Exit (REX) Motion Sensor <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

          - Performance Criteria:

            - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Listing Criteria: UL CCN ALVY; including UL 294.

          - Options:

            - Input Power: [125 V(ac)] <Insert power input>.

            - Operating Temperature: [Minus 13 to plus 140 deg F (Minus 25 to plus 60 deg C)] <Insert temperature>.

            - Sensing Technology: [Passive infrared (PIR)] [Active infrared (AIR)].

            - Color: [Black] [Gray] [White] <Insert color>.

            - Mounting: [Wall surface] [Recessed in ceiling] [Door frame].

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Request-to-Exit (REX) Push Button <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Source Limitations: Obtain products from single manufacturer.

          - Performance Criteria:

            - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Listing Criteria: UL CCN ALVY; including UL 294.

          - Options:

            - Input Power: [12 to 24 V(ac/dc)] <Insert power input>.

            - Operating Temperature: [Minus 13 to plus 140 deg F (Minus 25 to plus 60 deg C)] <Insert operating temperature>.

            - Operating Mechanism: [Pneumatic] [Piezoelectric].

            - Faceplate Material: [Stainless steel] <Insert material>.

            - Button Material: [Plastic] [Anodized aluminum] <Insert material>.

            - Button Color: [Green] [Blue] [Red] <Insert color>.

            - Lettering Color: [White] [Black] <Insert color>.

            - Failure Mode: [Fail-safe] [Fail-secure].

      - EGRESS MANAGEMENT DEVICES

Products listed in this article are subset of products specified in Section 281517 "Egress Management Devices."

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Magnetic Lock Hardware with Special Locking Arrangement for Fire-Rated Doors <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

          - Performance Criteria:

            - Regulatory Requirements:

              - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

              - Compliant with NFPA 101, ICC IBC, and local life safety code requirements for use along means of egress.

            - Listing Criteria:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

              - Special Locking Arrangements: UL CCN FWAX or UL CCN FWAX2; including UL 294, NFPA 101, and ICC IBC.

              - Electromagnetic Locks for Fire-Rated Doors: UL CCN GWXT; including UL 10B and UL 10C.

          - Options:

            - Input Voltage: [12 to 24 V(dc)] <Insert voltage>.

            - Holding Force: [1200 lbf (5338 N)] <Insert force>.

            - Release Delay: [Zero] [Five] [10] [15] <Insert number> seconds.

            - Relock Function: [Manual] [Delayed automatic] relock.

            - Door Prop Alarm Delay: [None] [30 seconds] <Insert delay>.

            - Door Movement Detection: [1/8 inch (3 mm)] [1/4 inch (6 mm)] [1/2 inch (13 mm)] [3/4 inch (19 mm)] [1 inch (25 mm)].

            - Dry contact for external alarm relay[ to security system] [ to fire-alarm system] [ to BMS].

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Panic Hardware with Special Locking Arrangement for Fire-Rated Doors <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

          - Performance Criteria:

            - Regulatory Requirements:

              - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

              - Compliant with NFPA 101, ICC IBC, and local life safety code requirements for use along means of egress.

            - Listing Criteria:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

              - Special Locking Arrangements: UL CCN FWAX or UL CCN FWAX2; including UL 294, NFPA 101, and ICC IBC.

              - Panic Hardware for Fire-Rated Doors: UL CCN GXHX, UL 10C, and UL 305.

              - Controlled-Exit Panic Devices: UL CCN FULA; including UL 305.

          - Options:

            - Input Voltage: [12 to 24 V(dc)] <Insert voltage>.

            - Release Delay: [Zero] [Five] [10] [15] <Insert number> seconds.

            - Door Prop Alarm: [None] [Activate after 30 seconds] <Insert delay>.

            - Dry contact for external alarm relay[ to security system] [ to fire-alarm system] [ to BMS].

            - Secondary Power: [9 V battery] <Insert power source>.

      - ACCESS CONTROL REMOTE DEVICES

Products listed in this article are subset of products specified in Section 281519 "Access Control Remote Devices."

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Near Field Communications (NFC) Access Control Devices <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Performance Criteria:

            - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Listing Criteria: UL CCN ALVY; including UL 294.

          - Options:

            - Enclosure Rating: IEC 60529, [IP55] [IP65] [IP66] <Insert IP rating>.

            - Input Voltage: [5 to 12 V(dc)] [PoE] <Insert voltage>.

            - Operating Temperature: [Minus 40 to plus 160 deg F (Minus 40 to plus 71 deg C)] <Insert temperature>.

            - Read Range: Up to [1 inch (25 mm)] [2 inch (51 mm)] [3 inch (76 mm)].

            - Transmit Frequency: [125 kHz] [13.56 MHz].

            - Materials: [Long-wearing polymeric plastic] [Polycarbonate] [Metal].

            - Colors: [Black] [Gray] <Insert color>.

            - Climate: [Indoor] [and] [outdoor].

            - Size: [Single gang] [or] [double gang].

      - ELECTRONIC KEY MANAGEMENT SYSTEMS

Products listed in this article are subset of products specified in Section 281525 "Electronic Key Management Systems."

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Electronic Key Management System Unit <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Performance Criteria:

            - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Listing Criteria: UL CCN ALZK; including UL 294.

          - Options:

            - Input Voltage: [110 to 240 V(ac)] <Insert voltage>.

            - Operating Temperature: [32 to 122 deg F (0 to 50 deg C)] <Insert temperature>.

            - Key Storage Capacity: <Insert number>.

            - Operating Frequency: [125 kHz] [13.56 MHz].

            - Materials: [Stainless steel] <Insert material>.

            - Finishes: [Powder coated] <Insert finish>.

            - Backup Battery: [12 V(dc)] <Insert battery size>.

            - Front Cover: [Clear display window] [Solid panel].

            - Enclosure Size: <Insert size>.

          - Operation:

            - Access Method: [Proximity card] [and] [biometrics] [and] [keypad] [and] [standard key].

            - Alarm output: [Local sounder] [Output contacts].

- EXECUTION

      - DEPLOYMENT OF CREDENTIALS

        - Comply with manufacturer's published instructions.

Retain "Third-Party Issuing of Access Control Credentials" Paragraph if Owner requires that third-party print and issue access control credentials.

        - Third-Party Issuing of Access Control Credentials:

          - Printing of New Credentials: Contractor must be capable of programming and issuing credentials compatible with Owner's access control system.

            - Initial Issuance: Provide spreadsheet or form for collecting data for generation of credentials. Owner will submit completed form containing data for personnel to be issued credentials. Print and provide initial run, printed and programmed credentials in specified format within [four] <Insert number> weeks of request.

            - Ongoing Issuance: Produce additional credentials upon Owner request. Owner will submit completed form containing data for personnel to be issued credentials. Print and program credentials in specified format within [one] [two] weeks of request.

      - INSTALLATION

        - Comply with manufacturer's published instructions.

        - Special Techniques:

          - Cable Type: [Shielded] [Unshielded] <Insert cable size>.

          - Analog Maximum Cable Length: [1000 ft (300 m)] <Insert cable length>.

          - Digital Maximum Cable Length: [300 ft (100 m)] [500 ft (150 m)] <Insert cable length>.

        - Interfaces with Other Work:

          - Coordinate installation of new products for access control hardware devices with existing conditions.

            - <Insert requirements for transition between new and existing>.

          - Coordinate access control credentials with integrated credential readers and access control system architecture.

          - Egress Management Interfaces:

            - Coordinate with Section 282000 "Video Surveillance" for automatic video feed callup upon delayed egress activation.

            - Coordinate with Section 230923 "Direct Digital Control (DDC) System for HVAC" for monitoring of egress management device alarms by BMS.

            - Coordinate with [Section 284621.11 "Addressable Fire-Alarm Systems"] [Section 284621.13 "Conventional Fire-Alarm Systems"] for monitoring of egress management device alarms by fire-alarm system.

      - FIELD QUALITY CONTROL

        - [Acceptance ]Testing Preparation:

          - <Insert requirements>.

Retain first paragraph below to require that field quality-control tests be witnessed. Local ordinance or custom may require that authorities having jurisdiction witness the testing.

        - Field tests and inspections must be witnessed by [Architect] [Tenant] [authorities having jurisdiction] <Insert names or titles of witnesses>.

        - Tests and Inspections:

          - Perform manufacturer's recommended tests and inspections.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Nonconforming Work:

          - Device will be considered defective if it does not pass tests and inspections.

          - Remove and replace defective units and retest.

        - Collect, assemble, and submit test and inspection reports.

Retain "Manufacturer Services" Paragraph below if manufacturer's representative is required to support or supervise the administrant specified in Section 280010 "Supplemental Requirements for Electronic Safety and Security" for field tests and inspections performed by Installer or third-party agencies.

        - Manufacturer Services:

Retain "supervise" option in subparagraph below when third-party tests and inspections must be witnessed and approved by factory-authorized service representative to satisfy special extended-warranty requirements. In some cases, Installer may be factory authorized under warranty provisions to fulfill this role.

          - Engage factory-authorized service representative to [support] [supervise] field tests and inspections.

      - PROTECTION

        - After installation, protect integrated access control hardware devices from construction activities. Remove and replace items that are contaminated, defaced, damaged, or otherwise caused to be unfit for use prior to acceptance by Owner.

      - MAINTENANCE

Services in "Software and Firmware Service Agreement" Paragraph below may not be allowed for publicly funded projects.

        - Software and Firmware Service Agreement:

Retain three subparagraphs below if Owner intends to upgrade software and firmware of products when upgrade is available from manufacturer.

          - Technical Support: Beginning at Substantial Completion, verify that software and firmware service agreement includes software and firmware support for [two] <Insert number> years.

          - Upgrade Service: At Substantial Completion, update software and firmware to latest version. Install and program software and firmware upgrades that become available within [two] <Insert number> years from date of Substantial Completion.[ Verify that upgrading software includes operating system and new or revised licenses for using software.]

            - Upgrade Notice: No fewer than [30] <Insert number> days to allow Owner to schedule and access the system[ and to upgrade computer equipment if necessary].

          - Upgrade Reports: Prepare report after each update, documenting upgrades installed.

END OF SECTION 281500