Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 281515 - ELECTRIFIED LOCKING DEVICES AND ACCESSORIES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Electrically controlled single-point locks and latches.

          - Electrically controlled two- and three-point locks and latches.

          - High-security electronic locks.

          - Status monitoring and egress devices.

        - Related Requirements:

Always retain first two subparagraphs below.

          - Section 260011 "Facility Performance Requirements for Electrical" for seismic-load, wind-load, acoustical, and other field conditions applicable to Work specified in this Section.

          - Section 280010 "Supplemental Requirements for Electronic Safety and Security" for additional abbreviations, definitions, submittals, qualifications, testing agencies, and other Project requirements applicable to Work specified in this Section.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - NFC: Near Field Communications.

      - PREINSTALLATION MEETINGS

Retain "Preinstallation Coordination Meeting(s)" Paragraph below if Work of this Section does not justify a full preinstallation conference as specified in Section 013100 "Project Management and Coordination," but would benefit from a smaller coordination meeting. Consider videoconference option if Project requires social distancing for meetings for infection control.

        - Preinstallation Coordination Meeting(s): For electrified locking devices and accessories. Conduct meeting(s) [as videoconference] [or] [at Project site] <Insert location> before <Insert construction activity>.

          - Installers, fabricators, representatives of manufacturers, representatives from telecommunications, [Owner's security representatives,] [IT representatives,] and administrants for field tests and inspections. Notify Architect[, Construction Manager] [, and Owner's Commissioning Authority] of scheduled meeting dates.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

Retain one or more of four subparagraphs below as needed to verify compliance of Work with Project requirements.

          - Electrically controlled single-point locks and latches.

          - Electrically controlled two- and three-point locks and latches.

          - High-security electronic locks.

          - Status monitoring and egress devices.

        - Shop Drawings:

Retain one or more of six subparagraphs below as needed to verify compliance of Work with Project requirements.

          - Project general notes.

          - Device layout.

          - Block diagram and cable/conduit routing.

          - System communications details.

          - System mounting details.

          - Secondary power calculations.

Retain "Certificates" Paragraph below if certificate from manufacturer or fabricator is required by Architect to verify that product or assembly has been investigated and approved/recognized by third party prior to installation.

        - Certificates:

          - <Insert certificate requirement>.

        - Field Quality-Control Submittals:

          - Field quality-control reports.

      - INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Retain "Manufacturers' Published Instructions" Paragraph below when execution requirements state "in accordance with manufacturer's published instructions," especially if those instructions may require preinstallation review and coordination with Construction Documents to verify constructability and commissioning requirements.

        - Manufacturers' Published Instructions: Record copy of official installation[ and testing] instructions issued to Installer by manufacturer for the following:

          - Installation instructions for electrified locking devices and accessories.

        - Sample warranties.

      - CLOSEOUT SUBMITTALS

Submittals for record documents, operation and maintenance data, software, and software documentation are specified in Section 280010 "Supplemental Requirements for Electronic Safety and Security."

        - Maintenance Contracts:

          - Firmware service agreement.

        - Warranty documentation.

      - MAINTENANCE MATERIAL SUBMITTALS

See Section 017700 "Closeout Procedures" for submission of maintenance material items.

Extra stock items are replacement products; for example: luminaires, receptacles, and switches.

        - Extra Stock Material: Furnish to Owner extra materials[, from same production run,] that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.[ Include the following:]

          - Electrified Locking Devices and Accessories: [One] <Insert number> of each type.

Special tools are items that would not be available from a typical hardware store; for example: keys, circuit-breaker test sets, circuit-breaker racking handles, circuit-breaker hoists, and battery hoists.

        - Special Tools: Furnish to Owner proprietary equipment, keys, and software required to operate, maintain, repair, adjust, or implement future changes to electrified locking devices and accessories, that are packaged with protective covering for storage on-site and identified with labels describing contents.[ Include the following:]

          - <Insert item>.

      - WARRANTY

When warranties are required and available, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner, after one-year correction period specified in the Contract, under Contractor's general warranty and prevailing local laws.

Verify durations of extended warranty periods needed.

        - Special Installer Extended Warranty: Installer warrants that fabricated and installed electrified locking devices and accessories perform in accordance with specified requirements and agrees to repair or replace components or products that fail to perform as specified within extended-warranty period.

          - Extended-Warranty Period: [Two] [Three] [Four] <Insert number> years from date of Substantial Completion; full coverage for labor, materials, and equipment.

Retain "Special Manufacturer Extended Warranty" Paragraph below if Project requires that a special manufacturer extended warranty take over when the special Installer extended warranty expires. To benefit Owner, manufacturer extended-warranty period must be longer than Installer extended-warranty period.

        - Special Manufacturer Extended Warranty: Manufacturer warrants that electrified locking devices and accessories perform in accordance with specified requirements and agrees to provide repair or replacement of components or products that fail to perform as specified within extended-warranty period.

          - [Initial ]Extended-Warranty Period: [Three] [Four] [Five] <Insert number> years from date of Substantial Completion; [full] [prorated] coverage for labor, materials, and equipment.

Retain "origin" option in "Follow-On Extended-Warranty Period" Subparagraph below if recipient assumes ownership of goods when they are shipped. Retain "destination" option if seller retains ownership of goods until they are delivered. Damaged shipping containers labeled "FOB Origin" cannot be returned to sender, but carrier is liable to recipient for delay and damage claims.

          - Follow-On Extended-Warranty Period: [Eight] <Insert number> years from date of Substantial Completion; [full] [prorated] coverage for materials only, free on board [origin] [destination], freight prepaid.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - ELECTRICALLY CONTROLLED SINGLE-POINT LOCKS AND LATCHES

        - Description: This category covers single-point electrified locksets, including cylindrical and mortise-style locks, which are connected to the access control system via hardwired cabling or wireless. Electrified locksets communicate with credential readers through the access control system to unlock doors upon credential authorization. Electrified locksets may also be programmed to lock or unlock directly via a signal from the access control system without the need for credential authorization.

        - Performance Criteria:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - Listing Criteria:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Special Locking Arrangements: UL CCN FWAX; including UL 294, NFPA 101, and ICC IBC.

            - Electrically Controlled Single-Point Locks and Latches: UL CCN GYQS, UL 10B, and UL 10C; designed to be used with Class 2 control-voltage circuits in accordance with Article 725 of NFPA 70.

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Electrically Controlled Single-Point Latch <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

          - Options:

            - [Audible] [and] [visual] indication of door unlock.

            - Input Power: [12 V(ac/dc)] [or] [24 V(ac/dc)] [PoE] [AA batteries] <Insert power input>.

            - Operating Temperature: [Minus 31 to plus 151 deg F (Minus 35 to plus 66 deg C)] <Insert temperature>.

            - Connectivity: [Hardwired] [Wireless].

            - Materials: [Zinc] <Insert material>.

            - Finishes: [US26D Satin Chrome] <Insert finish>.

            - Integrated Credential Reader:

              - Proximity (125 kHz).

              - Smart (13.56 MHz).

              - Bluetooth low energy (2.4 GHz).

              - NFC.

            - Integrated [combination lock] [keypad].

            - Failure Mode: [Fail-safe] [Fail-secure].

            - Mechanical key override.

            - Latch bolt monitor.

            - [With] [or] [without] deadbolt.

      - ELECTRICALLY CONTROLLED TWO- AND THREE-POINT LOCKS AND LATCHES

        - Description: This category covers two- and three-point electrified locksets, which are connected to the access control system via hardwired cabling or wireless. Electrified locksets communicate with credential readers through the access control system to unlock doors upon credential authorization. Electrified locksets may also be programmed to lock or unlock directly via a signal from the access control system without the need for credential authorization.

        - Performance Criteria:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - Listing Criteria:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Special Locking Arrangements: UL CCN FWAX; including UL 294, NFPA 101, and ICC IBC.

            - Two- and Three-Point Locks and Latches: UL CCN GYXR; including UL 10B.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Electrically Controlled Two-Point Latch <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

          - Options:

            - [Audible] [and] [visual] indication of door unlock.

            - Input Power: [12 V(ac/dc)] [or] [24 V(ac/dc)] [PoE] <Insert power input>.

            - Operating Temperature: [Minus 31 to plus 151 deg F (Minus 35 to plus 66 deg C)] <Insert temperature>.

            - Connectivity: [Hardwired] [Wireless].

            - Materials: [Zinc] <Insert material>.

            - Finishes: [US26D Satin Chrome] <Insert finish>.

            - Integrated Credential Reader:

              - Proximity (125 kHz).

              - Smart (13.56 MHz).

              - Bluetooth low energy (2.4 GHz).

              - NFC.

            - Integrated [combination lock] [keypad].

            - Failure Mode: [Fail-safe] [Fail-secure].

            - Mechanical key override.

            - Latch bolt monitor.

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Electrically Controlled Three-Point Latch <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

          - Options:

            - [Audible] [and] [visual] indication of door unlock.

            - Input Power: [12 V(ac/dc)] [or] [24 V(ac/dc)] [PoE] <Insert power input>.

            - Operating Temperature: [Minus 31 to plus 151 deg F (Minus 35 to plus 66 deg C)] <Insert temperature>.

            - Connectivity: [Hardwired] [Wireless].

            - Materials: [Zinc] <Insert material>.

            - Finishes: [US26D Satin Chrome] <Insert finish>.

            - Integrated Credential Reader:

              - Proximity (125 kHz).

              - Smart (13.56 MHz).

              - Bluetooth low energy (2.4 GHz).

              - NFC.

            - Integrated [combination lock] [keypad].

            - Failure Mode: [Fail-safe] [Fail-secure].

            - Mechanical key override.

            - Latch bolt monitor.

      - HIGH-SECURITY ELECTRONIC LOCKS

        - Description: This category covers high-security electronic locks, which are connected to the access control system via hardwired cabling or wireless. High-security electronic locks typically have multilevel authentication or utilize heavy-duty components for increased security.

        - Performance Criteria:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

          - Listing Criteria:

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

            - Special Locking Arrangements: UL CCN FWAX; including UL 294, NFPA 101, and ICC IBC.

            - High-Security Electronic Locks: UL CCN OZDC; including UL Subject 2058.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Type 1 High-Security Electronic Lock <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

          - Additional Listing Criteria: UL CCN OZDU.

          - Options:

            - [Audible] [and] [visual] indication of door unlock.

            - Input Power: [12 V(ac/dc)] [or] [24 V(ac/dc)] [PoE] [Li-ion battery] <Insert power input>.

            - Operating Temperature: [Minus 4 to plus 140 deg F (Minus 20 to plus 60 deg C)] <Insert temperature>.

            - Connectivity: [Hardwired] [Wireless].

            - Memory:

              - Access time/date stamp stored in [key] [and] [cylinder].

              - Audit Trail: [100] [1000] <Insert number> events.

              - Directory of authorized keys stored in cylinder.

            - Cylinder Type: [Single] [Double] [Mortise] <Insert type>.

            - Materials: [Zinc] [Steel] <Insert material>.

            - Finishes: [US26D Satin Chrome] <Insert finish>.

            - Integrated credential reader.

            - Failure Mode: [Fail-safe] [Fail-secure].

            - Mechanical key override.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Type 1F High-Security Combination Lock <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

Retaining option in "Additional Listing Criteria" Subparagraph below may eliminate all available manufacturers.

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

          - Additional Listing Criteria: [UL CCN OZEM; including ]Fed. Spec. FF-L-2740.

          - Options:

            - [Audible] [and] [visual] indication of door unlock.

            - Input Power: [12 V(ac/dc)] [or] [24 V(ac/dc)] [PoE] [Li-ion battery] [Electromechanically self-powered] <Insert power input>.

            - Operating Temperature: [Minus 10 to plus 155 deg F (Minus 23 to plus 68 deg C)] <Insert temperature>.

            - Connectivity: [Hardwired] [Wireless].

            - Materials: [Zinc] [Steel] <Insert material>.

            - Finishes: [US26D Satin Chrome] <Insert finish>.

            - Failure Mode: [Fail-safe] [Fail-secure].

            - Mechanical key override.

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Type 2 High-Security Combination Lock <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

          - Additional Listing Criteria: UL CCN OZFE.

          - Options:

            - [Audible] [and] [visual] indication of door unlock.

            - Input Power: [12 V(ac/dc)] [or] [24 V(ac/dc)] [PoE] [Li-ion battery] <Insert power input>.

            - Operating Temperature: [Minus 4 to plus 140 deg F (Minus 20 to plus 60 deg C)] <Insert operating temperature>.

            - Connectivity: [Hardwired] [Wireless].

            - Materials: [Zinc] [Steel] <Insert material>.

            - Finishes: [US26D Satin Chrome] <Insert finish>.

            - Integrated credential reader.

            - Request-to-Exit (REX) switch.

            - Failure Mode: [Fail-safe] [Fail-secure].

            - Mechanical key override.

            - Keyed Cylinder Configurations:

              - Standard key in lever.

              - Small-format interchangeable core (SFIC).

              - Yale large-format removeable core.

      - STATUS MONITORING AND EGRESS DEVICES

        - Description: This category covers egress devices and sensors, which are installed integral to or adjacent to door assemblies. Equipment under this category may be interconnected to other access control equipment, such as credential readers and locking devices. Equipment under this category may also be directly connected to the access control system to report door status.

        - Performance Criteria:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

          - Listing Criteria: UL CCN ALVY; including UL 294.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Request-to-Exit (REX) Motion Sensor <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

          - Options:

            - Input Power: [125 V(ac)] <Insert power input>.

            - Operating Temperature: [Minus 13 to plus 140 deg F (Minus 25 to plus 60 deg C)] <Insert temperature>.

            - Sensing Technology [Passive infrared (PIR)] [Active infrared (AIR)].

            - Color: [Black] [Gray] [White] <Insert color>.

            - Mounting: [Wall surface] [Recessed in ceiling] [Door frame].

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Request-to-Exit (REX) Push Button <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain "Source Limitations" Subparagraph below to limit sources for this product type.

          - Source Limitations: Obtain products from single manufacturer.

          - Options:

            - Input Power: [12 to 24 V(ac/dc)] <Insert power input>.

            - Operating Temperature: [Minus 13 to plus 140 deg F (Minus 25 to plus 60 deg C)] <Insert temperature>.

            - Operating Mechanism: [Pneumatic] [Piezoelectric].

            - Faceplate Material: [Stainless steel] <Insert material>.

            - Button Material: [Plastic] [Anodized aluminum] <Insert material>.

            - Button Color: [Green] [Blue] [Red] <Insert color>.

            - Lettering Color: [White] [Black] <Insert color>.

            - Failure Mode: [Fail-safe] [Fail-secure].

- EXECUTION

      - INSTALLATION

        - Comply with manufacturer's published instructions.

        - Special Techniques:

          - Cable Type: [Shielded] [Unshielded] <Insert cable size>.

          - Maximum Cable Length: [15 ft (5 m)] [50 ft (15 m)] [100 ft (30 m)] <Insert cable length>.

        - Interfaces with Other Work:

          - Coordinate installation of new products for electrified locking devices and accessories with existing conditions.

            - <Insert requirements for transition between new and existing>.

      - FIELD QUALITY CONTROL

        - [Acceptance ]Testing Preparation:

          - <Insert requirements>.

Retain first paragraph below to require that field quality-control tests be witnessed. Local ordinance or custom may require that authorities having jurisdiction witness the testing.

        - Field tests and inspections must be witnessed by [Architect] [Tenant] [authorities having jurisdiction] <Insert names or titles of witnesses>.

        - Tests and Inspections:

          - Perform manufacturer's recommended tests and inspections.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Nonconforming Work:

          - Device will be considered defective if it does not pass tests and inspections.

          - Remove and replace defective units and retest.

        - Collect, assemble, and submit test and inspection reports.

Retain "Manufacturer Services" Paragraph below if manufacturer's representative is required to support or supervise the administrant specified in Section 280010 "Supplemental Requirements for Electronic Safety and Security" for field tests and inspections performed by Installer or third-party agencies.

        - Manufacturer Services:

Retain "supervise" option in subparagraph below when third-party tests and inspections must be witnessed and approved by factory-authorized service representative to satisfy special extended-warranty requirements. In some cases, Installer may be factory authorized under warranty provisions to fulfill this role.

          - Engage factory-authorized service representative to [support] [supervise] field tests and inspections.

      - PROTECTION

        - After installation, protect electrified locking devices and accessories from construction activities. Remove and replace items that are contaminated, defaced, damaged, or otherwise caused to be unfit for use prior to acceptance by Owner.

      - MAINTENANCE

Services in "Firmware Service Agreement" Paragraph below may not be allowed for publicly funded projects.

        - Firmware Service Agreement:

Retain three subparagraphs below if Owner intends to upgrade firmware of products when upgrade is available from manufacturer.

          - Technical Support: Beginning at Substantial Completion, verify that firmware service agreement includes software and firmware support for [two] <Insert number> years.

          - Upgrade Service: At Substantial Completion, update software to latest version. Install and program software and firmware upgrades that become available within [two] <Insert number> years from date of Substantial Completion.

            - Upgrade Notice: No fewer than [30] <Insert number> days to allow Owner to schedule and access the system.

          - Upgrade Reports: Prepare report after each update, documenting upgrades installed.

END OF SECTION 281515