Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 281519 - ACCESS CONTROL REMOTE DEVICES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Near Field Communications (NFC) access control devices.

          - Bluetooth communications access control devices.

          - Wireless communications access control devices.

        - Related Requirements:

Always retain two subparagraphs below.

          - Section 260011 "Facility Performance Requirements for Electrical" for seismic-load, wind-load, acoustical, and other field conditions applicable to Work specified in this Section.

          - Section 280010 "Supplemental Requirements for Electronic Safety and Security" for additional abbreviations, definitions, submittals, qualifications, testing agencies, and other Project requirements applicable to Work specified in this Section.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - NFC: Near Field Communications.

      - PREINSTALLATION MEETINGS

Retain "Preinstallation Coordination Meeting(s)" Paragraph below if Work of this Section does not justify a full preinstallation conference as specified in Section 013100 "Project Management and Coordination," but would benefit from a smaller coordination meeting. Consider videoconference option if Project requires social distancing for meetings for infection control.

        - Preinstallation Coordination Meeting(s): For access control remote devices. Conduct meeting(s) [as videoconference] [or] [at Project site] <Insert location> before <Insert construction activity>.

          - Attendees: Installers, fabricators, representatives of manufacturers, representatives from telecommunications, [Owner's security representatives,] [IT representatives,] and administrants for field tests and inspections. Notify Architect[, Construction Manager] [, and Owner's Commissioning Authority] of scheduled meeting dates.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

Retain one or more of three subparagraphs below as needed to verify compliance of Work with Project requirements.

          - NFC access control devices.

          - Bluetooth communications access control devices.

          - Wireless communications access control devices.

        - Shop Drawings:

Retain one or more of six subparagraphs below as needed to verify compliance of Work with Project requirements.

          - Project general notes.

          - Device layout.

          - Block diagram and cable/conduit routing.

          - System communications details.

          - System mounting details.

          - Secondary power calculations.

Retain "Certificates" Paragraph below if certificate from manufacturer or fabricator is required by Architect to verify that product or assembly has been investigated and approved/recognized by third party prior to installation.

        - Certificates:

          - <Insert certificate requirement>.

        - Field Quality-Control Submittals:

          - Field quality-control reports.

      - INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Retain "Manufacturers' Published Instructions" Paragraph below when execution requirements state "in accordance with manufacturer's published instructions," especially if those instructions may require preinstallation review and coordination with Construction Documents to verify constructability and commissioning requirements.

        - Manufacturers' Published Instructions: Record copy of official installation[ and testing] instructions issued to Installer by manufacturer for the following:

          - Installation instructions for access control remote devices.

          - Manufacturer's recommended tests and inspections for access control remote devices.

      - CLOSEOUT SUBMITTALS

Submittals for record documents, operation and maintenance data, software, and software documentation are specified in Section 280010 "Supplemental Requirements for Electronic Safety and Security."

        - Maintenance Contracts:

          - Software and firmware service agreement.

      - MAINTENANCE MATERIAL SUBMITTALS

See Section 017700 "Closeout Procedures" for submission of maintenance material items.

Special tools are items that would not be available from a typical hardware store; for example: keys, circuit-breaker test sets, circuit-breaker racking handles, circuit-breaker hoists, and battery hoists.

        - Special Tools: Furnish to Owner proprietary equipment, keys, and software required to operate, maintain, repair, adjust, or implement future changes to access control remote devices, that are packaged with protective covering for storage on-site and identified with labels describing contents.[ Include the following:]

          - <Insert item>.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - NEAR FIELD COMMUNICATIONS (NFC) ACCESS CONTROL DEVICES <Insert drawing designation>

Copy and re-edit this article for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

Retain this article for access control devices using smartphone or similar NFC interface.

        - Description: This category includes access control devices that use NFC technology to transmit data over short distances. Data may be transmitted between proximity card, fob, or smartphone and NFC-enabled credential readers.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Performance Criteria:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

          - Listing Criteria: UL CCN ALVY; including UL 294.

        - Options:

          - Enclosure Rating: IEC 60529, [IP55] [IP65] [IP66] <Insert IP rating>.

          - Input Voltage: [5 to 12 V(dc)] [PoE] <Insert voltage>.

          - Operating Temperature: [Minus 40 to plus 160 deg F (Minus 40 to plus 71 deg C)] <Insert temperature>.

          - Read Range: Up to [1 inch (25 mm)] [2 inch (51 mm)] [3 inch (76 mm)].

          - Transmit Frequency: [125 kHz] [13.56 MHz].

          - Materials: [Long-wearing polymeric plastic] [Polycarbonate] [Metal].

          - Colors: [Black] [Gray] <Insert color>.

          - Climate: [Indoor] [and] [outdoor].

          - Size: [Single gang] [or] [double gang].

      - BLUETOOTH COMMUNICATIONS ACCESS CONTROL DEVICES <Insert drawing designation>

Copy and re-edit this article for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

Retain this article for access control devices using smartphone or similar Bluetooth communications interface.

        - Description: This category includes access control devices that use Bluetooth communications to transmit data over short distances. Data are typically transmitted between smartphone and Bluetooth-enabled credential readers.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Performance Criteria:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

          - Listing Criteria: UL CCN ALVY; including UL 294.

        - Options:

          - Enclosure Rating: IEC 60529, [IP55] [IP65] [IP66] <Insert IP rating>.

          - Input Voltage: [5 to 12 V(dc)] [PoE] <Insert voltage>.

          - Operating Temperature: [Minus 40 to plus 160 deg F (Minus 40 to plus 71 deg C)] <Insert temperature>.

          - Read Range: Up to [3 inch (76 mm)] [5 inch (127 mm)] [8 inch (203 mm)].

          - Transmit Frequency: [2.4 GHz] <Insert frequency>.

          - Materials: [Long-wearing polymeric plastic] [Polycarbonate] [Metal].

          - Colors: [Black] [Gray] <Insert color>.

          - Climate: [Indoor] [and] [outdoor].

          - Size: [Single gang] [or] [double gang].

      - WIRELESS COMMUNICATIONS ACCESS CONTROL DEVICES <Insert drawing designation>

Copy and re-edit this article for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

Retain this article for access control devices using long-range radio frequency identification (RFID) transponders and receivers, such as transit toll pass systems.

        - Description: This category includes access control devices that use wireless technology and connect to a building's local area network (LAN). Data are typically transmitted from WiFi-enabled fobs or smartphones to WiFi-enabled credential readers.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Performance Criteria:

          - Regulatory Requirements: Listed and labeled in accordance with NFPA 70 by qualified electrical testing laboratory recognized by authorities having jurisdiction and marked for intended location and application.

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com/.

          - Listing Criteria: UL CCN ALVY; including UL 294.

        - Options:

          - Environmental Rating: IEC 60529, [IP55] [IP65] [IP66] <Insert IP rating>.

          - Input Voltage: [5 to 12 V(dc)] [PoE] <Insert voltage>.

          - Operating Temperature: [Minus 40 to plus 160 deg F (Minus 40 to plus 71 deg C)] <Insert temperature>.

          - Read Range: Up to <Insert distance>.

          - Transmit Frequency: [2.4 GHz] [5 GHz].

          - Materials: [Long-wearing polymeric plastic] [Polycarbonate] [Metal].

          - Colors: [Black] [Gray] <Insert color>.

          - Climate: [Indoor] [and] [outdoor].

          - Size: [Single gang] [or] [double gang].

- EXECUTION

      - INSTALLATION

        - Comply with manufacturer's published instructions.

        - Special Techniques:

          - Cable Type: [Shielded] [Unshielded] <Insert cable size>.

          - Maximum Cable Length: [300 ft (100 m)] [500 ft (150 m)] <Insert cable length>.

        - Interfaces with Other Work:

          - Coordinate installation of new products for <Insert system or product group> with existing conditions.

            - <Insert requirements for transition between new and existing>.

      - FIELD QUALITY CONTROL

        - [Acceptance ]Testing Preparation:

          - <Insert requirements>.

Retain first paragraph below to require that field quality-control tests be witnessed. Local ordinance or custom may require that authorities having jurisdiction witness the testing.

        - Field tests and inspections must be witnessed by [Architect] [Tenant] [authorities having jurisdiction] <Insert names or titles of witnesses>.

        - Tests and Inspections:

          - Perform manufacturer's recommended tests and inspections.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Nonconforming Work:

          - Device will be considered defective if it does not pass tests and inspections.

          - Remove and replace defective units and retest.

        - Collect, assemble, and submit test and inspection reports.

Retain "Manufacturer Services" Paragraph below if manufacturer's representative is required to support or supervise the administrant specified in Section 280010 "Supplemental Requirements for Electronic Safety and Security" for field tests and inspections performed by Installer or third-party agencies.

        - Manufacturer Services:

Retain "supervise" option in subparagraph below when third-party tests and inspections must be witnessed and approved by factory-authorized service representative to satisfy special extended-warranty requirements. In some cases, Installer may be factory authorized under warranty provisions to fulfill this role.

          - Engage factory-authorized service representative to [support] [supervise] field tests and inspections.

      - PROTECTION

        - After installation, protect access control remote devices from construction activities. Remove and replace items that are contaminated, defaced, damaged, or otherwise caused to be unfit for use prior to acceptance by Owner.

      - MAINTENANCE

Services in "Software and Firmware Service Agreement" Paragraph below may not be allowed for publicly funded projects.

        - Software and Firmware Service Agreement:

Retain three subparagraphs below if Owner intends to upgrade software and firmware of products when upgrade is available from manufacturer.

          - Technical Support: Beginning at Substantial Completion, verify that software and firmware service agreement includes software and firmware support for [two] <Insert number> years.

          - Upgrade Service: At Substantial Completion, update software and firmware to latest version. Install and program software and firmware upgrades that become available within [two] <Insert number> years from date of Substantial Completion.[ Verify that upgrading software includes operating system and new or revised licenses for using software.]

            - Upgrade Notice: No fewer than [30] <Insert number> days to allow Owner to schedule and access the system[ and to upgrade computer equipment if necessary].

          - Upgrade Reports: Prepare report after each update, documenting upgrades installed.

END OF SECTION 281519