Copyright 2018 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 282000 - VIDEO SURVEILLANCE

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section includes a video surveillance system consisting of cameras, digital video recorder, data transmission wiring, and a control station with its associated equipment.

        - Related Requirements:

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 281300 "Access Control System Software and Database Management" to integrate access control system interface and control.

          - Section 283100 "Intrusion Detection" to integrate video surveillance used for intrusion detection.

          - Section 283121 "Area and Perimeter Intrusion Detection" to integrate video surveillance used for intrusion detection.

          - Section 285121 "Detention Monitoring and Control Systems" to integrate video surveillance with detention monitoring interface and control.

      - DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

        - AGC: Automatic gain control.

        - BNC: Bayonet Neill-Concelman - type of connector.

        - B/W: Black and white.

        - CCD: Charge-coupled device.

        - FTP: File transfer protocol.

        - IP: Internet protocol.

        - LAN: Local area network.

        - MPEG: Moving picture experts group.

        - NTSC: National Television System Committee.

        - PC: Personal computer.

        - PTZ: Pan-tilt-zoom.

        - RAID: Redundant array of independent disks.

        - TCP: Transmission control protocol - connects hosts on the Internet.

        - UPS: Uninterruptible power supply.

        - WAN: Wide area network.

      - ACTION SUBMITTALS

        - Product Data: For each type of product indicated. Include dimensions and data on features, performance, electrical characteristics, ratings, and finishes.

Retain first paragraph below if custom equipment, such as operator panels and consoles, is specified in this Section. Coordinate with Drawings.

        - Shop Drawings: For video surveillance. Include plans, elevations, sections, details, and attachments to other work.

          - Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

          - Functional Block Diagram: Show single-line interconnections between components for signal transmission and control. Show cable types and sizes.

          - Dimensioned plan and elevations of equipment racks, control panels, and consoles. Show access and workspace requirements.

          - UPS: Sizing calculations.

Retain subparagraph below if equipment includes wiring.

          - Wiring Diagrams: For power, signal, and control wiring.

        - Design Data: Include an equipment list consisting of every piece of equipment by model number, manufacturer, serial number, location, and date of original installation. Add pretesting record of each piece of equipment, listing name of person testing, date of test, set points of adjustments, name and description of the view of preset positions, description of alarms, and description of unit output responses to an alarm.

      - INFORMATIONAL SUBMITTALS

Retain first paragraph below if required by seismic criteria applicable to Project. Coordinate with Sections specifying electrical supports and seismic controls. See ASCE/SEI 7 for certification requirements for equipment and components.

        - Seismic Qualification Data: Certificates, for cameras, camera-supporting equipment, accessories, and components, from manufacturer.

          - Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

          - Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

          - Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Retain first paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

        - Product Warranty: Sample of special warranty.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For cameras, power supplies, infrared illuminators, monitors, videotape recorders, digital video recorders, video switches, and control-station components to include in emergency, operation, and maintenance manuals. In addition to items specified in Section 017823 "Operation and Maintenance Data," include the following:

          - Lists of spare parts and replacement components recommended to be stored at the site for ready access.

      - PROJECT CONDITIONS

        - Environmental Conditions: Capable of withstanding the following environmental conditions without mechanical or electrical damage or degradation of operating capability:

Retain subparagraphs below; revise conditions and specify features required to provide satisfactory service. See Editing Instruction No. 2 in the Evaluations for discussion of service conditions.

          - Control Station: Rated for continuous operation in ambient temperatures of 60 to 85 deg F (16 to 29 deg C) and a relative humidity of 20 to 80 percent, noncondensing.

          - Interior, Controlled Environment: System components, except central-station control unit, installed in [air-conditioned] [temperature-controlled] interior environments shall be rated for continuous operation in ambient temperatures of [36 to 122 deg F (2 to 50 deg C)] <Insert temperature range> dry bulb and 20 to 90 percent relative humidity, noncondensing. Use NEMA 250, Type 1 enclosures.

          - Interior, Uncontrolled Environment: System components installed in non-[air-conditioned] [temperature-controlled] interior environments shall be rated for continuous operation in ambient temperatures of [0 to 122 deg F (minus 18 to plus 50 deg C)] <Insert temperature range> dry bulb and 20 to 90 percent relative humidity, noncondensing. Use NEMA 250, [Type 3R] [Type 4] [Type 12] [Type 12K] enclosures.

          - Exterior Environment: System components installed in locations exposed to weather shall be rated for continuous operation in ambient temperatures of [minus 30 to plus 122 deg F (minus 34 to plus 50 deg C)] <Insert temperature range> dry bulb and 20 to 90 percent relative humidity, condensing. Rate for continuous operation when exposed to rain as specified in NEMA 250, winds up to 85 mph (137 km/h)[ and snow cover up to 24 inches (610 mm) thick]. Use NEMA 250, [Type 3] [Type 3R] [Type 3S] [Type 4] [Type 4X] enclosures.

          - Hazardous Environment: System components located in areas where fire or explosion hazards may exist because of flammable gases or vapors, flammable liquids, combustible dust, or ignitable fibers shall be rated, listed, and installed according to NFPA 70.

          - Corrosive Environment: System components subject to corrosive fumes, vapors, and wind-driven salt spray in coastal zones. Use NEMA 250, [Type 4X] [Type 6P] enclosures.

          - Security Environment: Camera housing for use in high-risk areas where surveillance equipment may be subject to physical violence.

      - WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

        - Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of cameras, equipment related to camera operation, and control-station equipment that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2 articles.

          - Warranty Period: [Three] <Insert number> years from date of Substantial Completion.

- PRODUCTS

Manufacturers and products listed in SpecAgent and MasterWorks Paragraph Builder are neither recommended nor endorsed by the AIA or Deltek. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - SYSTEM REQUIREMENTS

        - Video-signal format shall comply with NTSC standard, composite interlaced video. Composite video-signal termination shall be 75 ohms.

        - Surge Protection: Protect components from voltage surges originating external to equipment housing and entering through power, communication, signal, control, or sensing leads. Include surge protection for external wiring of each conductor's entry connection to components.

          - Minimum Protection for Power Connections 120 V and More: Auxiliary panel suppressors complying with requirements in Section 264313 "Surge Protection for Low-Voltage Electrical Power Circuits."

          - Minimum Protection for Communication, Signal, Control, and Low-Voltage Power Connections: Comply with requirements in Section 264313 "Surge Protection for Low-Voltage Electrical Power Circuits" as recommended by manufacturer for type of line being protected.

        - Tamper Protection: Tamper switches on enclosures, control units, pull boxes, junction boxes, cabinets, and other system components shall initiate a tamper-alarm signal when unit is opened or partially disassembled. Control-station, control-unit alarm display shall identify tamper alarms and indicate locations.

      - PERFORMANCE REQUIREMENTS

Retain this article with "Seismic Qualification Data" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Verify requirements of authorities having jurisdiction.

        - Seismic Performance: Video surveillance system shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

          - The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

        - Comply with NECA 1.

        - Comply with NFPA 70.

Retain paragraph below if integrating video surveillance system with access-control system.

        - Electronic data exchange between video surveillance system with an access-control system shall comply with SIA TVAC.

      - STANDARD CAMERAS

See the Camera Schedule in the Evaluations. If cameras are scheduled on Drawings, revise camera characteristics accordingly.

        - <Double click here to find evaluate, and insert list of manufacturers and products.>

        - B/W Camera:

Retain first subparagraph below for intrusion-detection units only.

          - Comply with UL 639.

          - Pickup Device: CCD interline transfer, 252,000 [512(H) by 492(V)] <Insert other> pixels.

          - Horizontal Resolution: 380 lines.

          - Signal-to-Noise Ratio: Not less than 46 dB.

          - With AGC, manually selectable on or off.

Retain one of first two subparagraphs below. See the "Cameras and Lenses" Article in the Evaluations for a discussion about specifying camera sensitivity. If retaining first subparagraph, insert light level from manufacturer's data sheet. Light level and f-stop are associated with the camera and do not specify the lens. Specify lens speed in a schedule.

          - Sensitivity: Camera shall provide usable images in low-light conditions, delivering an image at a scene illumination of <Insert light level> lux at f/1.4[, with camera AGC off].

          - Sensitivity: Camera shall deliver 1-V peak-to-peak video signal at the minimum specified light level. Illumination for the test shall be with lamps rated at approximately 2200-K color temperature, and with camera AGC off.

          - Manually selectable modes for backlight compensation or normal lighting.

          - Scanning Synchronization: Determined by external synch over the coaxial cable. Camera shall revert to internally generated synchronization on loss of external synch signal.

          - Motion Detector: Built-in digital.

        - Color Camera:

Retain first subparagraph below for intrusion-detection units only.

          - Comply with UL 639.

          - Pickup Device: CCD interline transfer, 380,000 [771(H) by 492(V)] <Insert other> pixels.

          - Horizontal Resolution: 480 lines.

          - Signal-to-Noise Ratio: Not less than 50 dB, with camera AGC off.

          - With AGC, manually selectable on or off.

Retain one of first two subparagraphs below. See the "Cameras and Lenses" Article in the Evaluations for a discussion about specifying camera sensitivity. If retaining first subparagraph, insert light level and f-stop from manufacturer's data sheet. Light level and f-stop are associated with the camera and do not specify the lens. Specify lens speed in a schedule.

          - Sensitivity: Camera shall provide usable images in low-light conditions, delivering an image at a scene illumination of <Insert light level> lux at <Insert f-stop of lens>[, with camera AGC off].

          - Sensitivity: Camera shall deliver 1-V peak-to-peak video signal at the minimum specified light level. Illumination for the test shall be with lamps rated at approximately 2200-K color temperature, and with camera AGC off.

          - Manually selectable modes for backlight compensation or normal lighting.

          - Scanning Synchronization: Determined by external synch over the coaxial cable. Camera shall revert to internally generated synchronization on loss of external synch signal.

          - White Balance: Auto-tracing white balance, with manually settable fixed balance option.

          - Motion Detector: Built-in digital.

        - Automatic Color Dome Camera: Assembled and tested as a manufactured unit, containing dome assembly, color camera, motorized pan and tilt, zoom lens, and receiver/driver.

Retain first subparagraph below for intrusion-detection units only.

          - Comply with UL 639.

          - Pickup Device: CCD interline transfer, 380,000 [768(H) by 494(V)] <Insert other> pixels.

          - Horizontal Resolution: 480 lines.

          - Signal-to-Noise Ratio: Not less than 50 dB, with camera AGC off.

          - With AGC, manually selectable on or off.

Retain one of first two subparagraphs below. See the "Cameras and Lenses" Article in the Evaluations for a discussion about specifying camera sensitivity. If retaining first subparagraph, insert light level and f-stop from manufacturer's data sheet. Light level and f-stop are associated with the camera and do not specify the lens. Specify lens speed in a schedule.

          - Sensitivity: Camera shall provide usable images in low-light conditions, delivering an image at a scene illumination of <Insert light level> lux at <Insert f-stop of lens>[, with camera AGC off].

          - Sensitivity: Camera shall deliver 1-V peak-to-peak video signal at the minimum specified light level. Illumination for the test shall be with lamps rated at approximately 2200-K color temperature, and with camera AGC off.

          - Manually selectable modes for backlight compensation or normal lighting.

          - Pan and Tilt: Direct-drive motor, 360-degree rotation angle, and 180-degree tilt angle. Pan-and-tilt speed shall be controlled by operator. Movement from preset positions shall be not less than 300 degrees per second.

          - Preset Positioning: Eight user-definable scenes, each allowing 16-character titles. Controls shall include the following:

            - In "sequence mode," camera shall continuously sequence through preset positions, with dwell time and sequencing under operator control.

            - Motion detection shall be available at each camera position.

            - Up to four preset positions may be selected to be activated by an alarm. Each of the alarm positions may be programmed to output a response signal.

          - Scanning Synchronization: Determined by external synch over the coaxial cable. Camera shall revert to internally generated synchronization on loss of external synch signal.

          - White Balance: Auto-tracing white balance, with manually settable fixed balance option.

          - Motion Detector: Built-in digital.

          - Dome shall support multiplexed control communications using coaxial cable recommended by manufacturer.

      - SUBMERSIBLE CAMERAS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Camera: Color, designed for underwater monitoring and for inspecting pipes and storm drains. Attributes as follows:

          - Infrared LEDs to provide illumination in zero-light conditions.

          - 60-foot (18.3-m) factory-installed cable with BNC connector for video and a 2.1-mm jack for 12-V dc power supply.

          - An adjustable swivel mount and attachment base.

          - Pickup Device: CCD interline transfer, 290,000 [500(H) by 580(V)] <Insert other> pixels.

          - Horizontal Resolution: 380 lines.

          - Signal-to-Noise Ratio: Not less than 50 dB.

          - With AGC, from 4 to 39 dB.

          - Sensitivity: Camera shall provide usable images in low-light conditions, delivering an image at a scene illumination of 0.1 lux at f/2.0.

          - Scanning Synchronization: Internal.

          - White Balance: Auto-tracing white balance, for colors ranging from 2800 to 8200 deg K.

      - REINFORCED DOME CAMERAS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Camera: Designed for high-abuse locations, with a weathertight [semirecessed] [surface] mounting, impact-resistance polycarbonate dome, and heavy-gage, 6061 T6 aluminum body.

          - Suitable for exterior environment, rated for continuous operation in ambient temperatures of minus 40 to plus 122 deg F (minus 40 to plus 50 deg C) dry bulb and up to 85 percent relative humidity.

          - Pickup Device: CCD interline transfer, 290,000 [510(H) by 492(V)] <Insert other> pixels.

          - Horizontal Resolution: 350 lines.

          - Signal-to-Noise Ratio: Not less than 46 dB.

          - With AGC and automatic backlight compensation.

          - Sensitivity: Camera shall provide usable images in low-light conditions, delivering an image at a scene illumination of 6 lux at f/2.0.

          - Scanning Synchronization: Determined by external synch over the coaxial cable. Camera shall revert to internally generated synchronization on loss of external synch signal.

          - White Balance: Auto-tracing white balance.

      - LENSES

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Optical-quality coated lens, designed specifically for video-surveillance applications and matched to specified camera. Provide color-corrected lenses with color cameras.

Coordinate subparagraphs below with Drawings. See the Camera Schedule in the Evaluations.

          - Auto-Iris Lens: Electrically controlled iris with circuit set to maintain a constant video level in varying lighting conditions.

          - Fixed Lens: With calibrated focus ring.

          - Zoom Lens: Motorized, remote-controlled unit, rated as "quiet operating." Features include the following:

            - Electrical Leads: Filtered to minimize video signal interference.

            - Motor Speed: Variable.

            - Lens shall be available with preset positioning capability to recall the position of specific scenes.

      - POWER SUPPLIES

        - Low-voltage power supplies matched for voltage and current requirements of cameras and accessories, and of type as recommended by manufacturer of camera[, infrared illuminator,] and lens.

          - Enclosure: NEMA 250, [Type 1] [Type 3] [Type 4X] <Insert type>.

      - INFRARED ILLUMINATORS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

See Editing Instruction No. 3 in the Evaluations for discussion of infrared illuminators and associated cameras.

        - Description: Lighting fixtures that emit light only in the infrared spectrum, suitable for use with cameras indicated, for nighttime surveillance, without emitting visible light.

          - Field-Selectable Beam Patterns: Narrow, medium, and wide.

          - Rated Lamp Life: More than 8000 hours.

          - Power Supply: [12-V ac/dc] [120-V ac].

Retain first paragraph below if areas are not shown on Drawings.

        - Area Coverage: Illumination to 150 feet (50 m) in a narrow beam pattern.

See Editing Instruction No. 2 in the Evaluations for discussion of ambient conditions.

        - Exterior housings shall be suitable for same environmental conditions as the associated camera.

      - CAMERA-SUPPORTING EQUIPMENT

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain first paragraph below if Project is in a seismic area. Revise to insert wind and seismic loads to be carried by housings, illuminators, and pan-and-tilt units.

        - Minimum Load Rating: Rated for load in excess of the total weight supported times a minimum safety factor of two.

        - Pan Units: Motorized automatic-scanning units arranged to provide remote-controlled manual and automatic camera panning action, and equipped with matching mounting brackets.

          - Scanning Operation: Silent, smooth, and positive.

          - Stops: Adjustable without disassembly, to limit the scanning arc.

        - Pan-and-Tilt Units: Motorized units arranged to provide remote-controlled aiming of cameras with smooth and silent operation, and equipped with matching mounting brackets.

          - Panning Rotation: 0 to 355 degrees, with adjustable stops.

          - Tilt Movement: 90 degrees, plus or minus 5 degrees, with adjustable stops.

          - Speed: 12 degrees per second in both horizontal and vertical planes.

          - Wiring: Factory prewired for camera and zoom lens functions and pan-and-tilt power and control.

Retain first subparagraph below to require displaying pan-and-tilt information at control station. Delete optional text if heater is provided in camera enclosure.

          - Built-in encoders or potentiometers for position feedback[, and thermostat-controlled heater].

Retain subparagraph below if any pan-and-tilt unit is remotely controlled and is scheduled with computer-controlled preset positioning feature.

          - Pan-and-tilt unit shall be available with preset positioning capability to recall the position of a specific scene.

Coordinate first paragraph below with Drawings.

        - Mounting Brackets for Fixed Cameras: Type matched to items supported and mounting conditions. Include manual pan-and-tilt adjustment.

        - Protective Housings for Fixed and Movable Cameras: Steel[ or 6061 T6 aluminum] enclosures with internal camera mounting and connecting provisions that are matched to camera/lens combination and mounting and installing arrangement of camera to be housed.

Retain first subparagraph below if part of intrusion-detection system. Coordinate requirements with Section 283100 "Intrusion Detection."

          - Tamper switch on access cover sounds an alarm signal when unit is opened or partially disassembled. Central-control unit shall identify tamper alarms and indicate location in alarm display. Tamper switches and central-control unit are specified in Section 283100 "Intrusion Detection."

          - Camera Viewing Window: [Polycarbonate] [Lexan] window, aligned with camera lens.

          - Duplex Receptacle: Internally mounted.

          - Alignment Provisions: Camera mounting shall provide for field aiming of camera and permit removal and reinstallation of camera lens without disturbing camera alignment.

          - Built-in, thermostat-activated [heater] [and] [blower] units. Units shall be automatically controlled so the environmental limits of the camera equipment are not exceeded.

          - Sun shield shall not interfere with normal airflow around the housing.

          - Mounting bracket and hardware for wall or ceiling mounting of the housing. Bracket shall be of same material as the housing; mounting hardware shall be stainless steel.

          - Finish: Housing and mounting bracket shall be factory finished using manufacturer's standard finishing process suitable for the environment.

See Editing Instruction No. 4 in the Evaluations for discussion of enclosure ratings.

          - Enclosure Rating: <Insert NEMA Type designation> <Insert Ingress Protection code designation>.

      - MONITORS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Monochrome:

          - Metal cabinet units designed for continuous operation.

Retain first subparagraph below if screen size is not indicated on Drawings.

          - Screen Size (Diagonal Dimension): <Insert dimension>.

          - Horizontal Resolution: [600] <Insert resolution> lines, minimum, at center.

          - Minimum Front Panel Devices and Controls: Power switch; power-on indicator; and brightness, horizontal-hold, vertical-hold, and contrast controls.

          - Mounting: Adjustable tilting and training.

          - Mounting: [Single, 14-inch (356-mm)] [Dual, 9-inch (229-mm)], vertical, EIA 19-inch (483-mm) electronic equipment rack or cabinet complying with CEA 310-E.

          - Electrical: 120-V ac, 60 Hz.

        - Color:

          - Metal cabinet units designed for continuous operation.

Retain first subparagraph below if screen size is not indicated on Drawings.

          - Screen Size (Diagonal Dimension): <Insert dimension>.

          - Horizontal Resolution: [300] <Insert resolution> lines.

          - Minimum Front Panel Devices and Controls: Power switch; power-on indicator; and brightness, contrast, color, and tint controls.

          - Degaussing: Automatic.

          - Mounting: [Single, 14-inch (356-mm)] [Dual, 9-inch (229-mm)], vertical, EIA 19-inch (483-mm) electronic equipment rack or cabinet complying with CEA 310-E.

          - Electrical: 120-V ac, 60 Hz.

      - VIDEOTAPE RECORDERS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Industrial, time-lapse type recorder, designed for continuous operation. Tape format is 1/2 inch (13 mm) using industrial-grade, T-120 cassettes.

          - Horizontal Resolution: 400 lines, minimum.

          - Recording Heads: Rotary-scan type.

          - Integral Timer: Permits programming of recording operation for adjustable daily and weekly periods.

          - Time-Lapse Operating Modes: Multiple, covering 24 to 240 hours, minimum.

          - Other Operating Modes:

            - Manual play and recording at two- and six-hour speeds.

            - Forward and reverse high-speed search.

            - Reverse, slow, and single-frame play.

          - Alarm Recording: Operating mode is automatically switched from time-lapse to two- or six-hour recording mode when an externally generated alarm signal is received.

          - Audio Recording: 70 to 7000 Hz. Phono and microphone input; phono output.

          - Time and Date Generator: Records time and date legend in corner of recorded scenes.

          - Tape Counter: Displays tape position.

          - Manual Recording Lock: Key or keypad operated. Prevents unauthorized tampering or control changes during preset operation.

          - Signal-to-Noise Ratio: 45 dB for video output in standard play mode.

Coordinate subparagraph below with Drawings.

          - Mounting: Standard 19-inch (483-mm) rack complying with CEA 310-E, or freestanding desktop.

      - DIGITAL VIDEO RECORDERS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Digital, time-lapse type, full-frame and motion recorder, with removable hard drive.

          - Recording Time: 400 hours minimum.

          - Resolution: 720 by 480 lines, minimum.

          - Programming shall be from trackball and push buttons on face of the recorder, settings shall be displayed on any video monitor connected to the recorder. Programming shall include the following:

            - Motion analysis graph.

            - Password protection.

            - Alarm and timer controls.

            - Continuous recording option.

            - Time-lapse operating modes.

            - Search video by time, event, or motion.

          - Programming: SmartMedia card for software updating, image archiving, and image transfer to a PC.

          - Storage: [80-GB] <Insert size>, removable hard drive. Software shall permit hot-swapping drives.

          - Compression: [MPEG-2] <Insert type>.

          - Time and Date Generator: Records time (hr:min:sec) and date legend of each frame.

          - Audio Recording: 70 to 7000 Hz. Phono and microphone input; phono output.

Coordinate subparagraph below with Drawings.

          - Mounting: Standard 19-inch (483-mm) rack complying with CEA 310-E, or freestanding desktop.

      - NETWORK VIDEO RECORDERS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - External storage or internal 250-1, 500-GB hard disk drive.

          - Video and audio recording over TCP/IP network.

          - Video recording of MPEG-2 and MPEG-4 streams.

          - Video recording up to 48 Mbps for internal storage and up to 100 Mbps for external storage.

          - Duplex Operation: Simultaneous recording and playback.

          - Continuous and alarm-based recording.

          - Full-Featured Search Capabilities: Search based on camera, time, or date.

          - Automatic data replenishment to ensure recording even if network is down.

          - Digital certification by watermarking.

          - Internal RAID storage or non-RAID storage of up to 1500 GB.

          - Capable of adding external RAID storage up to 7000 GB for models with no internal storage.

          - Full integration with LAN, Intranet, or Internet through standard Web browser or video management software.

          - Integrated Web server FTP server functionality.

          - Supports up to 16[, 32,] or [64] <Insert number> devices.

      - DIGITAL SWITCHERS

In small systems, a digital switcher may be integral in the monitor or may be another component. Coordinate this article with Drawings.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Quad Switch: For displaying images from four cameras on a single monitor. Provide color switcher if one or more cameras or monitors are in color.

          - Controls: Unit-mounted front panel.

          - Resolution: [720 by 480] lines <Insert resolution>.

          - Modes: Auto, manual, and alarm. In manual mode, each channel can also be viewed in single display mode. In the event of an alarm, alarming channel shall automatically switch to full screen. If several alarms are activated, channels in alarm shall be in auto-switching mode.

          - Channel Loss Alarm: Audible buzzer; occurrence details shall be recorded.

          - Time: Indicate date and time.

          - Timing of Auto-Switcher: 1 to 30 seconds, selectable.

          - Mounting: Standard 19-inch (483-mm) rack complying with CEA 310-E, or freestanding desktop.

        - Manual Switch Bank: Low-loss, high-isolation, multiple-video switch to allow manual switching of multiple quad switches and cameras to a single output. Switches shall be illuminated.

        - Sequential Switchers: Automatically sequence outputs of multiple cameras to single monitor and videotape recorder.

          - Switching Time Interval: Continuously adjustable, 5 to 20 seconds minimum, with manual override.

          - Skip-Sequential-Hold Switch: One for each camera, with LED to indicate active camera.

          - Camera Identification Legend: Either on-screen message or label at skip-sequential switch.

          - Alarm Switching: In the event of an alarm, alarming channel shall automatically switch the monitor to full screen.

          - Mounting: Standard 19-inch (483-mm) rack complying with CEA 310-E.

Revise paragraph below if only one camera is controlled.

        - PTZ Controls: Arranged for multiple-camera control, with switches to select camera to be controlled.

          - Pan-and-Tilt Control: Joystick type.

          - Zoom Control: Momentary-contact, "in-out" push button.

          - Automatic-Scan Control: A push button for each camera with pan capability that places camera in automatic-scanning mode.

      - IP VIDEO SYSTEMS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description:

          - System shall provide high-quality delivery and processing of IP-based video, audio, and control data using standard Ethernet-based networks.

          - System shall have seamless integration of all video surveillance and control functions.

          - Graphical user interface software shall manage all IP-based video matrix switching and camera control functions, two-way audio communication, alarm monitoring and control, and recording and archive/retrieval management. IP system shall also be capable of integrating into larger system environments.

          - System design shall include all necessary compression software for high-performance, dual-stream, MPEG-2/MPEG-4 video. Unit shall provide connections for all video cameras, camera PTZ control data, bidirectional audio, discreet sensor inputs, and control system outputs.

          - All camera signals shall be compressed, encoded, and delivered onto the network for processing and control by the IP video-management software.

          - Camera system units shall be ruggedly built and designed for extreme adverse environments, complying with NEMA Type environmental standards.

          - Encoder/decoder combinations shall place video, audio, and data network stream that can be managed from multiple workstations on the user's LAN or WAN.

          - All system interconnect cables, workstation PCs, PTZ joysticks, and network intermediate devices shall be provided for full performance of specified system.

      - VIDEO MOTION SENSORS (INTERIOR)

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Device Performance: Detect changes in video signal within a user-defined protected zone. Video inputs shall be composite video as defined in SMPTE 170M. Provide an alarm output for each video input.

          - Detect movement within protected zone of intruders wearing clothing with a reflectivity that differs from that of background scene by a factor of two. Reject all other changes in video signal.

          - Modular design that allows for expansion or modification of number of inputs.

          - Controls:

            - Size of detection zones.

            - Sensitivity of detection of each protected zone.

          - Mounting: Standard 19-inch (483-mm) rack complying with CEA 310-E.

      - CONTROL STATIONS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Heavy-duty, freestanding, modular, metal furniture units arranged to house electronic equipment. Coordinate component arrangement and wiring with components and wiring of other systems.

        - Equipment Mounting: Standard 19-inch (483-mm) rack complying with CEA 310-E.

        - Normal System Power Supply: 120 V, 60 Hz, through a locked disconnect device and an isolation transformer in central-station control unit. Central-station control unit shall supply power to all components connected to it unless otherwise indicated.

Retain first paragraph below if UPS is not specified for central-station control units and central-station control-unit hardware.

        - Power Continuity for Control Station: Batteries in power supplies of central-station control units and individual system components shall maintain continuous system operation during outages of both normal and backup ac system supply.

          - Batteries: Rechargeable, valve-regulated, recombinant, sealed, lead-acid type with nominal 10-year life expectancy. Capacity adequate to operate portions of system served including audible trouble signal devices for up to four hours and audible and visual alarm devices under alarm conditions for an additional 10 minutes.

          - Battery Charger: Solid-state, fully automatic, variable-charging-rate type. Charger shall recharge fully discharged battery within 24 hours.

        - Annunciation: Indicate change in system condition and switching of system or component to backup power.

      - SIGNAL TRANSMISSION COMPONENTS

        - Cable: Coaxial cable elements have 75-ohm nominal impedance. Comply with requirements in Section 26519 "Low-Voltage Electrical Power Conductors and Cables."

        - Video Surveillance Coaxial Cable Connectors: BNC type, 75 ohms. Comply with requirements in Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

- EXECUTION

      - EXAMINATION

        - Examine pathway elements intended for cables. Check raceways and other elements for compliance with space allocations, installation tolerance, hazards to camera installation, and other conditions affecting installation.

        - Examine roughing-in for LAN, WAN, and IP network before device installation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - WIRING

Retain one of first two paragraphs below. Delete both if wiring method is indicated on Drawings.

        - Comply with requirements in Section 270528 "Pathways for Communications Systems."

        - Wiring Method: Install cables in raceways unless otherwise indicated.

Retain one or both of first two subparagraphs below to make exceptions to the wiring method specified above.

          - Except raceways are not required in accessible indoor ceiling spaces and attics.

          - Except raceways are not required in hollow gypsum board partitions.

          - Conceal raceways and wiring except in unfinished spaces.

        - Wiring within Enclosures: Bundle, lace, and train conductors to terminal points with no excess and without exceeding manufacturer's limitations on bending radii. Provide and use lacing bars and distribution spools.

        - Splices, Taps, and Terminations: For power and control wiring, use numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures. Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values. If manufacturer's torque values are not indicated, use those specified in UL 486A-486B.

        - For communication wiring, comply with the following:

          - Section 271313 "Communications Copper Backbone Cabling."

          - Section 271323 "Communications Optical Fiber Backbone Cabling."

          - Section 271333 "Communications Coaxial Backbone Cabling."

          - Section 271513 "Communications Copper Horizontal Cabling."

          - Section 271523 "Communications Optical Fiber Horizontal Cabling."

          - Section 271533 "Communications Coaxial Horizontal Cabling."

Retain paragraph below only if required by manufacturer. Show independent-signal circuit-grounding methods and details on Drawings.

        - Grounding: Provide independent-signal circuit grounding recommended in writing by manufacturer.

      - VIDEO SURVEILLANCE SYSTEM INSTALLATION

        - Install cameras and infrared illuminators level and plumb.

Coordinate first paragraph below with Drawings.

        - Install cameras with 84-inch- (2134-mm-) minimum clear space below cameras and their mountings. Change type of mounting to achieve required clearance.

        - Set pan unit and pan-and-tilt unit stops to suit final camera position and to obtain the field of view required for camera. Connect all controls and alarms, and adjust.

        - Install power supplies and other auxiliary components at control stations unless otherwise indicated.

Retain first paragraph below if not indicated on Drawings, or coordinate with Drawings, schedules, and other Sections. Indicate which components are to be fitted with tamper switches and which Section covers tamper-switch connection.

        - Install tamper switches on components indicated to receive tamper switches, arranged to detect unauthorized entry into system-component enclosures and mounted in self-protected, inconspicuous positions.

        - Avoid ground loops by making ground connections only at the control station.

          - For 12- and 24-V dc cameras, connect the coaxial cable shields only at the monitor end.

        - Identify system components, wiring, cabling, and terminals according to Section 270553 "Identification for Communications Systems."

      - FIELD QUALITY CONTROL

Retain first paragraph below to identify who shall perform tests and inspections. If retaining second option in first paragraph, or if retaining second or third paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain first paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

        - Manufacturer's Field Service: Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.

Retain first paragraph below to require Contractor to perform tests and inspections.

        - Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

          - Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph below to describe tests and inspections to be performed.

        - Tests and Inspections:

          - Inspection: Verify that units and controls are properly installed, connected, and labeled, and that interconnecting wires and terminals are identified.

          - Pretesting: Align and adjust system and pretest components, wiring, and functions to verify that they comply with specified requirements. Conduct tests at varying lighting levels, including day and night scenes as applicable. Prepare video-surveillance equipment for acceptance and operational testing as follows:

            - Prepare equipment list described in "Informational Submittals" Article.

            - Verify operation of auto-iris lenses.

            - Set back-focus of fixed focal length lenses. At focus set to infinity, simulate nighttime lighting conditions by using a dark glass filter of a density that produces a clear image. Adjust until image is in focus with and without the filter.

            - Set back-focus of zoom lenses. At focus set to infinity, simulate nighttime lighting conditions by using a dark glass filter of a density that produces a clear image. Additionally, set zoom to full wide angle and aim camera at an object 50 to 75 feet (17 to 23 m) away. Adjust until image is in focus from full wide angle to full telephoto, with the filter in place.

            - Set and name all preset positions; consult Owner's personnel.

            - Set sensitivity of motion detection.

            - Connect and verify responses to alarms.

            - Verify operation of control-station equipment.

          - Test Schedule: Schedule tests after pretesting has been successfully completed and system has been in normal functional operation for at least 14 days. Provide a minimum of 10 days' notice of test schedule.

          - Operational Tests: Perform operational system tests to verify that system complies with Specifications. Include all modes of system operation. Test equipment for proper operation in all functional modes.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Video surveillance system will be considered defective if it does not pass tests and inspections.

        - Prepare test and inspection reports.

      - ADJUSTING

        - Occupancy Adjustments: When requested within [12] <Insert number> months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions. Provide up to [two] <Insert number> visits to Project during other-than-normal occupancy hours for this purpose. Tasks shall include, but are not limited to, the following:

          - Check cable connections.

          - Check proper operation of cameras and lenses. Verify operation of auto-iris lenses and adjust back-focus as needed.

          - Adjust all preset positions; consult Owner's personnel.

          - Recommend changes to cameras, lenses, and associated equipment to improve Owner's use of video surveillance system.

          - Provide a written report of adjustments and recommendations.

      - CLEANING

        - Clean installed items using methods and materials recommended in writing by manufacturer.

        - Clean video-surveillance-system components, including camera-housing windows, lenses, and monitor screens.

      - DEMONSTRATION

        - [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain video-surveillance equipment.

END OF SECTION 282000