Copyright 2018 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 283121 - AREA AND PERIMETER INTRUSION DETECTION

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Perimeter detection and alarm system.

Delete subparagraph below for standalone systems with no systems integration and for other projects with prime responsibility for systems integration specified in another Section. For discussion of this concept, see "Systems Integration" Article in the Evaluations.

          - Integration of other electronic and electrical systems and equipment.

        - Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 271313 "Communications Copper Backbone Cabling" for Category 5e, 6, and 7 backbone (riser-rated) cabling.

          - Section 271323 "Communications Optical Fiber Backbone Cabling" for multi- and single-mode backbone (riser-rated) optical fiber.

          - Section 271513 "Communications Copper Horizontal Cabling" for Category 5e, 6, and 7 horizontal (general use, riser-, and plenum-rated) cabling.

          - Section 271523 "Communications Optical Fiber Horizontal Cabling" for multi- and single-mode horizontal (general use, riser-, and plenum-rated) optical fiber.

          - Section 260519 "Low-Voltage Electrical Power Conductors and Cables" for cabling between master control units and field-mounted devices and control units.

      - DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

        - CCTV: Closed-circuit television.

        - EMI: Electromagnetic interference.

        - PIR: Passive infrared.

        - RFI: Radio-frequency interference.

        - UPS: Uninterruptible power supply.

        - Control Unit: System component that monitors inputs and controls outputs through various circuits.

        - Master Control Unit: System component that accepts inputs from other control units and may also perform control-unit functions. The unit has limited capacity for the number of protected zones and is installed at an unattended location or at a location where it is not the attendant's primary function to monitor the security system.

        - Monitoring Station: Facility that receives signals and has personnel in attendance at all times to respond to signals. A central station is a monitoring station that is listed.

        - Protected Zone: A protected premises or an area within a protected premise that is provided with means to prevent an unwanted event.

In first paragraph below, adjust standard intruder's height, weight, and clothing to suit Project.

        - Standard Intruder: A person who weighs 100 lb (45 kg) or less and whose height is 60 inches (1525 mm) or less; dressed in a long-sleeved shirt, slacks, and shoes[ unless environmental conditions at the site require protective clothing].

In first paragraph below, adjust standard-intruder movement to suit Project.

        - Standard-Intruder Movement: Any movement, such as walking, running, crawling, rolling, or jumping, of a "standard intruder" in a protected zone.

Retain first paragraph below if systems integration is specified in this Section.

        - Systems Integration: The bringing together of components of several systems containing interacting components to achieve indicated functional operation of combined systems.

        - Zone. A defined area within a protected premise. It is a space or area for which an intrusion must be detected and uniquely identified. The sensor or group of sensors must then be assigned to perform the detection, and any interface equipment between sensors and communication must link to master control unit.

      - ACTION SUBMITTALS

        - Product Data: Components for sensing, detecting[, systems integration], and control, including dimensions and data on features, performance, electrical characteristics, ratings, and finishes.

Retain first paragraph below if custom equipment, such as operator panels and consoles, is specified in this Section. Revise to suit Project and coordinate with Drawings.

        - Shop Drawings: Detail assemblies of standard components that are custom assembled for specific application on this Project.

Retain first subparagraph below for integration with systems in other Sections.

          - Functional Block Diagram: Show single-line interconnections between components including interconnections between components specified in this Section and those furnished under other Sections. Indicate methods used to achieve systems integration. Indicate control, signal, and data communication paths and identify [programmable logic controllers] [networks] [and] control interface devices and media to be used. Describe characteristics of network and other data communication lines.

Retain first four subparagraphs below if systems integration is specified in this Section.

            - Indicate methods used to achieve systems integration.

            - Indicate control, signal, and data communication paths and identify PLCs, networks, control interface devices, and media to be used.

            - Describe characteristics of network and other data communication lines.

            - Describe methods used to protect against power outages and transient voltages including types and ratings of isolation and surge suppression devices used in data, communication, signal, control, and ac and dc power circuits.

          - Raceway Riser Diagrams: Detail raceway runs required for perimeter security[ and for systems integration]. Include designation of devices connected by raceway, raceway type and size, and type and size of wire and cable fill for each raceway run.

          - UPS: Sizing calculations.

Retain first subparagraph below for projects where conduit and cable routing is critical but only device locations are shown on Drawings.

          - Site and Floor Plans: Indicate final outlet and device locations, routing of raceways, and cables inside and outside the building.[ Include room layout for master control-unit console, terminal cabinet, racks, and UPS.]

          - Master Control-Unit Console Layout: Show required artwork and device identification.

Retain first subparagraph below for addressable systems.

          - Device Address List: Coordinate with final system programming.

          - System Wiring Diagrams: Include system diagrams unique to Project. Show connections for all devices, components, and auxiliary equipment. Include diagrams for equipment and for system with all terminals and interconnections identified.

Surge protection is required by NFPA 731.

          - Details of surge protection.

          - Sensor detection patterns and adjustment ranges.

        - Design Data: Include method of operation and supervision of each component and each type of circuit. Show sequence of operations for manually and automatically initiated system or equipment inputs. Description must cover this specific Project; manufacturer's standard descriptions for generic systems are unacceptable.

        - Samples for Initial Selection: For units with factory-applied color finishes.

Delete "Samples for Initial Selection" Paragraph above if colors and other characteristics are preselected and specified or scheduled. Retain first paragraph below with or without above.

        - Samples for Verification: For each type of exposed finish required.

      - INFORMATIONAL SUBMITTALS

Coordinate first paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as supplemented in "Quality Assurance" Article.

        - Qualification Data: For [Installer] [security systems integrator] [testing agency].

Retain first paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

          - Anchor inspection reports documenting inspections of built-in and cast-in anchors.

        - Product Warranty: Sample of special warranty.

        - Field Test Reports: Test plan and report defining all tests required to ensure that system meets technical, operational, and performance specifications within [60 days] <Insert number> of date of Contract award.

        - Evaluation Reports: Examination reports documenting inspections of substrates, areas, and conditions.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For perimeter security system to include in emergency, operation, and maintenance manuals. In addition to items specified in Section 017823 "Operation and Maintenance Data," include the following:

          - Data for each type of product, including features and operating sequences, both automatic and manual.

          - Master control-unit hardware and software data.

      - MAINTENANCE MATERIAL SUBMITTALS

        - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - [One] <Insert number> spare control-unit board(s) for strain-sensitive cable system and [one] <Insert number> cable repair and splice kit(s).

          - [One] <Insert number> of each type of microwave sensor and one of each type of power supply for microwave perimeter security system.

          - [One] <Insert number> of each spare sensor and PIR unit and [one] <Insert number> alignment telescope(s) for long-range PIR system.

          - [One] <Insert number> spare control-unit board(s) for electrostatic-field system.

          - [One] <Insert number> spare control-unit board(s) for buried, ported coaxial cable system, 10 feet (3 m) of cable; and [one] <Insert number> cable repair and splice kit(s).

          - Fuses: [Three] <Insert number> of each kind and size.

          - Tool Kit: Provide [six] <Insert number> sets of tools for use with security fasteners, each packaged in a compartmented kit configured for easy handling and storage.

          - Security Fasteners: Furnish no fewer than [1 box for every 50] <Insert numbers> boxes or fraction thereof, of each type and size of security fastener installed.

      - QUALITY ASSURANCE

        - Installer Qualifications:

          - An employer of workers, at least one of whom is a technician certified by the National Burglar & Fire Alarm Association.

          - Manufacturer's authorized representative who is trained and approved for installation of units required for this Project.

          - Layout Responsibility: Preparation of Shop Drawings[ and cabling administration Drawings][, cabling administration Drawings, and field testing program development] by [an RCDD] [a Technician].

          - Installation Supervision: Installation shall be under the direct supervision of [Technician] [Level 2 Commercial Installer], who shall be present at all times when Work of this Section is performed at Project site.

Delete "Testing Supervisor" Subparagraph below if Contractor performs field quality-control testing.

          - Testing Supervisor: Currently certified by BICSI as [an RCDD] [a Technician] to supervise on-site testing.

Retain "Testing Agency Qualifications" Paragraph below if Contractor or manufacturer selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article. Qualification requirements are in addition to those specified in Section 014000 "Quality Requirements."

        - Testing Agency Qualifications: Certified by BICSI.

          - Testing Agency's Field Supervisor: Currently certified by BICSI as an RCDD to supervise on-site testing.

Retain first paragraph below if systems integration is specified in this Section.

        - Security Systems Integrator Qualifications: An experienced perimeter security equipment supplier[ and Installer] who has completed systems integration work for installations similar in material, design, and extent to that indicated for this Project, whose work has resulted in construction with a record of successful in-service performance.

      - PROJECT CONDITIONS

        - Environmental Conditions: Capable of withstanding the following environmental conditions without mechanical or electrical damage or degradation of operating capability:

Retain and revise conditions below and specify features required to provide satisfactory service. See Editing Instruction No. 2 in the Evaluations.

          - Altitude: Sea level to [4000 feet (1220 m)] <Insert elevation>.

          - Master Control Unit: Rated for continuous operation in an ambient of 60 to 85 deg F (16 to 29 deg C) and a relative humidity of 20 to 80 percent, noncondensing.

          - Exterior Environment: System components installed in locations exposed to weather shall be rated for continuous operation in ambients of [minus 30 to plus 122 deg F (minus 34 to plus 50 deg C)] <Insert temperature range> dry bulb and 20 to 90 percent relative humidity, condensing. Comply with UL 294 and UL 639 for outdoor-use equipment. Rate for continuous operation when exposed to rain as specified in NEMA 250, winds up to [85 mph (137 km/h)] [and snow cover up to 24 inches (610 mm) thick].

          - Hazardous Environment: System components located in areas where fire or explosion hazards may exist because of flammable gases or vapors, flammable liquids, combustible dust, or ignitable fibers or flyings shall be rated, listed, and installed according to NFPA 70.

      - WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

        - Special Warranty: Manufacturer's standard form in which manufacturer and Installer agree to repair or replace components of perimeter security devices and equipment that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2 articles. One-year warranty is industry standard for perimeter security devices and equipment; some manufacturers provide two-year warranties if requested.

          - Warranty Period: [Two] <Insert number> years from date of Substantial Completion.

- PRODUCTS

      - FUNCTIONAL DESCRIPTION OF SYSTEM

        - Description: Perimeter protection system with [fence-mounted systems] [buried sensors] [volumetric detectors] integrated into a single perimeter detection and alarm system.

        - Supervision: System components shall be continuously monitored for normal, alarm, [supervisory, ]and trouble conditions. Indicate deviations from normal conditions at any location in system. Indication includes identification of device or circuit in which deviation has occurred and whether deviation is an alarm or malfunction.

          - Alarm Signal: Display at master control unit and actuate audible and visual alarm devices.

          - Trouble Condition Signal: Distinct from other signals, indicating that system is not fully functional. Trouble signal shall indicate system problems such as battery failure, open or shorted transmission line conductors, or control-unit failure.

Retain subparagraph below if retaining "supervisory," option in paragraph above.

          - Supervisory Condition Signal: Distinct from other signals, indicating an abnormal condition as specified for the particular device or control unit.

Retain one of two "System Control" paragraphs below. See "Control Units" Article in the Evaluations.

        - System Control: Master control unit shall directly monitor gate detection devices, perimeter detection units, and connecting wiring.

        - System Control: One or more remote, addressable control units operate under control of a master control-unit microcomputer in a multiplexed distributed control system or as part of a network. Control units shall receive programming by multiplexed signal transmission from the associated master control unit and hold data in nonvolatile memory. System shall automatically reboot program without error or loss of status or alarm data after any system disturbance.

        - Operator Commands:

Subparagraphs below are optional. Retain subparagraphs required for Project. Coordinate with operator commands listed for "Master Control Unit" Article. Delete nonapplicable commands.

          - Help with System Operation: Display all commands available to operator. Help command, followed by a specific command, shall produce a short explanation of the purpose, use, and system reaction to that command.

          - Acknowledge Alarm: To indicate that alarm message has been observed by operator.

          - Place Protected Zone in Access: Disable all intrusion-alarm circuits of a specific protected zone. Tamper circuits may not be disabled by operator.

          - Place Protected Zone in Secure: Activate all intrusion-alarm circuits of a protected zone.

          - Protected Zone Test: Initiate operational test of a specific protected zone.

          - System Test: Initiate system-wide operational test.

          - Print reports.

Coordinate function in first paragraph below with timing device specified in "Master Control Unit" Article.

        - Timed Control at Master Control Unit: Allow automatically timed "secure" and "access" functions of selected protected zones.

Retain first paragraph below if alarm signals control lights, intercom, sound, or CCTV components. Revise to suit Project design and systems integration specifications. Coordinate with Drawings.

        - Automatic Control of Related Systems: Alarm or supervisory signals from certain perimeter security devices control the following functions in related systems:

          - Switch selected lights.

          - Open a signal path between certain intercommunication stations.

          - Shift sound system to "listening mode" and open a signal path to certain system speakers.

          - Switch signal to selected monitor from CCTV camera in vicinity of sensor signaling an alarm.

          - <Insert description of automatic control required>.

Retain first paragraph below for system with printer.

        - Printed Record of Events: Print a record of alarm, supervisory, and trouble events on system printer. Sort and report by protected zone, device, and function. When master control unit receives a signal, print a report of alarm, supervisory, or trouble condition. Report type of signal (alarm, supervisory, or trouble), control-unit address, protected zone description, date, and time of occurrence. Differentiate alarm signals from other indications. When system is reset, report reset event with the same information concerning device, location, date, and time. Commands shall initiate the reporting of a list of current alarm, supervisory, and trouble conditions in system or a log of past events.

Two-second maximum time in first paragraph below applies to hard-wired systems. Multiplexed systems may require longer times.

        - Response Time: [Two] <Insert number> seconds between actuation of any alarm and its indication at master control unit.

        - Circuit Supervision: Supervise all signal and data transmission lines, links with other systems, control units, and sensors from master control unit. Indicate circuit and detection device faults with both protected zone and trouble signals, sound a distinctive audible tone, and illuminate an LED. Maximum permissible elapsed time between occurrence of a trouble condition and indication at master control unit is 20 seconds. Initiate an alarm in response to opening, closing, shorting, or grounding of a signal or data transmission line.

"Programmed Secure-Access Control" Paragraph below is an optional feature. Coordinate with Drawings.

        - Programmed Secure-Access Control: System shall be programmable to automatically change status of various combinations of protected zones between secure and access conditions at scheduled times. Status changes may be preset for repetitive, daily, and weekly; specially scheduled operations may be preset up to a year in advance. Manual secure-access control stations shall override programmed settings.

        - Manual Secure-Access Control: Coded entries at manual stations shall change status of associated protected zone between secure and access conditions.

      - SYSTEM COMPONENT REQUIREMENTS

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

        - Control Units, Devices, and Communications to Monitoring Station: Listed and labeled by a qualified testing agency for compliance with SIA CP-01.

Retain first paragraph below if Owner requires FM Global approval.

        - FM Global Compliance: FM-Approved and -labeled perimeter security devices and equipment.

        - Comply with NFPA 70.

Retain first paragraph below if systems integration is required. If retaining, identify equipment and Section that specifies integrated system console.

        - Compatibility: Detection devices and their communication features, connecting wiring, and master control unit shall be selected and configured with accessories for full compatibility with the following equipment:

          - Door hardware specified in Section 087100 "Door Hardware."

          - Door hardware specified in Section 087111 "Door Hardware (Descriptive Specification)."

          - Lighting controls specified in Section 260923 "Lighting Control Devices."

          - Lighting controls specified in Section 260943.16 "Addressable-Luminaire Lighting Controls" and Section 260943.23 "Relay-Based Lighting Controls."

          - Intercom and program systems specified in Section 275123.20 "Commercial Intercommunications and Program Systems."

          - Intercom and program systems specified in Section 275123.50 "Educational Intercommunications and Program Systems."

          - Access control system specified in Section 281300 "Access Control System Software and Database Management."

          - Intrusion detection system specified in Section 283100 "Intrusion Detection."

          - Video surveillance system specified in Section 282000 "Video Surveillance."

          - <Insert system or equipment> specified in Section <Insert Section number> "<Insert Section title>."

        - Perimeter Security Units: Listed and labeled by a qualified testing agency for compliance with UL 639.

        - Surge Protection: Protect components from voltage surges originating external to equipment housing and entering through power, communication, signal, control, or sensing leads. Include surge protection for external wiring of each conductor entry connection to components.

          - Minimum Protection for Power Lines 120 V and More: Auxiliary panel suppressors complying with requirements in Section 264313 "Surge Protection for Low-Voltage Electrical Power Circuits."

          - Minimum Protection for Communication, Signal, Control, and Low-Voltage Power Lines: Listed and labeled by a qualified testing agency for compliance with NFPA 731.

        - Interference Protection: Components shall be unaffected by radiated RFI and electrical induction of 15 V/m over a frequency range of 10 to 10,000 MHz and conducted interference signals up to 0.25-V rms injected into power supply lines at 10 to 10,000 MHz.

Coordinate first paragraph below with Drawings and Specifications of each component.

        - Tamper Protection: Tamper switches on detection devices, control units, annunciators, pull boxes, junction boxes, cabinets, and other system components shall initiate a tamper-alarm signal when unit is opened or partially disassembled and when entering conductors are cut or disconnected. Master control-unit alarm display shall identify tamper alarms and indicate locations.

Coordinate first three paragraphs below with Drawings and with features specified for master control unit. Indicate features in a device schedule.

        - Self-Testing Devices: Automatically test themselves periodically, but not less than once per hour, to verify normal device functioning and alarm initiation capability. Devices transmit test failure to master control unit.

        - Antimasking Devices: Automatically check operation continuously or at intervals of a minute or less, and use signal-processing logic to detect blocking, masking, jamming, tampering, or other operational dysfunction. Devices transmit detection of operational dysfunction to master control unit as an alarm signal.

        - Addressable Devices: Transmitter and receivers shall communicate unique device identification and status reports to master control unit.

Retain paragraph below if specifying remotely adjustable detectors.

        - Remote-Controlled Devices: Individually and remotely adjustable for sensitivity and individually monitored at master control unit for calibration, sensitivity, and alarm condition.

      - ENCLOSURES

        - Interior Electronics: NEMA 250, Type 12.

        - Exterior Electronics: NEMA 250, Type 4X, [fiberglass] [stainless steel].

        - Corrosion Resistant: NEMA 250, Type 4X, [PVC] [stainless steel].

        - Terminal cabinets in handholes and manholes shall be NEMA 250, [Type 6] [Type 6P].

        - Screw Covers: Where enclosures are readily accessible, secure with security fasteners of type appropriate for enclosure.

      - SECURE AND ACCESS DEVICES

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Delete one or both paragraphs below.

        - Keypad and Display Module: Arranged for entering and executing commands for system-status changes and for displaying system-status and command-related data.

        - Key-Operated Switch: Change protected zone between secure and access conditions.

      - STRAIN-SENSITIVE CABLE

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Fence-mounted strain-sensitive, coaxial transducer cable shall monitor chain-link-type and welded-mesh-type fence and generate an alarm when a standard intruder attempts to climb over, cut through, or lift fence fabric.

See Editing Instruction No. 2 in the Evaluations for discussion of ambient conditions.

        - Environment: Suitable for exterior installation and the following conditions:

          - Ambient Temperatures: Ranging from [minus 22 to plus 158 deg F (minus 30 to plus 70 deg C)] <Insert temperature range>.

          - <Insert applicable environmental conditions>.

        - Transducer Cable:

          - UV-resistant cable furnished by system manufacturer.

          - Suitable for up to 1000 feet (300 m) of sensor cable per single-zone control unit and up to 2000 feet (600 m) of sensor cable per dual-zone processor.

          - Sensitivity shall be uniform throughout its entire length, requiring only one variable sensitivity adjustment throughout its entire length.

        - Control Unit:

          - Field mounted, with tamper switch at control-unit board.

          - Electronic circuitry shall discriminate between acceptable fence movement and intrusion-related disturbances.

          - Sensitivity, count control, and climb-over processors shall be adjustable with a minimum of five individual count-control and climb-over adjustments.

          - Control-unit output shall have adjustable pulse width to adjust the time the alarm relay will activate per detected intrusion attempt.

        - System Performance:

          - Immune to RFI and EMI environments; interference shall have no effect on normal operational characteristics.

          - Trouble and Tamper: Entire sensor system shall be fully supervised with individually monitored tamper and supervision alarms. Disconnecting, cutting, or shorting of strain-sensitive cable results in supervisory alarm.

          - Intrusion Simulation: Each zone shall have a self-test feature that, when activated by a signal from master control unit will produce an intrusion alarm and verify operation of sensor.

      - MICROWAVE INTRUSION DETECTORS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Volumetric microwave detection system.

Revise first paragraph below considering site-specific factors. See discussion in Evaluations.

        - Device Performance: Microwave transmitter establishes an electromagnetic field in an adjustable detection pattern and detects intrusion by monitoring changes in that pattern.

          - Movement Sensitivity: Adjustable, able to detect standard-intruder movement within sensor's detection pattern at any speed between 0.1 to 50 fps (0.03 to 15.2 m/s). Sensor sensitivity adjustments shall be accessible only when sensor housing is removed, and sensors shall comply with 47 CFR 15.

          - Detection Range: 15 to 600 feet (5 to 180 m).

          - Range Sensitivity: Adjustable for setting area of protection between 15 to 500 feet (5 to 152 m) in range and from 2 to 40 feet (0.6 to 12 m) in beam diameter.

          - Trouble and Tamper: Fully supervised with individually monitored tamper and supervision alarms. System failure shall result in tamper alarm. System jamming or wrong modulation shall result in supervisory alarm.

          - Activation Indicator: LED indicator shall not be visible during normal operation. Indicator shall light when sensor detects a standard intruder. Locate test-enabling switch under sensor housing cover.

Add remote-test feature to master control unit if retaining subparagraph below.

          - Remote Test: When initiated by master control unit, start a test sequence for each detector element that simulates standard-intruder movement within sensor's detection patterns, causing an alarm.

See Editing Instruction No. 2 in the Evaluations for discussion of ambient conditions.

        - Environment: Suitable for exterior installation and the following conditions:

          - Ambient Temperatures: Ranging from [minus 30 to plus 158 deg F (minus 34 to plus 70 deg C)] <Insert temperature range> and in rainfall up to 4 inches (100 mm).

          - <Insert applicable environmental conditions>.

      - ELECTROSTATIC FIELD

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

If the detection system is independently mounted, show pole details on Drawings.

        - Description: Fence-mounted[, independently mounted], above-ground, electrostatic-field detection system, consisting of electronically balanced phase electrostatic-field detection system with a field generator that generates an electrical field in one or more field wires and that has two or more sensing wires, a sense filter, amplifier, and a control unit. Detection fields shall have a minimum of four different frequencies so adjacent zones cannot interfere with each other.

See Editing Instruction No. 2 in the Evaluations for discussion of ambient conditions.

        - Environment: Suitable for exterior installation and the following conditions:

          - Ambient Temperatures: Ranging from [minus 22 to plus 158 deg F (minus 30 to plus 70 deg C)] <Insert temperature range>.

          - <Insert applicable environmental conditions>.

        - System Performance:

          - Detect, via sense wires, a compound signal form consisting of amplitude change, rate of change, and preset time disturbance that forms a "signature" of human movement. Generate an alarm when all exist simultaneously. Provide detection fields of no fewer than four different frequencies so adjacent zones do not interfere with each other.

          - Control Units: Single or multiple zone, with sense filter. Front panel with calibration meter, status of alarm transmitter, sensitivity selector, test point selector, power indicator, and power control. Control unit shall reject signals due to wind and small objects striking the wires.

          - Motion Detection: Sense standard-intruder movement at rates from 0.15 to 26 fps (0.045 to 8.0 m/s).

Detection is improved by shorter zone lengths. First option in first subparagraph below is standard; second option is recommended for high-security applications.

          - Zone Length: Not to exceed [500 feet (152 m)] [325 feet (100 m)].

          - Supervision: Generate trouble signal if field or sense wires are cut or shorted to ground or to each other. Generate supervisory alarm if received signal is substantially reduced.

        - Insulators, Wire-Tensioning Devices, and Brackets: Manufacturer's standard for mounting and tensioning of wires.

        - Field and Sensing Wires: Stainless steel.

      - BURIED, PORTED COAXIAL CABLE

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Buried electrostatic-field detection system consisting of parallel, ported coaxial cables that generate a detection field between cables.

See Editing Instruction No. 2 in the Evaluations for discussion of ambient conditions.

        - Environment: Suitable for exterior installation and the following conditions:

          - Ambient Temperatures: Ranging from [minus 22 to plus 158 deg F (minus 30 to plus 70 deg C)] <Insert temperature range>.

          - <Insert applicable environmental conditions>.

        - System Performance: One of two parallel cables receives a continuous wave signal from a transmitter module. Second cable, connected to a sensor module, detects, preamplifies, and analyzes variations in signal. When system senses "signature" of a standard intruder in the detection zone, based on mass, motion, and time of day, it generates an alarm.

          - Transmitter: Locate at one end of zone, with standby battery.

          - Preamplifier-Sensor: Locate at opposite end from transmitter, with standby battery.

          - Front panel with sensitivity calibration meter, calibrated self-test potentiometer, power switch, and LED normal and malfunction indicators.

          - Electromagnetic Radiation: Less than 50 mV per meter at 30 m.

          - Motion Detection: Sense standard-intruder movement at rates from 0.17 to 26 fps (0.05 to 8.0 m/s).

Detection is improved by shorter zone lengths. First option in first subparagraph below is standard; second option is recommended for high-security applications.

          - Zone Length: Not to exceed [500 feet (152 m)] [325 feet (100 m)].

          - Zone Width: Not to exceed 15 feet (4.6 m), with an average width of 12 feet (3.7 m).

          - Zone Height: Approximately 3.3 feet (1.0 m), depending on sensitivity setting.

          - Supervision: Generate trouble signal if cable is cut or shorted to ground. Generate supervisory alarm if cabinets are tampered with.

        - Enclosures: Hinged cover with tamper switch and security fasteners.

        - Buried, Ported Coaxial Cable: Approximately 1/2-inch (1.3-mm) diameter, minimum 10 AWG center conductor, foam polyethylene dielectric, braided copper outer conductor, and polyethylene jacket.

      - LONG-RANGE PIR DETECTORS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Volumetric passive infrared detection system.

        - Listed and labeled by a qualified testing agency for compliance with SIA PIR-01.

See Editing Instruction No. 2 in the Evaluations for discussion of ambient conditions.

        - Environment: Suitable for exterior installation and the following conditions:

          - Ambient Temperatures: Ranging from [minus 30 to plus 150 deg F (minus 34 to plus 65 deg C)] <Insert temperature range>.

          - <Insert applicable environmental conditions>.

        - System Performance: Detect an interruption of dual-infrared light beams that link transmitters and receivers. Generate an alarm when signal is interrupted due to presence of an object that interrupts both beams.

          - Sensitivity: Field adjustable to allow adjustment of range from 25 to 500 feet (7.6 to 152 m), generating an alarm within 20 to 50 ms when both beams are interrupted.

          - Detection system shall adjust automatically to compensate for weather, including fog, rain, snow, blowing dust, and rapid temperature changes.

          - Motion Detection: Detect standard-intruder movement at rates from 0.1 to 50 fps (0.03 to 15.2 m/s).

          - Supervision: Generate supervisory alarm if any portion of system is tampered with.

Add remote-test feature to master control unit if retaining subparagraph below.

          - Remote Test: When initiated by master control unit, start a test sequence for each detector element that simulates standard-intruder movement within sensor's detection patterns, causing an alarm.

      - GEOPHONE FENCE DETECTION

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Fence-mounted system to detect attempts to cut or climb the protected fence, using geophone sensors that respond to specific shock or vibrations.

See Editing Instruction No. 2 in the Evaluations for discussion of ambient conditions.

        - Environment: Suitable for exterior installation and the following conditions:

          - Ambient Temperatures: Ranging from [minus 30 to plus 150 deg F (minus 34 to plus 65 deg C)] <Insert temperature range>.

          - <Insert applicable environmental conditions>.

        - System Performance:

          - Control Unit: [10] <Insert number> zone capacity for processing geophone generated analog signals. Each zone shall consist of not more than [10] <Insert number> sensors.

            - Adjustments: For each zone, provide stepped gain control for sensitivity and switches for geophone signal filters to minimize nuisance alarms. System shall adjust automatically to compensate for weather, including fog, rain, snow, blowing dust, and rapid temperature changes.

            - Trouble Condition Signal: Generate when any zone fails.

            - Supervisory Condition Signal: Generate on interference with control-unit operation or when detecting a break-in into an enclosure housing electronics.

          - Sensors: Fence mounted [20 feet (6 m)] <Insert dimension> o.c.

          - Cable for Interconnection of System Components: Shielded, PVC jacketed and armored, as supplied by system manufacturer.

Retain first option in subparagraph below if there is digital data transmission between the control units and master control unit.

          - Test each zone simulating an alarm condition. Test by [command from master control] [test switch at control unit inside the enclosure].

Retain article below only when including a video surveillance system. The motion sensing relies on video signal from the video surveillance system.

      - VIDEO MOTION SENSOR

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Video signal sources are not included in the Section Text because this equipment is typically specified in Section 282000 "Video Surveillance." Equipment compatibility is an issue because when this Section was updated, there was no global standard defining how network video products such as cameras, video encoders, and video management systems should communicate with each other.

        - Description: Video-surveillance-based detection system.

        - Device Performance: Detect changes in video signal within a user-defined protected zone. Provide an alarm output for each video input.

          - Detect movement within protected zone of standard intruders wearing clothing with a reflectivity that differs from that of background scene by a factor of 2. Reject all other changes in video signal.

          - Modular design that allows for expansion or modification of number of inputs.

          - Adjustable Controls:

            - Number of detection zones.

            - Size of detection zones.

            - Sensitivity of detection of each protected zone.

          - Mounting: Standard 19-inch (480-mm) rack as described in EIA/ECA 310-E.

        - Environment: Suitable for installation in interior air-conditioned spaces. <Insert applicable environmental conditions>.

      - GATE UNITS

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Fence-mounted gate-movement detectors, balanced-magnetic type, and UL listed for outdoor locations. Units shall be designed for mounting on single- or double-leaf swinging or rolling gates and have armored jumper cables between switch and stationary junction box for wiring to master control unit and tamper switches in junction box.

        - Device Performance: Bias magnet and at least three encapsulated-reed switches that resist compromise from introduction of foreign magnetic fields, with integral overcurrent protective device to limit current to 80 percent of switch capacity.

Add remote-test feature to master control unit if retaining paragraph below.

        - Remote Test: Simulate movement of actuating magnet from master control unit.

      - FIELD-MOUNTED CONTROL UNITS

Coordinate with "Functional Description of System" Article.

        - Field-mounted control units shall include the power supply and detector specific functions, and provide for communications with the master control unit. Control unit shall include read-only resident software needed for startup, a time clock, and all automatic operations. Software shall be downloaded from the master control unit.

Retain first paragraph below when field-mounted control units are not powered from the master control unit.

        - Battery Backup: UPS, providing [six] <Insert number> hours of run time during a power outage, with two-rate automatic battery charger to fully recharge batteries within [12] <Insert number> hours after normal power is restored.

          - Batteries: Rechargeable, valve-regulated, recombinant, sealed, lead-acid type with nominal 10-year life expectancy.

          - Battery Charger: Solid-state, fully automatic, variable-charging-rate type. Charger shall recharge fully discharged battery within 24 hours.

        - Annunciation: Indicate a change in system condition and switching of system or component to backup power.

      - MASTER CONTROL UNIT

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Retain first paragraph below and revise general features to suit Project. Coordinate with implementation details and Drawings.

        - Description: Supervise sensors and detection subsystems and their connecting communication links, status control (secure or access) of sensors and detector subsystems, activation of alarms and supervisory and trouble signals, and other indicated functions.

          - System software and programs shall be held in flash electrically erasable programmable read-only memory (EEPROM), retaining the information through failure of primary and secondary power supplies.

          - Include a real-time clock for time annotation of events on the event recorder and printer.

          - Addressable initiation devices that communicate device identity and status.

Retain subparagraph below if response to certain alarms includes turning on lights, actuating or positioning video cameras, controlling elevators, sounding a siren, or similar responses. Indicate features on Drawings.

          - Control circuits for operation of mechanical equipment in response to an alarm.

        - Construction: [Freestanding equipment rack] [Desk-mounted console], modular, with separate and independent alarm and supervisory system modules. [Alarm-initiating protected zone boards shall be plug-in cards. ]Arrangements that require removal of field wiring for module replacement are unacceptable.

See Editing Instruction No. 3 in the Evaluations for criteria in selecting appropriate UL standard. For additional information on UL listing, see "Standards" Article in the Evaluations.

        - Comply with [UL 609] [UL 681] [UL 1076].

        - Console Controls and Displays: Arranged for interface between human operator at master control unit and addressable system components including annunciation and supervision. Display alarm, supervisory, and component status messages and the programming and control menu.

Some systems have 40-character display unit that may be adequate for simple projects.

          - Annunciator and Display: LCD type, [one] [two] [three] line(s) of [40] [80] characters, minimum.

          - Keypad: Arranged to permit entry and execution of programming, display, and control commands

          - Control-Unit Network: Automatic communication of alarm, status changes, commands, and other communications required for system operation. Communication shall return to normal after partial or total network interruption such as power loss or transient event. Total or partial signaling network failures shall identify the failure and record the failure at the annunciator display and at the system printer.

          - Field Device Network: Communicate between the control unit and field devices of the system. Communications shall consist of alarm, network status, and status and control of field-mounted processors. Each field-mounted device shall be interrogated during each interrogation cycle.

Coordinate operator commands in first subparagraph below with "Functional Description of System" Article.

          - Operator Controls: Manual switches and push-to-test buttons that do not require a key to operate. Prevent resetting of alarm, supervisory, or trouble signals while alarm or trouble condition persists. Include the following:

            - Acknowledge alarm.

            - Silence alarm.

            - System reset.

            - LED test.

            - <Insert operator functions>.

          - Timing Unit: Solid state, programmable, 365 days.

          - Confirmation: Relays, contactors, and other control devices shall have auxiliary contacts that provide confirmation signals to system for their on or off status. Software shall interpret such signals, display equipment status, and initiate failure signals.

Retain one of three "Alarm Indication" subparagraphs below to specify method of notifying alarm condition. Retain reference to annunciator if used.

          - Alarm Indication: An audible signal sounds and an LED lights at master control unit identifying the [protected zone] [addressable detector] originating the alarm.[ Annunciator panel displays a common alarm light and sounds an audible tone.]

          - Alarm Indication: An audible signal sounds and a plain-language identification of the [protected zone] [addressable detector] originating the alarm appears on [LED] [or] [LCD]display at master control unit.[ Annunciator panel displays a common alarm light and sounds an audible tone.]

          - Alarm Indication: An audible signal sounds and a plain-language identification of the [protected zone] [addressable detector] originating the alarm appears on [LED] [LCD] [or] [cathode-ray-tube] display at master control unit.[ Annunciator panel alarm light and audible tone identify protected zone signaling an alarm.]

Retain subparagraph below with any of three "Alarm Indication" subparagraphs above if system has a remote alarm bell, siren, strobe, or combination of these devices.

          - Alarm activation sounds a [bell] [siren] [strobe] [bell or siren and strobe].

Coordinate first paragraph below with Drawings.

        - Protected Zones: Quantity of alarm and supervisory zones as indicated, with capacity for expanding number of protected zones by a minimum of [25] <Insert number> percent.

        - Power Supply Circuits: Master control units shall provide power for remote power-consuming detection devices. Circuit capacity shall be adequate for at least a [25] <Insert number> percent increase in load.

Verify that manufacturer can provide UPS with requirements that comply with Section 263353 "Static Uninterruptible Power Supply."

        - UPS: Comply with Section 263353 "Static Uninterruptible Power Supply." UPS shall be sized to provide a minimum of six hours of master control-unit operation.

        - Cabinet: Lockable, steel enclosure arranged so operations required for testing, normal operation, and maintenance are performed from front of enclosure. If more than a single cabinet is required to form a complete control unit, provide exactly matching modular enclosures. Accommodate all components and allow ample gutter space for field wiring. Identify each enclosure by an engraved, laminated, phenolic-resin nameplate. Lettering on enclosure nameplate shall not be less than 1 inch (25 mm) high. Identify, with permanent labels, individual components and modules within cabinets.

        - Transmission to Monitoring Station: A communications device to automatically transmit alarm, supervisory, and trouble signals to the monitoring station, operating over a standard voice grade telephone leased line. Comply with UL 1635.

        - Printout of Events: On receipt of signal, print alarm, supervisory, and trouble events. Identify zone, device, and function. Include type of signal (alarm, supervisory, or trouble) and date and time of occurrence. Differentiate alarm signals from all other printed indications. Also print system reset event, including same information for device, location, date, and time. Commands initiate the printing of a list of existing alarm, supervisory, and trouble conditions in the system and a historical log of events.

      - AUDIBLE AND VISUAL ALARM DEVICES

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Bell: 10 inches (254 mm) in diameter, rated to produce a minimum sound output of 84 dB at 10 feet (3 m) from master control unit.

          - Enclosure: Weather-resistant steel box equipped with tamper switches on cover and on back of box.

        - Klaxon Weatherproof Motor-Driven Hooter: UL listed, rated to produce a minimum sound output of 120 dB at 3 feet (1 m), plus or minus 3 dB, at a frequency of 470 Hz. Rated for intermittent use: two minutes on, five minutes off.

          - Designed for use in industrial areas and in high-noise, severe-weather marine environments.

        - Siren: 30-W speaker with siren driver, rated to produce a minimum sound output of 103 dB at 10 feet (3 m) from master control unit.

          - Enclosure: Weather-resistant steel box with tamper switches on cover and on back of box.

        - Strobe: Xenon light complying with UL 1638, with a clear polycarbonate lens.

          - Light Output: 115 cd, minimum.

          - Flash Rate: 60 per minute.

      - SECURITY FASTENERS

        - Operable only by tools produced for use on specific type of fastener by fastener manufacturer or other licensed fabricator. Drive system type, head style, material, and protective coating as required for assembly, installation, and strength.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

Insert additional types of security fasteners below with other drive systems and head styles if necessary or for special applications. Coordinate type of security fasteners retained in this Section with other Sections specifying security fasteners. See Evaluations.

        - Drive System Types: [Pinned Torx-Plus] [pinned Torx] [or] [pinned hex (Allen)].

        - Socket Flat Countersunk Head Fasteners:

          - Heat-treated alloy steel, ASTM F835 (ASTM F835M).

          - Stainless steel, ASTM F879 (ASTM F879M), Group 1 CW.

        - Socket Button Head Fasteners:

          - Heat-treated alloy steel, ASTM F835 (ASTM F835M).

          - Stainless steel, ASTM F879 (ASTM F879M), Group 1 CW.

        - Socket Head Cap Fasteners:

          - Heat-treated alloy steel, ASTM A574 (ASTM A574M).

          - Stainless steel, ASTM F837 (ASTM F837M), Group 1 CW.

        - Protective Coatings for Heat-Treated Alloy Steel:

          - Zinc chromate, ASTM F1135, Grade 3 or Grade 4, for exterior applications and interior applications where indicated.

          - Zinc phosphate with oil, ASTM F1137, Grade I, or black oxide unless otherwise indicated.

      - SOURCE QUALITY CONTROL

If appropriate, revise this article to require testing by an NRTL, in lieu of manufacturer's tests.

        - [Electrostatic-Field] [and] [Buried, Ported Coaxial Cable] Systems Electronics: Precondition at factory by subjecting modules to at least four days' operational burn-in at temperatures not less than 140 deg F (60 deg C).

- EXECUTION

      - EXAMINATION

        - Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of perimeter security.

        - Examine roughing-in for embedded and built-in anchors to verify actual locations of perimeter security connections before perimeter security installation.

        - Prepare written report, endorsed by Installer, listing conditions detrimental to performance of perimeter security.

        - Inspect built-in and cast-in anchor installations, before installing perimeter security, to verify that anchor installations comply with requirements. Prepare inspection reports.

          - Remove and replace anchors where inspections indicate that they do not comply with requirements. Reinspect after repairs or replacements are made.

          - Perform additional inspections to determine compliance of replaced or additional anchor installations. Prepare inspection reports.

        - For material whose orientation is critical for its performance as a ballistic barrier, verify installation orientation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - SYSTEMS INTEGRATION

Retain this article to integrate perimeter security system with other systems. See Evaluations for discussion of systems integration. Also see definition of term "systems integration" in "Definitions" Article.

        - Integrate perimeter security system with the following systems and equipment:

Revise list below to include only items in Project that require integration with perimeter security system.

          - Electronic door hardware.

          - Elevators.

          - Network lighting controls.

          - Intercommunications and program systems.

          - Public address and mass notification systems.

          - Access control.

          - Fire-alarm system.

          - Intrusion detection system.

          - Video surveillance.

          - <Insert applicable systems and equipment>.

      - SYSTEM INSTALLATION

        - Comply with UL 681 and NFPA 731.

Retain first paragraph below for equipment supported on finished floor.

        - Equipment Mounting: Install master control unit on finished floor with tops of cabinets not more than 72 inches (1830 mm) above the finished floor.

Retain subparagraph below if Project requires seismic bracing. Coordinate with Section 270548.16 "Seismic Controls for Communications Systems."

          - Comply with requirements for seismic-restraint devices specified in Section 270548.16 "Seismic Controls for Communications Systems."

        - Install wall-mounted equipment, with tops of cabinets not more than 72 inches (1830 mm) above the finished floor.

Retain subparagraph below if Project requires seismic bracing. Coordinate with Section 270548.16 "Seismic Controls for Communications Systems."

          - Comply with requirements for seismic-restraint devices specified in Section 270548.16 "Seismic Controls for Communications Systems."

        - Connecting to Existing Equipment: Verify that existing perimeter security system is operational before making changes or connections.

          - Connect new equipment to existing control panel in existing part of the building.

          - Connect new equipment to existing monitoring equipment at the Supervising Station.

          - Expand, modify, and supplement existing [control] [monitoring] equipment as necessary to extend existing [control] [monitoring] functions to the new points. New components shall be capable of merging with existing configuration without degrading the performance of either system.

        - Security Fasteners: Where accessible to public, install perimeter security components using security fasteners with head style appropriate for fabrication requirements, strength, and finish of adjacent materials except that a maximum of two different sets of tools shall be required to operate security fasteners for Project.[ Provide stainless-steel security fasteners in stainless-steel materials.]

        - Wiring Method: Install power, signal, and data transmission wire and cable in metal raceways according to Section 270543 "Underground Pathways and Structures for Communications Systems" and Section 270528 "Pathways for Communications Systems." Minimum conduit size shall be 1/2 inch (13 mm). Control and data transmission wiring shall not share conduit with other building wiring systems.

        - Wiring within Enclosures: Bundle, lace, and train conductors to terminal points. Use lacing bars and distribution spools. Separate power-limited and non-power-limited conductors as recommended in writing by manufacturer. Install conductors parallel with or at right angles to sides and back of enclosure. Connect conductors that are terminated, spliced, or interrupted in any enclosure associated with perimeter security system to terminal blocks. Mark each terminal according to system's wiring diagrams. Make all connections with approved crimp-on terminal spade lugs, pressure-type terminal blocks, or plug connectors.

        - Wires and Cables:

Coordinate subparagraphs below with Drawings.

          - Conductors: Size as recommended in writing by system manufacturer unless otherwise indicated.

          - 120-V Power Wiring: Install according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables" unless otherwise indicated.

          - Cable for Low-Voltage Control and Signal Circuits: Install unshielded, twisted-pair cable unless otherwise indicated or if manufacturer recommends shielded cable, according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

          - Data and Television Signal Transmission Cables: Install according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

        - Splices, Taps, and Terminations: Make connections only on numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures.

        - Install power supplies and other auxiliary components for detection devices at control units unless otherwise indicated or required by manufacturer. Do not install such items near devices they serve.

Three paragraphs below are for specific system types; delete those not applicable.

        - Stain-Sensitive Transducer Cable: Attached to fence at 12-inch (300-mm) intervals with tie wraps.

        - Electrostatic-Field System: Install field and sense wires on insulators and standoffs on a fence, wall, or roof. Provide intermediate supports recommended in writing by manufacturer as needed for specified performance.

        - Buried, Ported Coaxial Cable: Transmitters may be located at one end of parallel coaxial cables, and preamplifier-sensor module may be located at opposite end. Install cable so shield is uniform throughout the length, without twisting or distorting cable during installation. Field-cut cables to exact zone length at the site. To attach data transmission cable to sensing cable, use heat-shrink splice kits approved by manufacturer. Provide sufficient overlap of detector cables to eliminate the possibility of entry between zones.

      - IDENTIFICATION

        - Identify system components, wiring, cabling, and terminals. Comply with identification requirements in Section 270553 "Identification for Communications Systems."

        - Install instructions frame in a location visible from master control unit.

      - GROUNDING

        - Ground the master control unit and associated circuits; comply with IEEE 1100. Install a ground wire from main service ground to master control unit.

        - Ground system components and conductor and cable shields to eliminate shock hazard and to minimize ground loops, common-mode returns, noise pickup, cross talk, and other impairments.

        - Signal Ground Terminal: Locate at main equipment rack or cabinet. Isolate from power system and equipment grounding. Provide [5] <Insert value>-ohm ground. Measure, record, and report ground resistance.

Coordinate paragraph below with Drawings.

        - Install grounding electrodes of type, size, location, and quantity indicated. Comply with installation requirements in Section 270526 "Grounding and Bonding for Communications Systems."

      - FIELD QUALITY CONTROL

        - Pretesting: After installation, align, adjust, and balance system and perform complete pretesting to determine compliance of system with requirements in the Contract Documents. Correct deficiencies observed in pretesting. Replace malfunctioning or damaged items with new ones and retest until satisfactory performance and conditions are achieved. Prepare forms for systematic recording of acceptance test results.

          - Report of Pretesting: After pretesting is complete, provide a letter certifying that installation is complete and fully operable; include names and titles of witnesses to preliminary tests.

Retain one of first three paragraphs below to identify who shall perform tests and inspections. If retaining second option in first paragraph, or if retaining second or third paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain first paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

        - Manufacturer's Field Service: Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.

Retain first paragraph below to require Contractor to perform tests and inspections.

        - Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

          - Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph below to describe tests and inspections to be performed.

        - Tests and Inspections: Comply with provisions in NFPA 731, Ch. 9, "Testing and Inspections."

          - Inspection: Verify that units and controls are properly labeled and interconnecting wires and terminals are identified.

          - Test Methods: Perimeter security systems and other systems and equipment that are associated with detection and accessory equipment shall be tested according to Table "Test Methods" and Table "Test Methods of Initiating Devices."

Subparagraphs below are for specific system types; delete those not applicable.

          - Geophone System Tests: Test each zone at a minimum of two different locations. Test each zone as follows:

            - Horizontal Movement: Adjust sensitivity to screen out alarms from wind.

            - Vertical Climb: 100 percent detection required. Set count at three occurrences within 90-second window.

            - Cut Test: 100 percent detection required. Set count at two occurrences within 120-second window.

            - Set sensitivity to value as low as possible, consistent with reliable detection.

            - If performance tests fail, make adjustments to sensors to comply with requirements. Retest failing and adjacent zones to comply with test.

          - Strain-Sensitive Cable System Tests: Adjust sensitivity and count control to value as low as possible, consistent with reliable detection.

          - Microwave Perimeter Security System Tests: Adjust sensitivity to value as low as possible, consistent with reliable detection.

          - Long-Range PIR System Tests: Adjust sensitivity and hold time between activity duration to value as low as possible, consistent with reliable detection.

        - Documentation: Comply with provisions in NFPA 731, Ch. 4, "Documentation."

        - Tag all equipment, stations, and other components at which tests have been satisfactorily completed.

      - ADJUSTING

Revise this article to suit Project.

        - Occupancy Adjustments: When requested within [12] <Insert number> months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions. Provide up to [two] <Insert number> visits to Project during other than normal occupancy hours for this purpose.[ Visits for this purpose shall be in addition to any required by warranty.]

      - DEMONSTRATION

        - [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain the perimeter security system. Comply with documentation provisions in NFPA 731, Ch. 4, "Documentation and User Training."

END OF SECTION 283121