Copyright 2021 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

SECTION 284800 - EMERGENCY RESPONSE SYSTEMS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Emergency responder communications enhancement systems.

          - Emergency responder telephone systems.

          - Two-way emergency communications systems for rescue assistance.

        - Related Requirements:

Always retain first two subparagraphs below.

          - Section 260011 "Facility Performance Requirements for Electrical" for seismic-load, wind-load, acoustical, and other field conditions applicable to Work specified in this Section.

          - Section 280010 "Supplemental Requirements for Electronic Safety and Security" for additional abbreviations, definitions, submittals, qualifications, testing agencies, and other Project requirements applicable to Work specified in this Section.

          - Section 284621.11 "Addressable Fire-Alarm Systems" for interfacing emergency response systems with fire-alarm systems.

          - Section 284700 "Mass Notification" for interfacing emergency response systems with mass notification systems.

      - DEFINITIONS

Do not duplicate common acronyms, abbreviations, and terms defined in Section 280010 "Supplemental Requirements for Electronic Safety and Security."

Retain terms that remain after this Section has been edited for a project. Include only essential definitions or acronyms not well understood by the affected industry or trade.

        - BDA: Bi-directional amplifier.

        - ERCES: Emergency responder communications enhancement system.

        - PES: Public emergency service.

        - RF: Radio frequency.

        - UHF: Ultra-high frequency.

      - PREINSTALLATION MEETINGS

Retain "Preinstallation Coordination Meeting(s)" Paragraph below if Work of this Section does not justify a full preinstallation conference as specified in Section 013100 "Project Management and Coordination," but would benefit from a smaller coordination meeting. Consider videoconference option if Project requires social distancing for meetings for infection control.

        - Preinstallation Coordination Meeting(s): For emergency communications systems. Conduct meeting(s) [as videoconference] [or] [at Project site] <Insert location> before <Insert construction activity>.

          - Attendees: Installers, fabricators, representatives of manufacturers, representatives of authorities having jurisdiction, and administrants for field tests and inspections. Notify Architect[, Construction Manager] [, and Owner's Commissioning Authority] of scheduled meeting dates.

      - ACTION SUBMITTALS

Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.

        - Product Data:

Retain one of three subparagraphs below, or all, as needed to verify compliance of Work with Project requirements.

          - ERCESs:

            - BDAs.

            - In-building service antennas.

            - Outdoor donor antenna.

            - Coaxial cabling.

            - Couplers and splitters.

            - Remote indicator panels.

          - Emergency Responder Telephone Systems:

            - Master control station.

            - Remote telephone cabinets.

            - Remote telephone jack stations.

            - Handsets.

          - Two-Way Emergency Communications Systems for Rescue Assistance:

            - Master control station.

            - Remote communications stations.

Coordinate "Shop Drawings" Paragraph below with "Regulatory Agency Approvals" Article.

        - Shop Drawings:

Retain subparagraphs below as needed to verify compliance of Work with Project requirements.

          - Project general notes.

          - ERCESs:

            - Device layout.

            - Block diagrams and cable/conduit routing.

            - Pathway class and survivability identification.

            - System communications details.

            - System sequence of operations.

            - System mounting details.

            - Secondary power calculations.

          - Emergency Responder Telephone Systems:

            - Device layout.

            - Block diagrams and cable/conduit routing.

            - Pathway class and survivability identification.

            - System communications details.

            - System sequence of operations.

            - System mounting details.

            - Secondary power calculations.

          - Two-Way Emergency Communications Systems for Rescue Assistance:

            - Device layout.

            - Block diagrams and cable/conduit routing.

            - Pathway class and survivability identification.

            - System communications details.

            - System sequence of operations.

            - System mounting details.

            - Secondary power calculations.

Retain "Certificates" Paragraph below if certificate from manufacturer or fabricator is required by Architect to verify that product or assembly has been investigated and approved/recognized by third party prior to installation.

        - Certificates:

          - Certification from each system [vendor] [manufacturer] that equipment and components are compatible and represent a complete system in accordance with NFPA 72, NFPA 1221, and specified requirements.

          - <Insert certificate requirement>.

        - Field Quality-Control Submittals:

          - Field quality-control reports.

      - INFORMATIONAL SUBMITTALS

Information submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Retain "Manufacturers' Published Instructions" Paragraph below when execution requirements state "in accordance with manufacturer's published instructions," especially if those instructions may require preinstallation review and coordination with Construction Documents to verify constructability and commissioning requirements.

        - Manufacturers' Published Instructions: Record copy of official installation[ and testing] instructions issued to Installer by manufacturer for the following:

          - Installation instructions for ERCESs.

          - Installation instructions for emergency responder telephone systems.

          - Installation instructions for two-way emergency communications systems for rescue assistance.

          - Recommended tests and inspections for ERCESs.

          - Recommended tests and inspections for emergency responder telephone systems.

          - Recommended tests and inspections for two-way emergency communications systems for rescue assistance.

        - Baseline Radio Signal Strength Testing Report:

          - Detailed report indicating NFPA 72 or NFPA 1221 plotted interior radio signal strength or delivered audio quality score throughout building critical and general areas with construction of interior partitions and doors completed, but without ERCES installed.

          - Approval from authorities having jurisdiction to omit ERCES installation within building areas where baseline radio signal strength testing demonstrates that minimum required radio signal strength values are provided within these areas.

        - System Record of Inspection and Testing: Record copy of completed system acceptance testing.[ Format must be approved by authorities having jurisdiction.]

        - Sample warranties.

      - CLOSEOUT SUBMITTALS

Submittals for record documents, operation and maintenance data, software, and software documentation are specified in Section 280010 "Supplemental Requirements for Electronic Safety and Security."

        - Warranty documentation.

      - REGULATORY AGENCY APPROVALS

Retain this article when review and approval of Contractor's submittals by authorities having jurisdiction is required.

Retain one of two paragraphs below. Retain first paragraph if Contractor's submittals are prepared by Contractor's professional engineer who is recognized by authorities having jurisdiction as designer of record for emergency communications systems. Retain second paragraph if Contractor's submittals require review and approval with signature and seal by Architect's professional engineer who is recognized as designer of record.

In first paragraph, first option may lead to unnecessary delays for resubmission of Contractor's submittals to authorities having jurisdiction after action by Architect. Second option may lead to unnecessary delays for rework if Contractor's submittals are rejected by authorities having jurisdiction after action by Architect. Architects typically prefer receiving approval by authorities having jurisdiction before taking action, but likelihood and consequences of risks under Project's delivery method (e.g., design-bid-build or design-build) should be considered before retaining an option.

        - Submittals for emergency communications systems requiring approval by authorities having jurisdiction must be signed and sealed by qualified electrical professional engineer or qualified fire protection professional engineer responsible for their preparation. [Obtain approval by authorities having jurisdiction prior to submitting for action by Architect.] [Submit for action by Architect prior to submitting for approval by authorities having jurisdiction.]

        - Submittals for emergency communications systems require action by Architect prior to submitting for approval by authorities having jurisdiction.

      - WARRANTY FOR EMERGENCY RESPONSE SYSTEMS

When warranties are required and available, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner, after one-year correction period specified in the Contract, under Contractor's general warranty and prevailing local laws.

Verify durations of extended-warranty periods needed.

        - Special Installer Extended Warranty: Installer warrants that fabricated and installed ERCES performs in accordance with specified requirements and agrees to repair or replace components or products that fail to perform as specified within extended-warranty period.

          - Extended-Warranty Period: [Two] [Three] [Four] <Insert number> years from date of Substantial Completion; full coverage for labor, materials, and equipment.

Retain "Special Manufacturer Extended Warranty" Paragraph below if Project requires that a special manufacturer extended warranty take over when the special Installer extended warranty expires. To benefit Owner, manufacturer extended-warranty period must be longer than Installer extended-warranty period.

        - Special Manufacturer Extended Warranty: Manufacturer warrants that ERCES performs in accordance with specified requirements and agrees to provide repair or replacement of components or products that fail to perform as specified within extended-warranty period.

          - [Initial ]Extended-Warranty Period: [Three] [Four] [Five] <Insert number> years from date of Substantial Completion; [full] [prorated] coverage for labor, materials, and equipment.

Retain transient voltage surges option in "Follow-On Extended-Warranty Period" Subparagraph below if assembly includes surge protective devices. Retain "origin" option if recipient assumes ownership of goods when they are shipped. Retain "destination" option if seller retains ownership of goods until they are delivered. Damaged shipping containers labeled "FOB Origin" cannot be returned to sender, but carrier is liable to recipient for delay and damage claims.

          - Follow-On Extended-Warranty Period: [Eight] <Insert number> years from date of Substantial Completion; [full] [prorated] coverage for materials[ that failed because of transient voltage surges] only, free on board [origin] [destination], freight prepaid.

      - WARRANTY FOR BATTERIES

        - Special Manufacturer Extended Warranty for Batteries: Manufacturer warrants that batteries perform in accordance with specified requirements and agrees to provide repair or replacement of batteries that fail to perform as specified within extended-warranty period.

Retain "Initial Extended-Warranty Period for Li-ion Batteries" and "Follow-On Extended-Warranty Period for Li-ion Batteries" subparagraphs below if emergency response system includes Li-ion battery standby power. Retain "origin" option if recipient assumes ownership of goods when they are shipped. Retain "destination" option if seller retains ownership of goods until they are delivered. Damaged shipping containers labeled "FOB Origin" cannot be returned to sender, but carrier is liable to recipient for delay and damage claims.

          - Initial Extended-Warranty Period for Li-ion Batteries: [Three] [Four] [Five] <Insert number> years from date of Substantial Completion; full coverage for materials only, free on board [origin] [destination], freight prepaid.

          - Follow-On Extended-Warranty Period for Li-ion Batteries: [Ten] <Insert number> years from date of Substantial Completion; prorated coverage for materials only, free on board [origin] [destination], freight prepaid.

Retain "Extended-Warranty Period for Ni-MH Batteries" Subparagraph below if emergency response system includes Ni-MH battery standby power. Retain "origin" option if recipient assumes ownership of goods when they are shipped. Retain "destination" option if seller retains ownership of goods until they are delivered. Damaged shipping containers labeled "FOB Origin" cannot be returned to sender, but carrier is liable to recipient for delay and damage claims.

          - Extended-Warranty Period for Ni-MH Batteries: [Three] <Insert number> years from date of Substantial Completion; prorated coverage for materials only, free on board [origin] [destination], freight prepaid.

Retain "Extended-Warranty Period for Ni-Cd Batteries" Subparagraph below if emergency response system includes Ni-Cd battery standby power. Retain "origin" option if recipient assumes ownership of goods when they are shipped. Retain "destination" option if seller retains ownership of goods until they are delivered. Damaged shipping containers labeled "FOB Origin" cannot be returned to sender, but carrier is liable to recipient for delay and damage claims.

          - Extended-Warranty Period for Ni-Cd Batteries: [Five] <Insert number> years from date of Substantial Completion; prorated coverage for materials only, free on board [origin] [destination], freight prepaid.

Retain "Warranted Cycle Life for Valve Regulated (Sealed) (Lead Calcium) (or) (Lead Selenium) Batteries" or "Warranted Cycle Life for Premium Valve Regulated (Sealed) (Lead Calcium) (or) (Lead Selenium) Batteries" Subparagraph below to specify typical industry emergency response system battery-life warranty for type of battery specified in Part 2. Consult manufacturers' literature and revise, if applicable, to suit Project. Discharge rate is the length of time a battery can maintain a current flow before the battery voltage falls below the discharge end voltage. Discharge duration is the period the current flow is maintained to establish one cycle. The cycle life is the number of times the battery is warranted to provide the discharge rate for the discharge duration before failing. Coordinate the required average battery temperature for maintaining warranty coverage with the HVAC design for the battery location and enclosure type.

          - Warranted Cycle Life for Valve Regulated (Sealed) [Lead Calcium] [or] [Lead Selenium] Batteries: Equal to or greater than that represented in manufacturer's published table, but not less than the following, based on annual average battery temperature of 77 deg F (25 deg C):

            - For discharge rate not faster than eight hours, discharge duration not longer than eight hours, and voltage at end of discharge not less than 1.67 V, warranted life must be not fewer than six discharge cycles.

            - For discharge rate not faster than 30 minutes, discharge duration not longer than 30 minutes, and voltage at end of discharge not less than 1.67 V, warranted life must be not fewer than 20 discharge cycles.

            - For discharge rate not faster than 15 minutes, discharge duration not longer than 45 seconds, and voltage at end of discharge not less than 1.67 V, warranted life must be not fewer than 120 discharge cycles.

          - Warranted Cycle Life for Premium Valve Regulated (Sealed) [Lead Calcium] [or] [Lead Selenium] Batteries: Equal to or greater than that represented in manufacturer's published table, but not less than the following, based on annual average battery temperature of 77 deg F (25 deg C):

            - For discharge rate not faster than eight hours, discharge duration not longer than eight hours, and voltage at end of discharge not less than 1.67 V, warranted life must be not fewer than 40 discharge cycles.

            - For discharge rate not faster than 30 minutes, discharge duration not longer than 30 minutes, and voltage at end of discharge not less than 1.67 V, warranted life must be not fewer than 125 discharge cycles.

            - For discharge rate not faster than 15 minutes, discharge duration not longer than 90 seconds, and voltage at end of discharge not less than 1.67 V, warranted life must be not fewer than 750 discharge cycles.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - EXISTING PRODUCTS[ TO BE MODIFIED] [ TO BE REMOVED AND RE-INSTALLED]

        - Basis for Pricing: <Insert name of manufacturer; model number or series for existing product>.

        - Description: <Insert description of existing product, including special features, options, and finishes that may impact Work>.

        - Accessories: <Insert accessories included with existing product>.

      - EMERGENCY RESPONDER COMMUNICATIONS ENHANCEMENT SYSTEMS

        - Description: This category includes in-building ERCES equipment to improve wireless communication. This FCC-certified enhancement system is inclusive of BDA, transmission lines, cables, power supplies, antennas, and other ancillary equipment that allows radio signals to pass to and from interior of structure for facilitating radio communications using PES radio frequencies.

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

            - Unless otherwise indicated in Contract Documents, products must comply with NFPA 1, NFPA 70, NFPA 72, NFPA 1221, [NFPA 101,] [ICC IBC,] [ICC IFC,] and local regulations enforced by authorities having jurisdiction.

Copy and re-edit first paragraph below for each configuration indicated on Drawings. UL CCN UTMH cautions that authorities having jurisdiction should be consulted before installation or revision of in-building emergency radio communication enhancement equipment.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - In-Building ERCES Bi-Directional Amplifiers <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com.

          - Listing Criteria: UL CCN UTMH; including UL 2524 and NFPA 1221.

          - Options:

            - Primary Power Supply: [120 V(ac)] [240 V(ac)] <Insert voltage>.

            - Secondary Power Supply: [24 V(dc)] <Insert voltage> supply system including batteries, automatic float-charge battery charger, and automatic transfer switch.

            - Supervision: Auxiliary contacts for remote status supervision by [protected premises fire-alarm system] [mass notification system] <Insert system>.

              - Signal booster failure.

              - Antenna malfunction.

              - Loss of primary power.

              - Low battery voltage.

              - Battery charger failure.

              - <Insert system status supervision>.

            - Cabinet Enclosures: [UL 50E, Type 4] steel enclosure for amplifiers and power supplies.

            - Mounting: [Surface] [Flush] <Insert type> mount.

            - Finish: [Factory-finish red enamel] <Insert finish>.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - In-Building ERCES Distributed Antennas <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Type: [Wide-band omnidirectional] [and] [multi-band] [single-band].

            - Mounting: Low-profile [ceiling] <Insert type> mount.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - In-Building ERCES Donor Antennas <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Configuration: Factory assembled and tuned directional UHF Yagi antenna.

            - Mounting: [Stainless steel] <Insert type> mounting hardware.

            - Finish: [Welded] [or] [seamless] corrosion-resistant aluminum construction.

            - Wind Velocity Rating: [Comply with minimum ICC IBC requirements] <Insert requirements>.

Copy and re-edit first paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - RF Antenna Cable Couplers and Splitters <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Configuration: Nominal [0.5 inch (13 mm)] <Insert diameter>, [50 Ω] <Insert impedance>, N-Type, weatherproof, medium-size, RF couplers and splitters for coaxial cables.

            - Bandwidth: [As required by in-building emergency radio enhancement system performance requirements] <Insert requirement>.

            - Gain (dB) Rating: [As required by in-building emergency radio enhancement system performance requirements] <Insert requirement>.

Retain first option in "Environmental Rating" Subparagraph below if UL 50E type rating is also needed for Project.

            - Environmental Rating: [Type 4 and ][IP65] <Insert IP rating>.

Copy and re-edit paragraph below for each configuration indicated on Drawings.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Remote Indicator Panel <Insert drawing designation>:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Options:

            - Primary Power Supply: [120 V(ac)] [240 V(ac)] <Insert voltage>.

            - Secondary Power Supply: [24 V(dc)] <Insert voltage> supply system including batteries, automatic float-charge battery charger, and automatic transfer switch.

            - Configuration: Zone indicator panel with LED indicators[, piezoelectric sounder] and switches for lamp test and alarm silence.

            - LED Indicators: Green indicator for primary power in normal state; red indicators for each individual fault status required to be indicated by authorities having jurisdiction.

            - Enclosure: [16-gauge steel] <Insert material> with factory-applied red enamel finish.

      - EMERGENCY RESPONDER TELEPHONE SYSTEMS

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

            - Unless otherwise indicated in Contract Documents, products must comply with NFPA 1, NFPA 70, NFPA 72, [NFPA 101,] [ICC IBC,] [ICC IFC,] and local regulations enforced by authorities having jurisdiction.

Copy and re-edit first paragraph below for each configuration indicated on Drawings. UL CCN UOXX cautions that authorities having jurisdiction should be consulted before installation or revision of telephone equipment accessories for use with protective signaling systems.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Emergency Responder Telephone Connected to Fire Alarm <Insert drawing designation>:

          - Description: This category includes telephone equipment accessories for use with fire-protective signaling systems. Operation of this equipment depends upon connection to fire-alarm control unit.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com.

          - Listing Criteria: UL CCN UOXX and marked Type T; including UL 864 and NFPA 72.

          - Options:

            - System Type:

Retain one of first two subparagraphs below.

              - Common-talk type for firefighter use only.

              - Selective-talk type for use by firefighters and fire wardens.

            - Master Control Station: Mount [within FACU] [adjacent to FACU] [in fire command center] to provide power, supervision, and control for emergency responder telephone system.

              - Power Supply: [24 V(dc)] <Insert voltage> supply system including batteries, automatic float-charge battery charger, and automatic transfer switch.

              - Communicate between master control station handset and remote telephone handsets.

              - Annunciate visual and audible signal at master control station when remote telephone handset is lifted from cradle or when phone is plugged into designated remote jack.

              - Silence audible signal when master control station handset is removed and remote telephone handset is acknowledged.

            - Remote Telephone Cabinet: Flush- or surface-mounted cabinet as indicated; factory-standard red finish; with handset.

              - Install one-piece handset to cabinet with vandal-resistant armored cord. Silk-screened or engraved label on cabinet door, designating[ "Fire Warden Phone" or] "Fire Emergency Phone."

              - With "break-glass" door access lock.

            - Remote Telephone Jack Stations: Single-gang, stainless steel-plate mounted plug, engraved[ "Fire Warden Phone" or] "Fire Emergency Phone."

            - Handsets: <Insert number> [push-to-talk] sets[ with noise-canceling microphone] stored in cabinet [adjacent to FACU] [in fire command center].

            - Pathway Survivability:

              - Riser Cables: [Level 2 or 3] <Insert requirement>.

              - Feeder Cables: [Level 0] <Insert requirement>.

Copy and re-edit paragraph below for each configuration indicated on Drawings. UL CCN UOQY cautions that authorities having jurisdiction should be consulted before installation or revision of telephone equipment for emergency voice communication.

Insert drawing designation. Use these designations on Drawings to identify each product.

        - Emergency Responder Telephone Not Connected to Fire Alarm <Insert drawing designation>:

          - Description: This category includes telephone equipment for providing emergency voice communication on either selective or general basis. Operation of this equipment does not depend upon connection to fire-alarm control unit.

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

For assistance with finding guide information for UL Category Control Numbers and identifying UL-approved manufacturers, consult the UL Product iQ database at https://iq.ulprospector.com.

          - Listing Criteria: UL CCN UOQY and marked Type T; including UL 864 and NFPA 72.

          - Options:

            - System Type:

Retain one of first two subparagraphs below.

              - Common-talk type for firefighter use only.

              - Selective-talk type for use by firefighters and fire wardens.

            - Master Control Station: Mount [adjacent to FACU] [in fire command center] [at designated location in building] to provide power, supervision, and control for emergency responder telephone system.

              - Power Supply: [24 V(dc)] <Insert voltage> supply system including batteries, automatic float-charge battery charger, and automatic transfer switch.

              - Communicate between master control station handset and remote telephone handsets.

              - Annunciate visual and audible signal at master control station when remote telephone handset is lifted from cradle or when phone is plugged into designated remote jack.

              - Silence audible signal when master control station handset is removed and remote telephone handset is acknowledged.

            - Remote Telephone Cabinet: Flush- or surface-mounted cabinet as indicated; factory-standard red finish; with handset.

              - Install one-piece handset to cabinet with vandal-resistant armored cord. Silk-screened or engraved label on cabinet door, designating[ "Fire Warden Phone" or] "Fire Emergency Phone."

              - With "break-glass" door access lock.

            - Remote Telephone Jack Stations: Single-gang, stainless steel-plate mounted plug, engraved[ "Fire Warden Phone" or] "Fire Emergency Phone."

            - Handsets: <Insert number> [push-to-talk] sets[ with noise-canceling microphone] stored in cabinet [adjacent to FACU] [in fire command center].

            - Pathway Survivability:

              - Riser Cables: [Level 2 or 3] <Insert requirement>.

              - Feeder Cables: [Level 0] <Insert requirement>.

      - TWO-WAY EMERGENCY COMMUNICATIONS SYSTEMS FOR RESCUE ASSISTANCE

The first edition of UL 2525 was issued June 2020. When this Section was written, there were no UL categories for investigating, listing, and labeling the products in this article. Until manufacturer products are listed in accordance with UL 2525, specifying basis of design and alternative manufacturers for these products is recommended. If unable to specify products from three manufacturers, indicate required general characteristics for evaluating product substitutions.

        - Description: This category includes equipment for providing two-way emergency voice communication for areas of refuge, stairway landings, elevator landings, and occupant evacuation elevator lobbies in accordance with NFPA 72.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

        - Basis-of-Design Product: Subject to compliance with requirements, provide <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

          - <Insert name of second manufacturer>.

          - <Insert name of third manufacturer>.

        - Performance Criteria:

          - Regulatory Requirements:

            - Listed and labeled in accordance with NFPA 70, by qualified electrical testing laboratory recognized by authorities having jurisdiction, and marked for intended location and application.

            - Unless otherwise indicated in Contract Documents, products must comply with NFPA 1, NFPA 70, NFPA 72, [NFPA 101,] [ICC IBC,] [ICC IFC,] and local regulations enforced by authorities having jurisdiction.

          - Listing Criteria: UL 2525 and NFPA 72.

        - General Characteristics:

          - Master Control Station: Mount [in fire command center] [in constantly attended location] to provide power, supervision, and control for two-way emergency communications systems for rescue assistance.

            - Power Supply: [24 V(dc)] <Insert voltage> supply system including batteries, automatic float-charge battery charger, and automatic transfer switch.

            - Communicate between master control station handset and remote communications stations.

            - Annunciate visual and audible signal at master control station when remote telephone handset is lifted from cradle or when phone is plugged into designated remote jack.

            - Silence audible signal when master control station handset is removed and remote telephone handset is acknowledged.

            - Display identification for location of remote communications stations in building.

          - Remote Communications Stations: [Single-gang] [or] [double-gang], stainless steel-plate mounted station with hands-free, two-way communication.

          - Pathway Survivability:

            - Riser Cables: [Level 2 or 3] <Insert requirement>.

            - Feeder Cables: [Level 0] <Insert requirement>.

          - <Insert additional required characteristics for evaluating product substitutions>.

        - Accessories: <Insert desired accessories>.

- EXECUTION

      - COMMON INSTALLATION REQUIREMENTS FOR EMERGENCY RESPONSE SYSTEMS

        - Comply with manufacturer's published instructions.

NFPA 70, NFPA 72, NFPA 731, and NECA NEIS 1 are already specified in Section 280010 "Supplemental Requirements for Electronic Safety and Security." Retain "Reference Standards" Paragraph below to specify other standards applicable to Work specified in this Section.

        - Reference Standards:

          - Unless more stringent requirements are specified in Contract Documents or manufacturers' published instructions, comply with NFPA 1, NFPA 70, NFPA 72, NFPA 1221, [NFPA 101,] [ICC IBC,] [ICC IFC,] and local regulations enforced by authorities having jurisdiction for installation of emergency communications systems.

          - Comply with NECA 305 for installation of emergency communications systems devices and their connections to fire-alarm system.

          - Consult [Architect] [Owner] for resolution of conflicting requirements.

        - Installation for Survivability:

          - Where NFPA 72 or NFPA 1221 Survivability Level 2 or 3 pathways are indicated or required, install cables and pathways within 2-hour fire-resistance-rated enclosures or provide fire-resistive pathway installation in accordance with NFPA 72 or NFPA 1221.

          - Install control equipment, power supplies, junction boxes, terminal cabinets, or similar components within dedicated 2-hour fire-resistance-rated fire-alarm system equipment rooms if components originate from or comprise a portion of NFPA 72 or NFPA 1221 Survivability Level 2 or 3 pathway.

      - INSTALLATION OF ERCES

        - Special Techniques:

          - Antenna Wiring Methods:

            - Coaxial Cabling:

              - Riser Coaxial Cable: Type CATVR, nominal [0.5 inch (13 mm)] <Insert diameter>, [50 Ω] <Insert impedance> coaxial jacketed cable with corrugated [copper] [or] [aluminum] outer conductor.

              - Plenum Coaxial Cable: Type CATVP, nominal [0.5 inch (13 mm)] <Insert diameter>, [50 Ω] <Insert impedance> coaxial jacketed cable with corrugated [copper] [or] [aluminum] outer conductor.

              - Plenum Radiating Coaxial Cable: Type CATVP, nominal [0.5 inch (13 mm)] <Insert diameter>, [50 Ω] <Insert impedance> radiating coaxial jacketed cable with corrugated [copper] [or] [aluminum] outer conductor.

              - Connectors: Nominal [0.5 inch (13 mm)] <Insert diameter>, [50 Ω] <Insert impedance> N-Type, weatherproof, medium-size, RF connectors for coaxial cables.

            - Pathway Survivability:

              - Riser Coaxial Cables: [Level 2 or 3] <Insert requirement>.

              - Feeder Coaxial Cables: [Level 0] <Insert requirement>.

          - Determine in-building service antenna locations based on baseline radio signal strength testing.

          - Request approval from authorities having jurisdiction to omit emergency responder radio coverage system from areas of building where baseline radio signal strength testing demonstrates that minimum required radio signal strength values are achieved without radio coverage system.

          - Install outdoor donor antenna with clear view to donor site with minimum [2 ft (0.6 m)] vertical clearance above nearby obstacles.

          - <Insert more stringent installation requirements that supplement or supersede listed standards and manufacturers' published instructions>.

        - Interfaces with Other Work:

          - Coordinate installation of new products for emergency responder radio coverage systems with existing conditions.

            - <Insert requirements for transition between new and existing>.

          - Coordinate with [Section 284621.11 "Addressable Fire-Alarm Systems"] [Section 284621.13 "Conventional Fire-Alarm Systems"] for interfaces with fire-alarm system.

      - INSTALLATION OF EMERGENCY RESPONDER TELEPHONE SYSTEMS

        - Special Techniques:

          - <Insert more stringent installation requirements that supplement or supersede listed standards and manufacturers' published instructions>.

        - Interfaces with Other Work:

          - Coordinate installation of new products for emergency responder telephone systems with existing conditions.

            - <Insert requirements for transition between new and existing>.

          - Coordinate with [Section 284621.11 "Addressable Fire-Alarm Systems"] [Section 284621.13 "Conventional Fire-Alarm Systems"] for interfaces with fire-alarm system.

      - INSTALLATION OF TWO-WAY EMERGENCY COMMUNICATIONS SYSTEMS FOR RESCUE ASSISTANCE

        - Special Techniques:

          - <Insert more stringent installation requirements that supplement or supersede listed standards and manufacturers' published instructions>.

        - Interfaces with Other Work:

          - Coordinate installation of new products for two-way emergency communications systems for rescue assistance with existing conditions.

            - <Insert requirements for transition between new and existing>.

          - Coordinate with [Section 284621.11 "Addressable Fire-Alarm Systems"] [Section 284621.13 "Conventional Fire-Alarm Systems"] for interfaces with fire-alarm system.

      - IDENTIFICATION

        - Identify system components, wiring, cabling, and terminals. Comply with requirements for identification specified in Section 270553 "Identification for Communications Systems."

      - FIELD QUALITY CONTROL OF EMERGENCY RESPONDER RADIO COVERAGE SYSTEMS

        - [Acceptance ]Testing Preparation:

          - <Insert requirements>.

Retain first paragraph below to require that field quality-control tests be witnessed. Local ordinance or custom may require that authorities having jurisdiction witness the testing.

        - Field tests and inspections must be witnessed by [Architect] [Tenant] [authorities having jurisdiction] <Insert names or titles of witnesses>.

        - Tests and Inspections:

          - Perform manufacturer's recommended tests and inspections.

          - Perform field tests and inspections required by NFPA 72 and NFPA 1221.

          - Baseline radio signal strength testing.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Nonconforming Work:

          - Device will be considered defective if it does not pass tests and inspections.

          - Remove and replace defective units and retest.

        - Collect, assemble, and submit test and inspection reports.

Retain "Manufacturer Services" Paragraph below if manufacturer's representative is required to support or supervise the administrant specified in Section 280010 "Supplemental Requirements for Electronic Safety and Security" for field tests and inspections performed by Installer or third-party agencies.

        - Manufacturer Services:

Retain "supervise" option in subparagraph below when third-party tests and inspections must be witnessed and approved by factory-authorized service representative to satisfy special extended-warranty requirements. In some cases, Installer may be factory authorized under warranty provisions to fulfill this role.

          - Engage factory-authorized service representative to [support] [supervise] field tests and inspections.

      - FIELD QUALITY CONTROL OF EMERGENCY RESPONDER TELEPHONE SYSTEMS

        - [Acceptance ]Testing Preparation:

          - <Insert requirements>.

Retain first paragraph below to require that field quality-control tests be witnessed. Local ordinance or custom may require that authorities having jurisdiction witness the testing.

        - Field tests and inspections must be witnessed by [Architect] [Tenant] [authorities having jurisdiction] <Insert names or titles of witnesses>.

        - Tests and Inspections:

          - Perform manufacturer's recommended tests and inspections.

          - Perform field tests and inspections required by NFPA 72 and NFPA 1221.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Nonconforming Work:

          - Device will be considered defective if it does not pass tests and inspections.

          - Remove and replace defective units and retest.

        - Collect, assemble, and submit test and inspection reports.

Retain "Manufacturer Services" Paragraph below if manufacturer's representative is required to support or supervise the administrant specified in Section 280010 "Supplemental Requirements for Electronic Safety and Security" for field tests and inspections performed by Installer or third-party agencies.

        - Manufacturer Services:

Retain "supervise" option in subparagraph below when third-party tests and inspections must be witnessed and approved by factory-authorized service representative to satisfy special extended-warranty requirements. In some cases, Installer may be factory authorized under warranty provisions to fulfill this role.

          - Engage factory-authorized service representative to [support] [supervise] field tests and inspections.

      - FIELD QUALITY CONTROL OF TWO-WAY EMERGENCY COMMUNICATIONS SYSTEMS FOR RESCUE ASSISTANCE

        - [Acceptance ]Testing Preparation:

          - <Insert requirements>.

Retain first paragraph below to require that field quality-control tests be witnessed. Local ordinance or custom may require that authorities having jurisdiction witness the testing.

        - Field tests and inspections must be witnessed by [Architect] [Tenant] [authorities having jurisdiction] <Insert names or titles of witnesses>.

        - Tests and Inspections:

          - Perform manufacturer's recommended tests and inspections.

          - Perform field tests and inspections required by NFPA 72 and NFPA 1221.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Nonconforming Work:

          - Device will be considered defective if it does not pass tests and inspections.

          - Remove and replace defective units and retest.

        - Collect, assemble, and submit test and inspection reports.

Retain "Manufacturer Services" Paragraph below if manufacturer's representative is required to support or supervise the administrant specified in Section 280010 "Supplemental Requirements for Electronic Safety and Security" for field tests and inspections performed by Installer or third-party agencies.

        - Manufacturer Services:

Retain "supervise" option in subparagraph below when third-party tests and inspections must be witnessed and approved by factory-authorized service representative to satisfy special extended-warranty requirements. In some cases, Installer may be factory authorized under warranty provisions to fulfill this role.

          - Engage factory-authorized service representative to [support] [supervise] field tests and inspections.

      - PROTECTION

        - After installation, protect emergency communications systems devices from construction activities. Remove and replace items that are contaminated, defaced, damaged, or otherwise caused to be unfit for use prior to acceptance by Owner.

END OF SECTION 284800